Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30491 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30503 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30536 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30557 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3058 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30764 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30863 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.30915 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33465 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.33613 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07532 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07983 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07983 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07986 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07986 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08006 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08006 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08008 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08008 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08008 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08015 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08015 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08015 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08016 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08017 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08018 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0802 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08021 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08022 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08022 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08033 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08036 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08038 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08052 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08066 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08066 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08066 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08069 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08069 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08138 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08138 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08155 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08155 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08159 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08159 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0819 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08201 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08201 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08224 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08263 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08264 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08269 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08557 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08559 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08577 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08577 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08614 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08644 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08644 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08812 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08845 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08845 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09306 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09339 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09359 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09359 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11229 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13271 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06564 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06957 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06957 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07457 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07459 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07474 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07474 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07679 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07708 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07708 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0811 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08139 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08156 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08156 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09785 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12806 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09359 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.09883 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10107 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10293 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10331 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1035 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10534 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10534 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10557 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10557 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10562 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10569 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10605 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1062 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1062 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10665 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10729 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10731 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.10732 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11058 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11092 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11092 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11126 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11128 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11144 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1115 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11154 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11483 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11491 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11491 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11568 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12164 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1239 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13115 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17478 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19654 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19738 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19738 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19738 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19738 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2022 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.08587 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.11367 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.17463 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19634 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19717 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19717 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19717 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.19717 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.202 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07532 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07983 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07983 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07983 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07986 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07986 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08006 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08006 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08008 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08008 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08008 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08009 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08015 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08015 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08015 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08016 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08017 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08018 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0802 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08021 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08022 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08022 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08033 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08036 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08038 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08052 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08066 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08066 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08066 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08069 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08069 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08096 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08138 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08138 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08155 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08155 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08159 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08159 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0819 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08201 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08201 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08224 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08263 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08264 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08269 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08557 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08559 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08577 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08577 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08614 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08644 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08644 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08845 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08845 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09306 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09339 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09359 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09359 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09383 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11229 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13271 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06564 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06957 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06957 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06957 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07457 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07459 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07474 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07474 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07708 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07708 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0811 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08139 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08156 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08156 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08177 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09785 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-010 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12806 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.05025 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08489 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08497 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08498 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08547 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08551 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08565 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0858 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08591 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08592 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08594 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08594 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08596 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08604 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08605 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08607 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08609 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0861 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08617 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08687 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08696 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08712 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08714 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08725 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08761 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08761 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08781 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08845 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08845 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08848 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08856 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08924 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09319 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09412 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09881 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09889 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09894 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.099 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09911 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09922 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09924 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09931 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09936 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09948 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0999 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10007 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10071 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10085 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10182 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10223 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10345 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10465 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10696 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10916 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11439 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.14874 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15538 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15745 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09851 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09881 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09883 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09897 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.099 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09911 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09922 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09924 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09931 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09936 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0999 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10007 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10071 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10085 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10182 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10223 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10345 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10465 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10696 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10916 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11439 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.14874 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15684 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15745 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12828 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13736 | 100.57 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13736 | 100.57 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.1377 | 101.14 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17233 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17629 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 105.86 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18681 | 107.23 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18681 | 107.23 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18705 | 106.66 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18717 | 107.87 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 100.95 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.91 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.91 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 103.92 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 105.74 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07668 | 101.48 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 100.83 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.21 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 102.98 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 104.53 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07923 | 102.37 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0802 | 104.71 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08127 | 118.26 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08684 | 115.9 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.03 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.37 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 114.65 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 114.65 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 114.42 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09013 | 114.86 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0925 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10331 | 125.72 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.37 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.99 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.99 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 103.73 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 106.35 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07668 | 101.45 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.04 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.45 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 103.25 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 104.94 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07923 | 102.48 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0802 | 104.88 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08127 | 120.17 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08684 | 116.62 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.55 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.92 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.92 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 115.22 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 115.22 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 114.98 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09013 | 115.44 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0925 | 119.36 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10331 | 126.07 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1119 | 139.31 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15186 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15186 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15189 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15193 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15196 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15197 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15199 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15201 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15201 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15209 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1521 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15212 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15212 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15213 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15218 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15222 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15224 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15224 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15257 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15257 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15265 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15266 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15301 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15311 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15311 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15314 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1533 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15331 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15334 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15394 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15398 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15406 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15406 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15464 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15579 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15579 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1581 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15832 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15887 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15956 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15956 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1633 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16841 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1717 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20192 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.202 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17966 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17979 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1798 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17985 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17996 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18003 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1806 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1808 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18088 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18165 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18201 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18266 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18329 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18335 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18472 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18515 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19004 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15973 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15979 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16098 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16135 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16562 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17466 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17818 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11603 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22324 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22469 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22474 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22595 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22628 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22629 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22646 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22651 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22783 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22816 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22825 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22841 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22847 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22848 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2301 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23078 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2319 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24205 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25113 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25198 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2663 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38265 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41996 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4214 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22208 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24432 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38232 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41955 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42097 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17966 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17979 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1798 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17985 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17996 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18003 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1806 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1808 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18088 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18165 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18201 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18266 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18329 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18335 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18472 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18526 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19004 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15973 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15979 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16098 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16562 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17466 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17818 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10288 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10337 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-060 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11581 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05025 | 141.57 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05025 | 140.52 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12144 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12144 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08985 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08994 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09017 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09019 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09026 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09026 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09043 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09047 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0906 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09062 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09062 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09065 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09065 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09067 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09072 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09076 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0908 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09084 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09085 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09085 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09085 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09086 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09088 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09088 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09088 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09089 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09089 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09089 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09089 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09089 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09089 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09091 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09092 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09095 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09095 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09095 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09097 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09097 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09099 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09101 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09102 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09102 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09102 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09103 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09103 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09106 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09108 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0911 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09112 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09112 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09113 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09136 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09136 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09141 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09141 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09143 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09144 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09148 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0918 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09199 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09204 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09204 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09213 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09241 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09253 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09253 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09261 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09261 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09261 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09262 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09262 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09264 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09266 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09339 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09347 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09373 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09373 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09471 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09511 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09511 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09511 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09511 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09579 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09579 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09695 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09943 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10096 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10155 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10155 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10155 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10155 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10155 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11125 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11125 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11125 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11689 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11689 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11689 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11883 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11883 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10415 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10415 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10415 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10415 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10415 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11386 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11386 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11386 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1195 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1195 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1195 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12144 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12144 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05344 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05344 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06023 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.05001 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07971 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06695 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06729 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06892 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07111 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07111 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07114 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07117 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0712 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07121 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07122 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07123 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07125 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07126 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07126 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07126 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07126 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07126 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07127 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07127 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07127 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07127 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07127 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07134 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07134 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07134 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07135 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07138 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07143 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07147 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0715 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0715 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07178 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07178 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0718 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0718 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07186 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07186 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07186 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07186 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07189 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07189 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07196 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07204 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07225 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07243 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07265 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07302 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07303 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0733 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07333 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07342 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07342 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07422 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07581 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07581 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08172 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08172 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0825 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09445 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09445 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09445 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.09445 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.11033 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07291 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07291 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09081 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0954 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0954 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0956 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0956 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09562 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09562 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09562 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09569 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09569 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09569 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0957 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09571 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09572 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09572 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09573 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09573 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09573 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09585 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09586 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09591 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09593 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09593 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09602 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0961 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09615 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09615 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09669 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09669 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09674 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09684 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09684 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09705 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0971 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09734 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09764 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09764 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09779 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09818 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09869 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0987 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09956 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09979 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09979 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10141 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10151 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10383 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10383 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11316 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11316 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13695 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13899 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15846 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06354 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06354 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07913 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08677 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08682 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08696 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08696 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08838 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08847 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09049 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09049 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09862 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09862 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11935 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12113 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15291 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.06759 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15105 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15702 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16492 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17034 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17448 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17597 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17597 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17604 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17619 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17619 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17619 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17619 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17648 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17648 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17662 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17682 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17682 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17763 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17819 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17905 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17906 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18004 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18013 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18029 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18034 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18036 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18257 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18278 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18284 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18284 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18546 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.18644 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20097 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26012 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26048 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33028 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33256 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33273 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33273 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33273 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.33273 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.18438 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23899 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25989 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.32995 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33223 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33239 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33239 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33239 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.33239 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07291 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07291 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07291 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09081 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09448 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0954 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0954 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0956 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0956 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09562 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09562 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09562 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09563 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09569 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09569 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09569 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0957 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09571 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09572 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09572 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09573 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09573 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09573 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09585 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09586 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09591 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09593 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09593 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09602 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0961 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09615 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09615 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09669 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09669 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09674 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09684 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09684 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09705 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0971 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09734 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09764 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09764 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09779 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09818 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09869 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0987 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09956 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09962 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09979 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09979 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10141 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10383 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10383 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11316 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.11316 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13695 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13899 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13964 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15846 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06354 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06354 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06354 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07913 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08677 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08682 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08696 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08696 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08838 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09049 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09049 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09862 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09862 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11935 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12113 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12169 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15291 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.07318 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08731 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08758 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08758 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08758 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08758 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08758 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08758 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08758 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08758 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-081 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09234 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05205 | 139.38 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05205 | 139.57 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05205 | 139.79 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05205 | 139.79 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05274 | 141.57 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05205 | 133.85 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05205 | 134.04 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05205 | 134.04 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05205 | 134.12 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05205 | 134.12 | Potential P4 Event - POI 560078_2 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05205 | 137.92 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05205 | 138.2 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05205 | 138.5 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05205 | 138.5 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05274 | 140.52 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.13479 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12842 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12842 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09682 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0969 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09691 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09712 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09716 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09723 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09723 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0974 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09744 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09757 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09759 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09759 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09762 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09762 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09764 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09769 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09773 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09777 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09781 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09782 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09782 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09782 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09783 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09785 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09785 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09785 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09786 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09786 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09786 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09786 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09786 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09786 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09788 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09789 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09791 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09791 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09792 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09793 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09794 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09794 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09795 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09798 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09798 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09799 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09799 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09799 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09799 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09803 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09804 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09805 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09807 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09808 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09809 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09831 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09832 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09835 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09835 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09837 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09838 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09874 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09891 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09892 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09903 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09914 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09914 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09919 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09945 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09945 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09945 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09947 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09947 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09953 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09954 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09954 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09954 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09957 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09957 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10031 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10039 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10142 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10143 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10196 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10239 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10239 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10239 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10239 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10392 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1062 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10642 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10929 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10929 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10929 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10929 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10929 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12336 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12336 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12336 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12396 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12396 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12396 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12582 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12582 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1119 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1119 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1119 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1119 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1119 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12597 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12597 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12597 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12657 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12657 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12657 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12842 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12842 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39619 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39677 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3973 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39739 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39783 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39797 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39798 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39798 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.398 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.398 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39801 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39804 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39805 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39805 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39805 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39806 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39806 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39807 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39818 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39822 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39831 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39832 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39845 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39852 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39853 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39865 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39876 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39876 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39985 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40095 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40154 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40397 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40422 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40556 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40881 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40891 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40897 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40897 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.43142 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39619 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39677 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3973 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39739 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39773 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39783 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39797 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39798 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39798 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.398 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.398 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39801 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39802 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39803 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39804 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39804 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39805 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39806 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39806 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39807 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39808 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39809 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3983 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39831 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39832 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39845 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39852 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39865 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39876 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39876 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3998 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39985 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39991 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40095 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40154 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40397 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40422 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40556 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40881 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40897 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40897 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40906 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.40908 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.43142 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.4329 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05013 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05013 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05016 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0502 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05023 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05024 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05025 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05028 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05028 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05028 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05028 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05028 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05029 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05029 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0503 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0503 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0503 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0503 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05037 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05038 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0504 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05046 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05048 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05048 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0505 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05053 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05053 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05083 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05083 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0509 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05091 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05091 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05096 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05096 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.051 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05106 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05107 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05146 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05147 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05158 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05167 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05184 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05185 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05246 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05249 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05252 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05255 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05255 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05261 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05261 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05369 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05399 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05483 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05483 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05552 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05848 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05848 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05848 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05848 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05895 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05895 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0598 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05983 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05983 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05985 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05985 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05985 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05985 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05985 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.05517 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12969 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12969 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12989 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12989 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12991 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12991 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12991 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12998 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12998 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12998 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12999 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13001 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13001 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13003 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13003 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13003 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13015 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13017 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1302 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13032 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13041 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13046 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13046 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1305 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1305 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13072 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13103 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13103 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13117 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13118 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13118 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13128 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13128 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13139 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13149 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13208 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13248 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13264 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13265 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13417 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13422 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13439 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13439 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13624 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13651 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1368 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1368 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13703 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13703 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13716 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13813 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13813 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14446 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14446 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14486 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17208 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21528 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11392 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11692 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11697 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11711 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11711 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11873 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11942 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11942 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11953 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12037 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12037 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12589 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12589 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12624 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14996 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20774 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15234 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15486 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15559 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15715 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15715 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15726 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15735 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15738 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15738 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1575 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1575 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15773 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1578 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15874 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15932 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15965 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15966 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16096 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16105 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1616 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16167 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16183 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16189 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16191 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16329 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16363 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16363 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1645 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16457 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16457 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16571 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16755 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17756 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19179 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27109 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29469 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29671 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29671 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29671 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29671 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.29784 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.14428 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.16291 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.27086 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2944 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2964 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2964 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2964 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.2964 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.29755 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.05517 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12969 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12969 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12989 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12989 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12991 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12991 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12991 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12992 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12998 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12998 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12998 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12999 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13001 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13001 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13003 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13003 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13003 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13015 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13017 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1302 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13032 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13041 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13046 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13046 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1305 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1305 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13072 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13103 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13103 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13117 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13118 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13118 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13128 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13128 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13139 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13149 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13165 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13208 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13248 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13264 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13265 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13417 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13422 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13439 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13439 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13651 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1368 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1368 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13703 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13703 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13703 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13716 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13813 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13813 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14446 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14446 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14486 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14553 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17208 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21528 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11392 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11692 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11697 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11711 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11711 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11942 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11942 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11942 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11953 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12037 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12037 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12589 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12589 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12624 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.12683 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14996 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-086 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20774 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05201 | 139.38 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05201 | 139.57 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05201 | 139.79 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05201 | 139.79 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05795 | 141.57 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05201 | 133.85 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05201 | 134.04 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05201 | 134.04 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05201 | 134.12 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05201 | 134.12 | Potential P4 Event - POI 560078_2 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05201 | 137.92 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05201 | 138.2 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05201 | 138.5 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05201 | 138.5 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05795 | 140.52 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10079 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10079 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06559 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06805 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06812 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06813 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06839 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06841 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06844 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06844 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06845 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06846 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06862 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06867 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06871 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06879 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0688 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06882 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06882 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06884 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06884 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06887 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06891 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06895 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.069 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06904 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06905 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06906 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06908 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06908 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06908 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06908 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06909 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06909 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06909 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06909 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0691 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06911 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06911 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06915 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06915 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06915 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06917 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06918 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06918 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0692 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06921 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06922 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06922 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06924 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06924 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06925 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06926 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0693 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06932 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06933 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06934 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06934 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06944 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06944 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06957 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06962 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06966 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06966 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06969 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06975 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07009 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07011 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07023 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07031 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07031 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07049 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07083 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07083 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0709 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0709 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07091 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07091 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07091 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07092 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07112 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07176 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07184 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07189 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07189 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07189 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07202 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07236 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07236 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07236 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07236 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07589 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07733 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07733 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07733 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07733 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07733 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.07793 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09586 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09586 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09586 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09818 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09818 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0745 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0745 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0745 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07993 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07993 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07993 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07993 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.07993 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09846 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09846 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09846 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10079 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-110 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10079 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.0796 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11427 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11427 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08411 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08418 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08419 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08445 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08445 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08451 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08452 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08469 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08473 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08486 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08488 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08488 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0849 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0849 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08493 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08497 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08501 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08506 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0851 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08511 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08512 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08514 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08514 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08514 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08514 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08515 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08515 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08515 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08515 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08516 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08517 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08517 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08521 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08521 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08521 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08524 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08526 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08527 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08529 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08531 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08536 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08537 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08539 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08539 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0854 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08563 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08566 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08574 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08574 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08619 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08619 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08635 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08636 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08636 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08648 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08662 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08683 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08683 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08703 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08705 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08721 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08721 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08721 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08764 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08764 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08771 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08874 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08911 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08911 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08911 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08911 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08983 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09117 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09322 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09517 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09517 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09517 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09517 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09517 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10311 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10311 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10311 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10963 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10963 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10963 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11166 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11166 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09778 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09778 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09778 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09778 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09778 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10572 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10572 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10572 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11224 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11224 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11224 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11427 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11427 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18968 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18968 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1897 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18971 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18972 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18972 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18972 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18972 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18973 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18973 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18974 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18974 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18974 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18975 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18975 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18977 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18977 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18977 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18983 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18988 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18994 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18995 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19005 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19016 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19019 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19026 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19032 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19045 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19046 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19064 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19064 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1911 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1911 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1911 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1911 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19129 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19136 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19178 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19198 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19198 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19198 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19199 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19211 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19239 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19377 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19453 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19976 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.20247 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21257 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21293 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21396 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21452 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21452 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21502 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18945 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18968 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18968 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1897 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1897 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18971 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18972 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18972 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18973 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18974 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18974 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18974 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18975 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18975 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18976 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18977 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18992 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18994 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.18995 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19005 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19016 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19019 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19026 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19032 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19045 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19064 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19064 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1911 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1911 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1911 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1911 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19129 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19136 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19178 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19198 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19198 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19198 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19199 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19211 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19239 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19377 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19453 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.19976 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.20247 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21257 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21293 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21405 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21411 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21452 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21452 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21474 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.21502 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05035 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05035 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05035 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05035 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05042 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05042 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05053 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05057 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.09023 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.09023 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14587 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22039 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22039 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22058 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22058 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22069 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2207 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22083 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22083 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22089 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.221 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22105 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22105 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22107 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22109 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22109 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22173 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22173 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22176 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22178 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22178 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22191 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22254 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22254 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22267 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22302 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2243 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22436 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22452 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22452 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22513 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22542 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22542 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22572 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22614 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22698 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22698 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23029 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23079 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23115 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23115 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23638 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23638 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.24072 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36557 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19547 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19552 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19566 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19566 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19671 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19708 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1978 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1978 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20069 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20112 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20144 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20144 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.206 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.206 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20978 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.35277 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12917 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23605 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23724 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23747 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23748 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23748 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23762 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23762 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23769 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23769 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23772 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23787 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23855 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23892 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23893 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23905 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23955 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24126 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24132 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24135 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24151 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24156 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24157 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24167 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24167 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24319 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24385 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24391 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24391 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24532 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24817 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2486 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25197 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25331 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25619 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.43191 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44359 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.44612 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.45016 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.45016 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.45016 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.45016 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23118 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.23505 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.43153 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.44315 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.44566 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4497 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4497 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4497 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4497 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14587 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22039 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22039 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22058 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22058 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22061 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22062 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22068 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22069 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2207 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22071 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22083 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22083 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22089 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.221 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22105 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22105 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22107 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22109 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22109 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22163 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22173 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22173 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22176 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22178 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22178 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22191 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22254 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22254 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22267 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22278 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22302 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2243 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22436 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22452 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22452 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22513 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22542 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22542 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22572 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22698 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.22698 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23029 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23079 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23115 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23115 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23186 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23638 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23638 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.23638 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.24072 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.36557 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19547 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19552 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19566 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19566 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.19671 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1978 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1978 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20069 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20112 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20144 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20144 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20206 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.206 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.206 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.206 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.20978 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-120 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.35277 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05294 | 141.57 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05475 | 139.38 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05475 | 139.57 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05475 | 139.79 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05475 | 139.79 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05475 | 133.85 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05475 | 134.04 | POI 515800_22 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05475 | 134.04 | Potential P4 Event - POI 560078_3 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05475 | 134.12 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 353 | 353 | 0.05475 | 134.12 | Potential P4 Event - POI 560078_2 | Cumulative Impact | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05294 | 140.52 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05475 | 137.92 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05475 | 138.2 | POI 515800_22 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05475 | 138.5 | Potential P4 Event - POI 560078_0 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05475 | 138.5 | Potential P4 Event - POI 560078_1 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 159 | 159 | 0.12121 | 103.5 | Potential P4 Event - POI 523097_33 | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 159 | 159 | 0.12121 | 103.5 | Potential P4 Event - POI 523961_4 | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 159 | 159 | 0.13768 | 104.88 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 159 | 159 | 0.17898 | 119.64 | P12:115:SPS:T08_2_SPRMN_PRNGLE:::: | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2 | 159 | 159 | 0.16075 | 107.72 | P12:115:SPS:T06_1_SPRMN_PRNGLE:::: | Cumulative Impact | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT2 line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.3973 | 106.36 | P12:115:SPS:T49_1_PRNGLE_BLKHK:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.3973 | 110.41 | 523214 WRB_REF 115 523346 BLKHAWK_E 3 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.40131 | 107.79 | 523551 HUTCHISON 6 230 524044 NICHOLS 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41541 | 105.4 | P12:230:SPS:K98::1_CHANN_XIT:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41546 | 103.32 | P12:345:OKGE:BKRBKR604_2 :::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41551 | 102.8 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41551 | 102.99 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.39 | 640312 PAULINE3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.4 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.64 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.68 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.84 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.84 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 102.85 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 102.7 | P11:230:WERE:JECU1-GEN:::HV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 102.7 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 102.71 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.24 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.37 | P12:EHV:EES::8PERRYVILLE%:1(1) | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.37 | P12:HV:EES::6LEWISCREEK!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.39 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.39 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.39 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.39 | P11:HV:EES::1CARVLE_C1!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.39 | P12:LV-EHV:EES::7GRIMES%:1FRNTR 1!:1FRNTR 2!:1FRNTR 3!:1FRNTR 4!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.4 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.4 | P12:LV-HV:EES::6GYPSY%:1GYP U3!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.61 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.63 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.63 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.63 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.64 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.64 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.64 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.65 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.65 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.69 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.7 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.7 | P23:345:XEL:8H14 PRI | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.71 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.71 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.74 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.74 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.74 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.75 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.75 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.76 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.76 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.76 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.78 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.78 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.79 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.79 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.79 | P23:345:MEC:CBEC 908 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.8 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.81 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.82 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.82 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.82 | P23:345:MEC:CBEC 905 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.83 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.84 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.85 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.85 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.85 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.86 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 102.93 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.05 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.1 | 772181 GEN-2023-010 230 772182 G23-010XFMR1 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.1 | 772181 GEN-2023-010 230 772185 G23-010XFMR2 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.27 | P12:115:GLHP:POWELL-LOBO-DRYTRAILS:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.59 | ASGI-2011-002_POI_523266_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.69 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.69 | ASGI-2016-010_POI_523090_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.8 | GEN-2023-010_POI_523309_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.83 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.83 | GEN-2017-100_POI_523090_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.07 | GEN-2002-009_POI_523195_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.28 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.28 | GEN-2017-047_POI_523120_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 108.72 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 109.32 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.61 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.63 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.64 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.67 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.68 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.68 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.74 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.83 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.85 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 102.86 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 102.65 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 102.71 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 102.75 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 102.91 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 102.93 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 102.94 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 102.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 102.96 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 102.96 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 104.22 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 104.22 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41561 | 102.91 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41561 | 102.91 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41565 | 102.97 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41565 | 102.99 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41567 | 102.96 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 103.13 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 103.76 | Potential P4 Event - POI 560022_9 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 103.76 | Potential P4 Event - POI 762216_5 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41572 | 103.27 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41574 | 103.31 | Potential P4 Event - POI 515800_13 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 104.01 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 104.06 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 104.06 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4158 | 103.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41601 | 104.74 | P42:345:OKGE:SB_BOER7384:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41604 | 104.45 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41604 | 104.45 | P12:345:OKGE:BKRBKR489:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41612 | 108.13 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41612 | 108.88 | Potential P4 Event - POI 523097_19 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41618 | 104.6 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41618 | 104.97 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41704 | 102.96 | 523977 HARRNG_WST 6 230 523978 HARRNG_MID 6 230 @1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41739 | 118.02 | Potential P4 Event - POI 523097_33 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41739 | 118.02 | Potential P4 Event - POI 523961_4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41768 | 106.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41775 | 105.51 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41775 | 105.52 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.43138 | 119.63 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.44784 | 107.5 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523266 PRINGLE 3 115 997653 ENRCO13617-1 115 1 | 168 | 193 | 1 | 144.49 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.3973 | 107.91 | P12:115:SPS:T49_1_PRNGLE_BLKHK:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.3973 | 112.56 | 523214 WRB_REF 115 523346 BLKHAWK_E 3 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.40131 | 109.48 | 523551 HUTCHISON 6 230 524044 NICHOLS 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41541 | 107.1 | P12:230:SPS:K98::1_CHANN_XIT:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41546 | 104.95 | P12:345:OKGE:BKRBKR604_2 :::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41551 | 104.41 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41551 | 104.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 103.97 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 104.25 | 539117 SPRVILL-EHVB 230 539695 SPEARVL6 230 Z1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 104.28 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 104.47 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 104.47 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41552 | 104.49 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 103.99 | 640183 GENTLMN3 345 640500 THEDFRD3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 104.2 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 104.31 | P11:230:WERE:JECU1-GEN:::HV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 104.31 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41553 | 104.32 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.8 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.96 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.96 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.96 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.97 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.98 | P12:LV-HV:EES::6GYPSY%:1GYP U3!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | P11:HV:EES::FLINTCR1:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | P12:HV:EES::4LEWIS%:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 103.99 | P12:LV-HV:EES::3GYPSY%:1GYP U2!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.2 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.21 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.23 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.23 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.23 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.24 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.24 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.24 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.25 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.25 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.27 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.3 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.31 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.32 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.32 | P23:345:XEL:8H14 PRI | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.32 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.35 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.35 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.36 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.37 | P23:345:XEL:8N17 SHC | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.37 | P23:345:XEL:8N22 SHC | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.38 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.38 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.39 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.39 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.4 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.41 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.41 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.41 | P23:345:MEC:CBEC 908 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.42 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.43 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.44 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.45 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.45 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.45 | P23:345:MEC:CBEC 905 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.47 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.48 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.48 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.49 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.49 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.5 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.55 | 772281 GEN-2023-015 345 772282 G23-015XFMR1 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.7 | 772181 GEN-2023-010 230 772182 G23-010XFMR1 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.7 | 772181 GEN-2023-010 230 772185 G23-010XFMR2 34.5 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.71 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 104.87 | P12:115:GLHP:POWELL-LOBO-DRYTRAILS:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.21 | ASGI-2011-002_POI_523266_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.3 | 588480 A16-010_SUB 115 3WXFMR A16-010_SUB 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.3 | ASGI-2016-010_POI_523090_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.37 | GEN-2023-010_POI_523309_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.43 | 589381 G17-100XFMR1 34.5 589380 GEN-2017-100 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.43 | GEN-2017-100_POI_523090_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.71 | GEN-2002-009_POI_523195_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.88 | 588861 G17-047XFMR1 34.5 588860 GEN-2017-047 115 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 105.88 | GEN-2017-047_POI_523120_Generator_outage | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 110.18 | 523344 BLKHAWK_W 3 115 523461 BLACKHAWK1 1 13.8 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41554 | 110.76 | 523346 BLKHAWK_E 3 115 523462 BLACKHAWK2 1 13.8 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.21 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.23 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.24 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.27 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.28 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.35 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.45 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41555 | 104.49 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 104.25 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 104.32 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41556 | 104.36 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41557 | 104.2 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 104.53 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 104.55 | 511456 O.K.U.-7 345 762467 G18-015-TAP 345 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 104.59 | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41558 | 104.6 | 515621 OPENSKY7 345 560053 G15052_T 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 104.33 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 104.6 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 104.6 | 532798 VIOLA 7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 105.82 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4156 | 105.82 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41561 | 104.54 | P23:345:AEPW:PITTSBURG CB 3445A NBTB:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41561 | 104.54 | P42:345:AEPW:PITTSBURG CB 3445A NBTB+FAULT:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41565 | 104.6 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41565 | 104.62 | 514801 MINCO 7 345 514901 CIMARON7 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 104.8 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 105.44 | Potential P4 Event - POI 560022_9 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41568 | 105.44 | Potential P4 Event - POI 762216_5 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41572 | 104.93 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 105.74 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 105.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41575 | 105.79 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4158 | 105.04 | POI 515800_22 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.4158 | 105.08 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41601 | 106.47 | P42:345:OKGE:SB_BOER7384:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41604 | 106.17 | 515375 WWRDEHV7 345 516059 BECKHAM7 345 2 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41604 | 106.17 | P12:345:OKGE:BKRBKR489:::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41612 | 110 | P42:345:SPS:HITCHLAND:1R15_SLG::EHV: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41618 | 106.42 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41618 | 106.88 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41704 | 104.63 | 523977 HARRNG_WST 6 230 523978 HARRNG_MID 6 230 @1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41717 | 110.9 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41739 | 120.48 | Potential P4 Event - POI 523097_33 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41739 | 120.48 | Potential P4 Event - POI 523961_4 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41768 | 108.17 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41775 | 107.33 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.41775 | 107.34 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.43138 | 122.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 0.44784 | 109.15 | 523978 HARRNG_MID 6 230 523979 HARRNG_EST 6 230 @1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523267 PRINGLE 6 230 997653 ENRCO13617-1 115 1 | 168 | 193 | 1 | 144.35 | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | Cumulative Impact | Upgrade the exsting PRINGLE6 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.1534 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14294 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14294 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11117 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11124 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11125 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11144 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11151 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11158 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11158 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11175 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11179 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11192 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11194 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11194 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11196 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11196 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11199 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11203 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11207 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11212 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11216 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11217 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11218 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11219 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11219 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1122 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1122 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1122 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1122 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1122 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1122 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11221 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11222 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11223 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11225 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11225 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11226 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11226 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11227 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11227 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11229 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11231 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11232 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11232 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11232 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11233 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11233 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11235 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11237 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11238 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11239 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11241 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11243 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1126 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11263 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11264 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11264 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11264 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11266 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11302 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11303 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11317 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11323 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11355 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11355 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11355 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11356 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11356 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11367 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11368 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11374 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11374 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11374 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11374 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11377 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11379 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11379 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11453 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11461 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11517 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11688 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11723 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11724 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11736 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11736 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11736 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11736 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11849 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11988 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12086 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12522 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12522 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12522 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12522 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12522 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1387 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1387 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1387 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14033 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14033 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14808 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14808 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.14808 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12783 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12783 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12783 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12783 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12783 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14131 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14131 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14131 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14294 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.14294 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15068 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15068 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.15068 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.344 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.34874 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.34955 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35016 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3504 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35109 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3519 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35192 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35192 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35195 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35195 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35198 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35199 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35199 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.352 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.352 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35202 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35204 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35206 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35216 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35219 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35232 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35232 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35235 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35236 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35238 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35244 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3526 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35261 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35261 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35283 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35313 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35369 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35412 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35412 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35425 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35606 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35631 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35746 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38567 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.42762 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.344 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.34874 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.34955 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35016 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3504 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35109 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35163 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3519 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35192 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35192 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35195 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35195 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35197 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35198 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35199 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35199 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35201 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35202 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35203 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35232 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35232 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35234 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35235 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35238 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35244 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.3526 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35261 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35261 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35283 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35313 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35349 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35369 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35412 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35412 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35415 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35437 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35441 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35606 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35631 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.35746 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.38567 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39848 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.39996 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.42762 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09097 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09409 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09409 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09429 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09429 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09431 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09431 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09431 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09439 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0944 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09441 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09442 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09444 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09444 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09444 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09455 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09459 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0946 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09474 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09486 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0949 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0949 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09507 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09507 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09553 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09553 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09569 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09569 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09584 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09586 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09586 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09587 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09597 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09597 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09598 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09649 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09684 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09692 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09922 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09925 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09942 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09942 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10154 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10282 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10282 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1035 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1038 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1038 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1045 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1077 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1077 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1079 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1316 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15629 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07927 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08354 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08354 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08646 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08649 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08664 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08664 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08849 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0896 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0896 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09107 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09386 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09386 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09403 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11469 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15082 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11104 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11375 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11603 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11802 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11891 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11921 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11973 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11973 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11996 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11996 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1202 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12025 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12035 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12035 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12037 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1212 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12179 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1218 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12181 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12495 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.125 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12516 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12521 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12524 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12821 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12828 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12828 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12875 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12909 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.12909 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13041 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13226 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.13824 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15004 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.20193 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22394 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22507 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22507 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22507 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22507 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22911 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.10188 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.12683 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.20176 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22371 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22484 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22484 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22484 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22484 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22888 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09097 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09409 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09409 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09429 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09429 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09431 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09431 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09431 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09432 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09438 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09439 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0944 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09441 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09442 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09444 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09444 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09444 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09455 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09459 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0946 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09474 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09486 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0949 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0949 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09507 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09507 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09539 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09553 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09553 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09569 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09569 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09584 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09586 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09586 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09586 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09587 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09597 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09597 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09598 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09649 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09684 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09685 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09692 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09922 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09925 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09942 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09942 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10282 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10282 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1035 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1038 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1038 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1045 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1077 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1077 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1079 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1084 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1316 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.15629 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07927 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08354 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08354 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08354 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08646 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08649 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08664 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08664 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0896 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0896 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09107 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09386 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09386 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09403 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09447 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11469 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-123 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15082 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.05025 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08489 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08497 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08498 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08547 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08551 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08565 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0858 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08591 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08592 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08594 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08594 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08596 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08604 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08605 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08607 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08609 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0861 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08617 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08687 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08696 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08712 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08714 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08725 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08761 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08761 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08781 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08845 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08845 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08848 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08856 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08924 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09319 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09412 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09881 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09889 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09894 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.099 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09911 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09922 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09924 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09931 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09936 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09948 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0999 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10007 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10071 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10085 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10182 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10223 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10345 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10465 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10696 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10916 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11439 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.14874 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15538 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15745 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09851 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09881 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09883 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09897 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.099 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09911 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09922 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09924 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09931 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09936 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0999 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10007 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10071 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10085 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10182 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10223 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10345 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10465 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10696 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10916 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11439 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.14874 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15684 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15745 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12828 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13736 | 100.57 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13736 | 100.57 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.1377 | 101.14 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17233 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17629 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 105.86 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18681 | 107.23 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18681 | 107.23 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18705 | 106.66 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18717 | 107.87 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 100.95 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.91 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.91 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 103.92 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 105.74 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07668 | 101.48 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 100.83 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.21 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 102.98 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 104.53 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07923 | 102.37 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0802 | 104.71 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08127 | 118.26 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08684 | 115.9 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.03 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.37 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 114.65 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 114.65 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 114.42 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09013 | 114.86 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0925 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10331 | 125.72 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.37 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.99 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.99 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 103.73 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 106.35 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07668 | 101.45 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.04 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.45 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 103.25 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 104.94 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07923 | 102.48 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0802 | 104.88 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08127 | 120.17 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08684 | 116.62 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.55 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.92 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.92 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 115.22 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 115.22 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 114.98 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09013 | 115.44 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0925 | 119.36 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10331 | 126.07 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1119 | 139.31 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15186 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15186 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15189 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15193 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15196 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15197 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15199 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15201 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15201 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15209 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1521 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15212 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15212 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15213 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15218 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15222 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15224 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15224 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15257 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15257 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15265 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15266 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15301 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15311 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15311 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15314 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1533 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15331 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15334 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15394 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15398 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15406 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15406 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15464 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15579 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15579 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1581 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15832 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15887 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15956 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15956 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1633 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16841 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1717 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20192 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.202 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17966 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17979 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1798 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17985 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17996 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18003 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1806 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1808 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18088 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18165 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18201 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18266 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18329 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18335 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18472 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18515 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19004 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15973 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15979 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16098 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16135 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16562 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17466 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17818 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11603 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22324 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22469 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22474 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22595 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22628 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22629 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22646 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22651 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22783 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22816 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22825 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22841 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22847 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22848 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2301 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23078 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2319 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24205 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25113 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25198 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2663 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38265 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41996 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4214 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22208 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24432 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38232 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41955 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42097 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17966 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17979 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1798 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17985 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17996 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18003 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1806 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1808 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18088 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18165 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18201 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18266 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18329 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18335 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18472 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18526 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19004 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15973 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15979 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16098 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16562 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17466 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17818 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10288 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10337 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-142 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11581 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.05025 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08489 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08497 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08498 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08547 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08551 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08565 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0858 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08591 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08592 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08594 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08594 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08596 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08604 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08605 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08607 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08609 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0861 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08617 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08687 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08696 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08712 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08714 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08725 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08761 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08761 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08781 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08845 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08845 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08848 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08856 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08924 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09319 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09412 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09881 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09889 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09894 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.099 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09911 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09922 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09924 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09931 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09936 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09948 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0999 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10007 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10071 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10085 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10182 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10223 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10345 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10465 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10696 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10916 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11439 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.14874 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15538 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15745 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09851 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09881 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09883 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09897 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.099 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09911 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09922 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09924 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09931 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09936 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0999 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10007 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10071 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10085 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10182 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10223 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10345 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10465 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10696 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10916 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11439 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.14874 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15684 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15745 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12828 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13736 | 100.57 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13736 | 100.57 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.1377 | 101.14 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17233 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17629 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 105.86 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18681 | 107.23 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18681 | 107.23 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18705 | 106.66 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18717 | 107.87 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 100.95 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.91 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.91 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 103.92 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 105.74 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07668 | 101.48 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 100.83 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.21 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 102.98 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 104.53 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07923 | 102.37 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0802 | 104.71 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08127 | 118.26 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08684 | 115.9 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.03 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.37 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 114.65 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 114.65 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 114.42 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09013 | 114.86 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0925 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10331 | 125.72 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.37 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.99 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.99 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 103.73 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 106.35 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07668 | 101.45 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.04 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.45 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 103.25 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 104.94 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07923 | 102.48 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0802 | 104.88 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08127 | 120.17 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08684 | 116.62 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.55 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.92 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.92 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 115.22 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 115.22 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 114.98 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09013 | 115.44 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0925 | 119.36 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10331 | 126.07 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1119 | 139.31 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15186 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15186 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15189 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15193 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15196 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15197 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15199 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15201 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15201 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15209 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1521 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15212 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15212 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15213 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15218 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15222 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15224 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15224 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15257 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15257 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15265 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15266 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15301 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15311 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15311 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15314 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1533 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15331 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15334 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15394 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15398 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15406 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15406 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15464 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15579 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15579 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1581 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15832 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15887 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15956 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15956 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1633 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16841 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1717 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20192 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.202 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17966 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17979 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1798 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17985 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17996 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18003 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1806 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1808 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18088 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18165 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18201 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18266 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18329 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18335 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18472 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18515 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19004 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15973 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15979 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16098 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16135 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16562 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17466 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17818 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11603 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22324 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22469 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22474 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22595 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22628 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22629 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22646 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22651 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22783 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22816 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22825 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22841 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22847 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22848 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2301 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23078 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2319 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24205 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25113 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25198 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2663 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38265 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41996 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4214 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22208 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24432 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38232 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41955 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42097 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17966 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17979 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1798 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17985 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17996 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18003 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1806 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1808 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18088 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18165 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18201 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18266 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18329 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18335 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18472 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18526 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19004 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15973 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15979 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16098 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16562 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17466 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17818 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10288 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10337 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-143 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11581 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11474 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11474 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08424 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08432 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08433 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08458 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08458 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08465 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08465 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08482 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08486 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.085 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08501 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08501 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08504 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08504 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08506 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08511 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08515 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08519 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08524 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08524 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08524 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08526 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08527 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08529 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08529 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08531 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08534 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08534 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08535 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08536 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08537 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08537 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08539 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0854 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08541 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08541 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08543 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08544 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08545 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08549 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0855 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08552 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08553 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08553 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08579 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08587 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08622 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08632 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08632 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08648 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08696 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08696 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0871 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0871 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08714 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08717 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08729 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08729 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08729 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08773 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08773 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08784 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08888 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08889 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08889 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08896 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08925 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08925 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08925 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08925 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0903 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09346 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09532 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09532 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09532 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09532 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09532 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1029 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1029 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1029 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11012 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11012 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11012 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11214 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11214 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09793 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09793 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09793 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09793 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09793 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10551 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10551 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10551 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11272 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11272 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11272 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11474 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11474 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06238 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06238 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06239 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06241 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06241 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06241 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06242 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06242 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06244 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06252 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06258 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06264 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06265 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06274 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06285 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06288 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06295 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.063 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06312 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06331 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06331 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06359 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06374 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06403 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06412 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06444 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06545 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06557 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06846 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07012 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07219 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07562 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0778 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12056 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12206 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12325 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12325 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12463 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06215 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06238 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06238 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06239 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0624 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06241 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06241 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06242 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06242 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06244 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06247 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06261 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06264 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06265 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06274 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06285 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06288 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06295 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.063 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06331 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06331 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06359 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06374 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06403 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06412 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06444 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06545 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06557 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06846 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07012 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07219 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07562 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0778 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12056 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12325 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12325 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12375 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12463 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09806 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10564 | 100.57 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10564 | 100.57 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10607 | 101.14 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13102 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13435 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1437 | 105.86 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1437 | 106.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1437 | 106.45 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1437 | 106.45 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14403 | 107.23 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14403 | 107.23 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14429 | 106.66 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14448 | 107.87 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05088 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05127 | 115.9 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.03 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.37 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05406 | 114.65 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05406 | 114.65 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05409 | 114.42 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05415 | 114.86 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05863 | 125.72 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05088 | 119.36 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05127 | 116.62 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.55 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.92 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.92 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05406 | 115.22 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05406 | 115.22 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05409 | 114.98 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05415 | 115.44 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05863 | 126.07 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.12906 | 139.31 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16902 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16902 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16905 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16909 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16912 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16914 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16918 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16918 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16918 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16918 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16919 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16925 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16925 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16926 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16926 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16928 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16934 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16937 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16939 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16939 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16966 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16967 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16967 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16972 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16972 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16975 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16975 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1698 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16982 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17001 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1701 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1701 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1703 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17048 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17048 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17049 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17108 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17112 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1712 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1712 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17173 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17231 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17294 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17294 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17582 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17639 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17687 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17687 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18383 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18631 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18631 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18631 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18631 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19209 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19893 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22153 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22153 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22183 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2219 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22144 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22144 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09431 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16883 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16883 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16902 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16902 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16913 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16914 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16916 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16916 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16927 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16928 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16933 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16938 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16938 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16944 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16951 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17017 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17017 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17022 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17022 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17028 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17034 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17113 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17135 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17135 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17149 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17166 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17274 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17281 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17296 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17296 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17407 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17459 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17567 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17587 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17587 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19332 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20067 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28014 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15054 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1506 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15073 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15073 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15169 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15215 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15309 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15326 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15326 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15859 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15859 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16847 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17487 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18104 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18104 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27032 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11812 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22642 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22643 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22643 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22657 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22657 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22664 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22664 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22678 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22681 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22803 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22804 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22838 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22838 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22842 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22843 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23021 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2303 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23046 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23052 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23052 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23068 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23137 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.232 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23281 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23286 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23286 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23492 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24452 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25473 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25581 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27549 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37554 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42379 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42533 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22435 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25276 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37521 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42338 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4249 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09431 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16883 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16883 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16902 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16902 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16913 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16914 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16916 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16916 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16927 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16928 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16933 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16938 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16938 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16944 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16951 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17017 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17017 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17022 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17022 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17028 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17034 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17113 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17135 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17135 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17149 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17166 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17274 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17281 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17296 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17296 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17407 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17567 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17587 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17587 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.184 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19332 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20067 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28014 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15054 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1506 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15073 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15073 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15169 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15309 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15326 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15326 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15859 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15859 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16847 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17487 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18104 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18104 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18104 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27032 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09688 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09796 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-158 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10988 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11474 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11474 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08424 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08432 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08433 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08458 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08458 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08465 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08465 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08482 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08486 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.085 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08501 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08501 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08504 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08504 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08506 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08511 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08515 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08519 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08524 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08524 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08524 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08526 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08527 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08528 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08529 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08529 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08531 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08534 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08534 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08535 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08536 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08537 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08537 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08539 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0854 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08541 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08541 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08543 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08544 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08545 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08549 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0855 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08552 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08553 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08553 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08579 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08587 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08622 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08632 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08632 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08648 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08696 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08696 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0871 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0871 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08714 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08717 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08729 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08729 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08729 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08773 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08773 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08784 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08888 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08889 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08889 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08896 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08925 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08925 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08925 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08925 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0903 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09269 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09346 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09532 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09532 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09532 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09532 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09532 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1029 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1029 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1029 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11012 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11012 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11012 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11214 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11214 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09793 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09793 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09793 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09793 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09793 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10551 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10551 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10551 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11272 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11272 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11272 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11474 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11474 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06238 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06238 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06239 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06241 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06241 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06241 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06242 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06242 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06244 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06252 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06258 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06264 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06265 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06274 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06285 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06288 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06295 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.063 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06312 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06331 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06331 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06359 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06374 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06403 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06412 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06444 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06545 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06557 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06846 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07012 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07219 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07562 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0778 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12056 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12206 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12325 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12325 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12463 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06215 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06238 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06238 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06239 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0624 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06241 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06241 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06242 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06242 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06243 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06244 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06245 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06246 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06247 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06261 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06264 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06265 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06274 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06285 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06288 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06295 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.063 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06331 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06331 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06347 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06359 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06374 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06403 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06412 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06444 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06461 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06545 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06557 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.06846 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07012 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07219 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07562 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0771 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0778 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12056 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12222 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12325 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12325 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12375 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12463 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09806 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10564 | 100.57 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10564 | 100.57 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.10607 | 101.14 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13102 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13435 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1437 | 105.86 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1437 | 106.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1437 | 106.45 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1437 | 106.45 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14403 | 107.23 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14403 | 107.23 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14429 | 106.66 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14448 | 107.87 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05088 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05127 | 115.9 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.03 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.37 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05406 | 114.65 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05406 | 114.65 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05409 | 114.42 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05415 | 114.86 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.05863 | 125.72 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05088 | 119.36 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05127 | 116.62 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.55 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.92 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05399 | 114.92 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05406 | 115.22 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05406 | 115.22 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05409 | 114.98 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05415 | 115.44 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.05863 | 126.07 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.12906 | 139.31 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16902 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16902 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16905 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16909 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16912 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16913 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16914 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16917 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16918 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16918 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16918 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16918 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16919 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16925 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16925 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16926 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16926 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16928 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16934 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16937 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16939 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16939 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16966 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16967 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16967 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16972 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16972 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16975 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16975 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1698 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16982 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17001 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1701 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1701 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1703 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17048 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17048 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17049 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17108 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17112 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1712 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1712 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17173 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17231 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17294 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17294 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17582 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17639 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17687 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17687 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18383 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18631 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18631 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18631 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18631 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19209 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19893 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22137 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22153 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22153 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22183 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2219 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22144 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22144 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09431 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16883 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16883 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16902 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16902 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16913 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16914 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16916 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16916 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16927 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16928 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16933 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16938 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16938 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16944 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16951 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17017 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17017 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17022 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17022 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17028 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17034 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17113 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17135 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17135 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17149 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17166 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17274 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17281 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17296 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17296 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17407 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17459 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17567 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17587 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17587 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19332 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20067 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28014 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15054 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1506 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15073 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15073 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15169 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15215 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15309 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15326 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15326 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15859 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15859 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16847 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17487 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18104 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18104 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27032 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11812 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.225 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22642 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22643 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22643 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22657 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22657 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22664 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22664 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22678 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22681 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22771 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22803 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22804 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22838 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22838 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22842 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22843 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22855 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23021 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2303 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23046 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23052 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23052 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23068 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23137 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.232 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23281 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23286 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23286 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23492 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24452 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25473 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25581 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.27549 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37554 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42379 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42533 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42908 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22435 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.25276 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37521 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42338 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.4249 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42864 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09431 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16883 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16883 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16902 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16902 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16905 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16906 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16912 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16913 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16914 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16915 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16916 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16916 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16927 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16928 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16933 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16938 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16938 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16944 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16951 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16954 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17007 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17017 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17017 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17022 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17022 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17028 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17034 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17113 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17135 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17135 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17149 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17166 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17195 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17274 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17281 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17296 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17296 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17407 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17567 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17587 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17587 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.184 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19332 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20067 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.2016 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20774 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28014 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15054 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1506 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15073 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15073 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15169 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15309 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15326 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15326 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15859 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15859 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16847 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17487 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17569 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18104 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18104 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18104 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27032 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09688 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09796 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09835 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-159 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10988 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 0.05025 | 108.18 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08489 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08497 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08498 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08523 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0853 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08547 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08551 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08565 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08567 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08571 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0858 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08589 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08591 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08592 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08594 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08594 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08595 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08596 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.086 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08604 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08605 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08606 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08607 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08609 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0861 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08617 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08644 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08687 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08696 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08712 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08714 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08725 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08761 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08761 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08774 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08779 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08781 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08792 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08845 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08845 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08848 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08856 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08879 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08924 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08993 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09319 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09412 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09604 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10402 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11078 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1128 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09865 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10663 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11339 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1154 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09881 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09889 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09894 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.099 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09911 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09922 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09924 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09931 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09936 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09948 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0999 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10007 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10071 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10085 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10182 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10223 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10345 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10465 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10696 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10916 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11439 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.14874 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15538 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15745 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09851 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09874 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09875 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09876 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09877 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09878 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09879 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0988 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09881 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09882 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09883 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09897 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.099 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09901 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09911 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09922 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09924 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09931 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09936 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09966 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0999 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.09992 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10007 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10071 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10085 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10096 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10182 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10223 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10345 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10465 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10696 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.10916 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11439 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.11588 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.14874 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15553 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15634 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15684 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.15745 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.12828 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13736 | 100.57 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.13736 | 100.57 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.1377 | 101.14 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17233 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.17629 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 105.86 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18655 | 106.45 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18681 | 107.23 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18681 | 107.23 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18705 | 106.66 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.18717 | 107.87 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 100.95 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.91 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.91 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 103.92 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 105.74 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07668 | 101.48 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 100.83 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.21 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 102.98 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 104.53 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.07923 | 102.37 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0802 | 104.71 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08127 | 118.26 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.08684 | 115.9 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.03 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.37 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.37 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 114.65 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 114.65 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 114.42 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.09013 | 114.86 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.0925 | 119.12 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 251 | 251 | 0.10331 | 125.72 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.37 | 524757 BETHEL_COL 3 115 524756 BETHEL_COL21 34.5 2 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.99 | 774381 GEN-2023-120 115 774382 G23-120XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 101.99 | GEN-2023-120_POI_525192_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 103.73 | 524757 BETHEL_COL 3 115 524755 BETHEL_COL11 34.5 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07641 | 106.35 | GEN-2014-040_POI_524746_Generator_outage | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07668 | 101.45 | 524909 ROOSEVELT 6 230 3WXFMR ABB LMM60042 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.04 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07718 | 101.45 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 103.25 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07828 | 104.94 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.07923 | 102.48 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0802 | 104.88 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08127 | 120.17 | P12:230:SPS:K37::1_TOLK_LAMB:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.08684 | 116.62 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.55 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.92 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09001 | 114.92 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 115.22 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09006 | 115.22 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09009 | 114.98 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.09013 | 115.44 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.0925 | 119.36 | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 251 | 251 | 0.10331 | 126.07 | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | Cumulative Impact | Upgrade the existing PLANTX 230/115 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1119 | 139.31 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15186 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15186 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15189 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15193 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15196 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15197 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15198 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15199 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15201 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15201 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15202 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15203 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15209 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1521 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15212 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15212 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15213 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15218 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15222 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15224 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15224 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15251 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15257 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15257 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15259 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15265 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15266 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15301 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15311 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15311 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15314 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1533 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15331 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15334 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15394 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15398 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15406 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15406 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15464 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15579 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15579 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1581 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15832 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15887 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15956 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.15956 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1633 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16562 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16841 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1717 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20155 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20168 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.20192 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.202 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.21015 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17966 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17979 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1798 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17985 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17996 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18003 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1806 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1808 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18088 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18165 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18201 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18266 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18329 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18335 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18472 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18515 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19004 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15973 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15979 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16098 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16135 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16562 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17466 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17818 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11603 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22291 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22324 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22435 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2245 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22456 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22469 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22474 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22595 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22628 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22629 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22646 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22651 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22685 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22783 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22816 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22825 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22841 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22847 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22848 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2301 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23078 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23083 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2319 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23285 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24205 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25113 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25198 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2663 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.38265 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41996 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.4214 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.42509 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22208 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24432 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.38232 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41955 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42097 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.42466 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10483 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17935 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17954 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17957 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17958 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17964 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17965 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17966 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17967 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17968 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17979 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1798 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17985 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17993 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17996 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18003 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18006 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18059 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1806 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1807 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18074 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1808 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18088 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18165 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18201 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18266 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18295 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18329 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18335 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18351 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18472 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18526 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1864 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19004 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19225 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20042 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20447 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20542 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21629 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.29756 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15973 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15979 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15992 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16098 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16244 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16562 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16754 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17466 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17818 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17902 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18849 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.28714 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10288 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10328 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10337 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-176 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.11581 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11599 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11599 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08535 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08542 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08543 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08568 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08569 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08576 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0861 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08612 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08612 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08617 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08621 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08625 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0863 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08634 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08635 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08635 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08636 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08638 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08639 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08639 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08639 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08639 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0864 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08641 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08645 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08645 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08645 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08647 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08649 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08651 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08653 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08654 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08655 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0866 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08661 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08663 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08687 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08689 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08694 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08694 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08697 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08698 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08732 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08732 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08745 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08745 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08756 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0876 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0877 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08806 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08806 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08819 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08819 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08823 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08826 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08835 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08835 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08835 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08893 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08893 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08893 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08901 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08956 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08956 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08996 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09003 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09041 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09041 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09041 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09041 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09154 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09402 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09462 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09655 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09655 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09655 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09655 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09655 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10465 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10465 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10465 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11138 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11138 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11138 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11338 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11338 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09916 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09916 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09916 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09916 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09916 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10725 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10725 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10725 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11398 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11398 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11398 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11599 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11599 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07101 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07241 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07241 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07242 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07244 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07244 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07244 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07244 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07244 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07247 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07248 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07256 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07261 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07267 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07268 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07278 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07289 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0729 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07297 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07302 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07313 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07332 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07332 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0734 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07355 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07355 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07355 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07355 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0736 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07423 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07454 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0746 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0746 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0746 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0751 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07563 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07853 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07896 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08013 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0822 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08668 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08816 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08816 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08816 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12783 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12798 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12798 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12798 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12798 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12888 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12888 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13049 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1306 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07101 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07217 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07241 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07241 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07242 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07243 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07244 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07244 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07244 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07245 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07246 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07247 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07248 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07249 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0725 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07264 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07267 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07268 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07278 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07289 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0729 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07297 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07302 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07332 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07332 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0734 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07355 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07355 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07355 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07355 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0736 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07423 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07454 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0746 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0746 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0746 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0751 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07563 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07853 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07896 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08013 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0822 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08668 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08816 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08816 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08816 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12798 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12798 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12798 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12798 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12888 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12888 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1302 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13049 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1306 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.07596 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08145 | 100.57 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08145 | 100.57 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08195 | 101.14 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.12286 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.1254 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13291 | 105.86 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13291 | 106.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13291 | 106.45 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13291 | 106.45 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13319 | 107.23 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13319 | 107.23 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13372 | 107.87 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13376 | 106.66 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.12419 | 139.31 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16415 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16415 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16418 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16422 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16425 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16426 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16427 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1643 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1643 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1643 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1643 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1643 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1643 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16431 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16431 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16431 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16431 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16432 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16438 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16438 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1644 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1644 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16441 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16447 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16451 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16453 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16453 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1648 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1648 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1648 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16486 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16486 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16488 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16488 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16489 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16495 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16496 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16521 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1653 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1653 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16544 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16563 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16565 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16566 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16624 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16627 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16636 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16636 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16695 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16817 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.16817 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17047 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17101 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17224 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17224 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17601 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17763 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17939 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17939 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17939 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17939 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18722 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21277 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21277 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21277 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21277 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21291 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21291 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21326 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.21354 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20565 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.20565 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0939 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16842 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16842 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16862 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16862 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16864 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16864 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16864 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16871 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16871 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16871 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16872 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16873 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16874 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16875 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16875 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16875 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16875 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16886 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16887 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16893 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16899 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16899 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16903 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16911 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16914 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16914 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16967 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16967 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16968 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16982 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16982 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16991 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16996 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17074 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17102 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17102 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1711 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17146 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17175 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17175 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17239 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17245 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17261 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17261 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17384 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17426 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17564 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17564 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17633 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19292 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1964 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20457 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20457 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27946 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15023 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15028 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15042 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15042 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1515 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15186 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15306 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15306 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15858 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15858 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16812 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17115 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17828 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17828 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26967 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11056 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2149 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21745 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21889 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21889 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2189 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21905 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21905 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21911 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21911 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21928 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21929 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2205 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22073 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22098 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22099 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22102 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22107 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22107 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22273 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22282 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22298 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22303 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22304 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22404 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22433 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2247 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22535 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22541 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22541 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22763 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23757 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24506 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.246 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26795 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.36755 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41012 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41112 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41468 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41468 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41468 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41468 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.21797 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24584 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.36723 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.40972 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41071 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41425 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41425 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41425 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41425 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0939 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16842 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16842 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16862 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16862 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16864 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16864 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16864 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16865 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16871 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16871 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16871 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16872 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16873 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16874 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16875 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16875 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16875 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16875 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16886 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16887 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16893 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16899 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16899 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16903 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16911 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16914 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16914 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16967 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16967 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16968 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16979 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16982 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16982 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16991 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.16996 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17074 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17102 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17102 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1711 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17146 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17175 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17175 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17239 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17245 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17261 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17261 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17384 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17454 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17564 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17564 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17633 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18198 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19292 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1964 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19732 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20457 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20457 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20457 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.27946 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15023 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15028 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15042 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15042 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1515 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15306 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15306 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15366 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15858 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15858 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16812 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17115 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17195 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17828 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17828 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17828 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.26967 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08848 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08886 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08886 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08886 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08886 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08886 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08886 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08886 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08886 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08987 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-178 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10194 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05133 | 141.57 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 279 | 330 | 0.05133 | 140.52 | Potential P4 Event - POI 515375_50 | Cumulative Impact | Upgrade the existing ELKCITY6 230/138 kV Transformer
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12298 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12298 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09115 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09123 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09124 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09147 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0915 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09156 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09157 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09173 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09177 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09191 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09193 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09193 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09195 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09195 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09197 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09202 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09206 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0921 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09214 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09215 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09215 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09215 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09217 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09218 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09218 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09219 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09219 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09219 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09219 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09219 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09219 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0922 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09221 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09222 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09225 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09225 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09225 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09226 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09227 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09227 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09229 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09231 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09232 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09232 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09232 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09233 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09233 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09236 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09237 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09239 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09241 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09242 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09243 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09266 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09266 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0927 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0927 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09273 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09273 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09275 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0931 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09327 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09338 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09338 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09341 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09346 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09352 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09383 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09383 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09385 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09385 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09385 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0939 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0939 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09391 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09393 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09468 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09476 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09512 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09512 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09606 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09647 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09647 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09647 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09647 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09681 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09681 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09848 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10081 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10283 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10299 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10299 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10299 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10299 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10299 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11321 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11321 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11321 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11845 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11845 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11845 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12037 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.12037 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1056 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1056 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1056 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1056 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1056 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11582 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11582 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11582 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12106 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12106 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12106 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12298 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.12298 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05601 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05601 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.06032 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07956 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05955 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05977 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.05979 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06249 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06249 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06252 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06256 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06259 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0626 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06261 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06264 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06264 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06264 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06264 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06264 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06265 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06265 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06266 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06266 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06266 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06266 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06273 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06273 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06273 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06274 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06276 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06282 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06286 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06289 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06289 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06315 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06317 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06317 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0632 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06325 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06325 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06325 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06325 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06325 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06325 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06336 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06341 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06346 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06383 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06404 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06449 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0645 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06472 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06475 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06483 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06483 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0657 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06736 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06736 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07318 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0737 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0737 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08454 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08454 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08454 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.08454 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.10859 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07236 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07236 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08223 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08839 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08839 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08859 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08859 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08861 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08861 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08861 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08868 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08868 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08868 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08869 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0887 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08871 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08872 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08885 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08886 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0889 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08892 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08892 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08902 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0891 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08915 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08915 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08969 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08969 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08976 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08985 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08985 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08986 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08986 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09008 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09015 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09025 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09054 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09054 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0908 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0912 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09183 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09184 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09261 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09267 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09284 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09284 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09459 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09459 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09713 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09713 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10715 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10715 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12958 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13722 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14685 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06306 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06306 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07166 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08071 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08076 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0809 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0809 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08243 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08243 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08465 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08465 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09338 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09338 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11292 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11958 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14171 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.05624 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.14219 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15063 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15147 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.15763 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16312 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16464 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16464 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16472 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16486 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16486 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16487 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16487 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16503 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16517 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16535 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16537 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16537 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16631 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16687 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16792 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16793 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16877 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16885 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16902 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16907 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.16909 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17147 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17154 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1716 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.1716 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.17553 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.19111 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2111 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.2425 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26426 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.30892 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31108 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31108 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31108 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31108 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.31204 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.17535 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24229 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24246 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.30861 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31076 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31076 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31076 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31076 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.31174 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07236 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07236 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.07236 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08223 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0872 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08839 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08839 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08859 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08859 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08861 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08861 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08861 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08862 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08868 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08868 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08868 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08869 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0887 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08871 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08872 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08873 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08885 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08886 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0889 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08892 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08892 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08902 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0891 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08915 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08915 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08969 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08969 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08976 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08985 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08985 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08986 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.08986 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09008 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09015 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09025 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09054 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09054 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0908 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.0912 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09183 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09184 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09261 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09267 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09284 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09284 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09459 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09713 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09713 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10715 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.10715 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.12958 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13018 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.13722 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.14685 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06306 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06306 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.06306 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.07166 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08071 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08076 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0809 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.0809 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08243 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08465 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.08465 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09338 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.09338 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11292 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11345 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.11958 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.14171 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.06785 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08208 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08234 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08234 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08234 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08234 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08234 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08234 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08234 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08234 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-184 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09441 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0721 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0721 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05005 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05005 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05008 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05022 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05025 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05025 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05046 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05046 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05046 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05046 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05097 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05144 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05152 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05405 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05405 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05405 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05405 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05405 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.05444 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06677 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06677 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06677 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06949 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.06949 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05666 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05666 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05666 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05666 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.05666 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06938 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06938 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.06938 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0721 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-188 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.0721 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11556 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11556 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08498 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08505 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08506 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08531 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08532 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08538 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08539 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08555 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0856 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08573 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08575 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08577 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08577 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0858 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08584 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08588 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08593 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08597 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08598 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08599 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08601 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08602 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08604 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08604 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08608 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0861 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0861 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0861 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08612 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08614 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08615 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08616 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08616 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08617 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08618 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08623 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08624 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08626 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08626 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08626 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0865 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08652 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08657 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0866 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08662 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08694 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08695 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08707 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08707 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0872 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08722 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08733 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08769 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08769 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08782 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08782 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08786 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08789 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08799 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08799 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08799 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08852 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08853 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08857 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08865 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08911 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08911 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08964 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08981 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09002 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09002 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09002 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09002 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09112 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09355 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09423 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09614 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09614 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09614 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09614 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09614 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10407 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10407 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10407 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11095 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11095 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11095 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11296 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11296 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09874 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09874 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09874 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09874 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.09874 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10668 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10668 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10668 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11355 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11355 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11355 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11556 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11556 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07055 | 139.3 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07141 | 132.94 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07141 | 133 | P22:345:OPPD:S3458 NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07142 | 133.01 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07142 | 138.87 | Potential P4 Event - POI 773600_4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07143 | 138.88 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07143 | 138.88 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07144 | 132.82 | 532792 FR2EAST7 345 588364 G16-153-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07144 | 132.87 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07145 | 132.62 | 514796 IODINE-4 138 515376 WWRDEHV4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07145 | 132.62 | 514796 IODINE-4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07145 | 132.92 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07146 | 132.81 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07146 | 132.83 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07146 | 132.85 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07147 | 132.88 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07147 | 132.88 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07148 | 133.45 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.45 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.59 | 659387 KUMMERDG-BE3 345 659390 PATENTGT-BE3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.61 | 655973 JDSNBTCN-MW4 230 659334 JUDSON__-BE4 230 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.81 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.81 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.84 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.84 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.84 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.86 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.9 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.9 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.91 | P12:069:GLHP:COLE-TURPIN-BEARD-ADAMS-JEFFERSON:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.93 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.94 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.95 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.96 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.96 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.96 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.96 | P23:500:EES-EAI:DELL:B8320::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.98 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.99 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.99 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.99 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 132.99 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133 | P12:EHV:EES::8ISES%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.01 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.01 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.04 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.04 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.05 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.05 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.05 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.06 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.06 | P11:HV:EES::1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.06 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.06 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.06 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.07 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.07 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.09 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.09 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.09 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.09 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.09 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.09 | P23:345:MEC:CBEC 908 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.1 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.1 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.11 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.11 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.11 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.11 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.15 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.18 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.18 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.19 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.19 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.21 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.21 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.28 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.3 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 133.47 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.76 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.88 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.24 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.42 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.43 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.91 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.91 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 138.67 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 138.67 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0715 | 133.04 | P23:500:EES-EAI:INDEP2:B6126 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07156 | 133.26 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07161 | 133.29 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07167 | 133.51 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07168 | 133.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07178 | 133.33 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07189 | 133.61 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07191 | 133.29 | P23:345:AEPW:PITTSBURG CB 3441A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07198 | 133.2 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07202 | 133.56 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07214 | 133.57 | P42:345:OKGE:SB_SEOL7385:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07233 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07233 | 133.67 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07248 | 133.93 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07254 | 134.9 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07254 | 134.91 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07254 | 135.3 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07254 | 135.32 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07266 | 136.02 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07322 | 138.51 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07352 | 137.34 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07361 | 136.22 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07361 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07361 | 136.3 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07428 | 139.38 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07461 | 137.06 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07719 | 137.63 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07818 | 135.99 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07932 | 138.61 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08143 | 140.79 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08548 | 163.65 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08696 | 157.16 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08696 | 157.17 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08696 | 157.17 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12881 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13273 | 161.82 | Potential P4 Event - POI 527656_9 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13289 | 161.31 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13289 | 161.31 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13289 | 164.87 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13289 | 164.87 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13377 | 163.21 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13377 | 163.21 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1352 | 163.83 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07055 | 142.25 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07118 | 134.6 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07141 | 134.9 | P23:345:WERE:JEC-345-16:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07141 | 134.92 | P13:345:OPPD:NEBCTY2G:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07142 | 134.93 | P23:345:WERE:JEC-345-20:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07142 | 142.83 | Potential P4 Event - POI 773600_1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07143 | 134.94 | P11:345:WERE:JECU3-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07143 | 142.91 | Potential P4 Event - POI 773600_7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07143 | 142.91 | Potential P4 Event - POI 773600_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07144 | 134.83 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07145 | 134.63 | 514787 DEWEY 4 138 515533 REDCLFT4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07145 | 134.63 | 514789 MENOTAP4 138 514790 IMO 4 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07145 | 134.82 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07146 | 134.83 | 532853 LAWHILL6 230 532854 LEC U5 6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07147 | 134.83 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07147 | 134.83 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07148 | 135.25 | P23:345:WERE:WOLF-345-50:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.3 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.64 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.82 | 542966 WGARDNR5 161 543105 BULLCRK5 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.82 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.83 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.83 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.86 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.87 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.89 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.92 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.92 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.92 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.93 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.93 | 300103 5NEWMAD 161 301536 5NEWMADGSU1 161 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.93 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.93 | P23:345:XEL:8H14 PRI | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.93 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.94 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.94 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.95 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.96 | 344884 7LABADIE1 345 344894 1LAB G1 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.96 | 344885 7LABADIE2 345 344895 1LAB G2 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.96 | 344886 7LABADIE3 345 344896 1LAB G3 20.0 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.96 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.97 | P12:115:GLHP:YROAD-REDDEVIL-115-KV:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC31G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.97 | P13:24-345:XEL:AUTO-SINGLE:SHERC32G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.97 | P23:345:XEL:8N22 SHC | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.97 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.98 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.98 | P23:345:MEC:LOUISA 964 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.99 | P23:345:MEC:CBEC 905 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 134.99 | P23:345:MEC:LOUISA 954 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.01 | P13:24-161:ALTW:AUTO-SINGLE:OTTUMW1G:OTTUMWA5:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.02 | P11:24:ALTW:AUTO-SINGLE:OTTUMW1G:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.02 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.02 | P23:500:EES-EAI:WH_BLF:B7942 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.03 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.03 | P42:345:NPPD:BKR-CPR-3310:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.04 | P11:26:EES-EAI:INDEP2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.04 | P11:26:EES-EAI:INDEP2:1:D401 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.04 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.04 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.04 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.05 | P11:22:NPPD:COOPER1G:1:983:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.05 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.05 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.06 | ASGI-2021-001_POI_766031_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.06 | ASGI-2023-001_POI_528252_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.06 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.06 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.07 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.09 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.09 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.1 | P11:21:EES:RVB:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.1 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.1 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.11 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.11 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.14 | P11:25:EES:WATERF:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.14 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.14 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.21 | P12:EHV:EES::7CALAWY 1:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.23 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.27 | P11:345:WERE:WOLFU1-GEN:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 135.34 | 587991 G16-121XFMR1 34.5 587990 GEN-2016-121 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 137.63 | 773601 GEN-2023-081 345 773602 G23-081XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 137.79 | 773601 GEN-2023-081 345 773608 G23-081XFMR3 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 137.99 | 775661 GEN-2023-184 115 775662 G23-184XFMR1 34.5 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 138.62 | 776000 G23-201-TAP 345 776001 GEN-2023-201 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 138.62 | GEN-2023-201_POI_776000_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 139.4 | 776700 G23-236-TAP 345 776701 GEN-2023-236 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 139.4 | GEN-2023-236_POI_776700_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 142.7 | 773600 G23-081-TAP 345 773601 GEN-2023-081 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07149 | 142.7 | GEN-2023-081_POI_773600_Generator_outage | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.0715 | 134.97 | P23:345:KCPL-WERE:237LACYGNE-R1-6:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07164 | 135.31 | P42:345:OKGE:SB_BVTY7387:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07167 | 135.72 | P23:345:SUNC:BU_BRK688:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07168 | 135.59 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07178 | 135.19 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07189 | 135.54 | P42:345:OKGE:SB_BAER7318:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07191 | 135.05 | P42:345:AEPW:PITTSBURG CB 3441A NBTB+FAULT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07198 | 134.98 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07202 | 135.28 | P23:345:AEPW:OKLAUNION CB 3401A NBTB:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07233 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07233 | 135.31 | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07248 | 135.66 | 515458 BORDER 7 345 762216 G17-151TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07254 | 136.85 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07254 | 136.86 | 512084 WELLGS4 138 512105 SHAM 4WT 138 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07254 | 137.23 | P13:69-115:AEPW:SHAM 2WT:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07254 | 137.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07266 | 137.76 | 515458 BORDER 7 345 774180 G23-110-TAP 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07322 | 140.57 | 523267 PRINGLE 6 230 3WXFMR ENRCO13617-1 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07352 | 139.06 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07361 | 137.62 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07361 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07361 | 137.63 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07428 | 141.48 | Potential P4 Event - POI 515458_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07461 | 139.08 | P12:115:SPS:W10_1_HITCH_HANSFRD:::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07719 | 138.3 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07818 | 138.08 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.07932 | 140.18 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08143 | 142.88 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08548 | 165.72 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08696 | 159.05 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08696 | 159.06 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.08696 | 159.06 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.12881 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13289 | 165.89 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13289 | 165.89 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13289 | 169.93 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13289 | 169.93 | Potential P4 Event - POI 527656_8 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13377 | 167.9 | Potential P4 Event - POI 527656_13 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13377 | 167.9 | Potential P4 Event - POI 527656_14 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.13473 | 166.55 | Potential P4 Event - POI 527656_10 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.1352 | 167.97 | Potential P4 Event - POI 527656_0 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.08927 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09788 | 100.57 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09788 | 100.57 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.09833 | 101.14 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13066 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.13517 | 106.67 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14468 | 105.86 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14468 | 106.45 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14468 | 106.45 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14468 | 106.45 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14496 | 107.23 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14496 | 107.23 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14539 | 106.66 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.14543 | 107.87 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.13423 | 139.31 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17419 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17419 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17422 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17426 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17429 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1743 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17431 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17434 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17434 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17434 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17434 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17434 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17434 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17435 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17435 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17435 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17435 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17436 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17442 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17442 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17444 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17444 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17445 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17451 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17454 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17457 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17457 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17484 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17484 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17484 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17489 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17489 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17492 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17492 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17498 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.175 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17523 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17533 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17533 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17547 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17567 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17567 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17568 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17627 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.1763 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17634 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17639 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17639 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17696 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17817 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.17817 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18117 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18176 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18217 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18217 | 148.81 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18729 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18791 | 149.61 | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18908 | 152.28 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18908 | 159.07 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18908 | 161.78 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.18908 | 163.27 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.19695 | 163.49 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22797 | 162.85 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22797 | 164.73 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22797 | 164.73 | Potential P4 Event - POI 527656_11 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22797 | 164.74 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22811 | 165.04 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22811 | 165.04 | Potential P4 Event - POI 527656_14 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.22841 | 165.64 | Potential P4 Event - POI 527656_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.2286 | 164.89 | Potential P4 Event - POI 527656_10 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22751 | 109.73 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 478 | 553 | 0.22751 | 110.69 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK7 345/230 kV Transformer 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09794 | 113.29 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17246 | 109.05 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17246 | 109.05 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17265 | 108.48 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17265 | 108.48 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17267 | 108.48 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17267 | 108.65 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17267 | 108.87 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17268 | 109.03 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.39 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.45 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.46 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.46 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.48 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.64 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.64 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.67 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.67 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.7 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.79 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.82 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.82 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.87 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.89 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.9 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.9 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.92 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.94 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.94 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.99 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.99 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.04 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.14 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.15 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.15 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.16 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.17 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.17 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.17 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.18 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.18 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.18 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.22 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.22 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.23 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.24 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.26 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.3 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.37 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.4 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.49 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.49 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.49 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.49 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.49 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.53 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.53 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.53 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.58 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.58 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.59 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.69 | 776721 GEN-2023-237 345 776722 G23-237XFMR1 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.69 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.69 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.75 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.75 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.78 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 110.66 | 526284 PLANTERS 2 69.0 526297 LUBBCK_EST 2 69.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 110.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 111.04 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 111.24 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 113.28 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17274 | 108.45 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17274 | 108.45 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17274 | 108.45 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17275 | 108.69 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17276 | 108.76 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17277 | 108.77 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17278 | 108.28 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17278 | 108.82 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17278 | 108.9 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17278 | 108.9 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1729 | 108.95 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1729 | 108.98 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17296 | 108.99 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17302 | 109.13 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17302 | 109.25 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17307 | 109.44 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17314 | 108.99 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17317 | 109.39 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17317 | 109.39 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1737 | 111.14 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1737 | 111.14 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17371 | 111.09 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17381 | 110.68 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17381 | 110.68 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17385 | 110.71 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17385 | 110.82 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17393 | 110.1 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17399 | 110.77 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17477 | 112.1 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17502 | 111.03 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17502 | 111.04 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17513 | 111.42 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17545 | 113.28 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17574 | 112.35 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17574 | 112.35 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 115.8 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17647 | 115.86 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17662 | 116.15 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17662 | 116.15 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17781 | 116.25 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17827 | 117.38 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1796 | 117.14 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1796 | 117.29 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18026 | 118.97 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18583 | 121.61 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18583 | 122.52 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19662 | 124.23 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19976 | 138.42 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 128.24 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 131.95 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 135.41 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 135.88 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 138.79 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 139.6 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 139.63 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 140.37 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21243 | 119.52 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21243 | 119.53 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28614 | 182.51 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 100.92 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15378 | 100.97 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15392 | 101.22 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15392 | 101.22 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15496 | 101.31 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15535 | 102.3 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 102.08 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 102.22 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15709 | 103.69 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16195 | 105.99 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16195 | 106.77 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17135 | 108.27 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17408 | 120.63 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 111.76 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 115 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 118.01 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 118.42 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 120.96 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 121.66 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 121.68 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 122.33 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18512 | 104.17 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18512 | 104.17 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27612 | 176.23 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.11329 | 102.88 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.21856 | 103.59 | 527896 HOBBS_INT 7 345 776700 G23-236-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.01 | P11:25:EES:WATERF:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.01 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.01 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.04 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.04 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.04 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.08 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.08 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.08 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.18 | 525192 KRESS_INT 3 115 3WXFMR ENRCO 136155 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 100.58 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 101.09 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 101.65 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22018 | 102.88 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22162 | 101.33 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22162 | 101.41 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22162 | 101.41 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22176 | 101 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22176 | 101 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22183 | 101.02 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22183 | 101.13 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22199 | 100.53 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22201 | 101.09 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22322 | 102.35 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22341 | 102.51 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22366 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22367 | 101.38 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22374 | 101.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22375 | 101.85 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22375 | 101.85 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22544 | 105.51 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22552 | 105.56 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22569 | 104.19 | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22574 | 104.06 | P42:345:SPS:FINNEY_OR70_SLG:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22575 | 105.82 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22624 | 102.19 | 527669 CROSSROADS 9 765 528014 PHANTOM 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22668 | 104.24 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22735 | 105.74 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22805 | 107.18 | Potential P4 Event - POI 523823_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22811 | 106.47 | Potential P4 Event - POI 523823_11 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.22811 | 106.97 | P42:345:SPS:CARPENTER:OR335_SLG::EHV: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.23026 | 107.16 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.24004 | 111.23 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25072 | 103.71 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.25165 | 104.54 | Potential P4 Event - POI 527656_13 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.26999 | 121.93 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.37384 | 154.86 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41505 | 188.13 | Potential P4 Event - POI 560022_7 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41626 | 187.42 | Potential P4 Event - POI 560022_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41988 | 183.57 | Potential P4 Event - POI 525832_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41988 | 183.59 | Potential P4 Event - POI 525832_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41988 | 188.53 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 1250 | 1250 | 0.41988 | 195.61 | Potential P4 Event - POI 560022_8 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.22023 | 101.96 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.24771 | 111.77 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.37352 | 155.38 | Potential P4 Event - POI 525832_5 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41465 | 188.56 | Potential P4 Event - POI 560022_3 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41583 | 187.81 | Potential P4 Event - POI 560022_1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41945 | 184.02 | Potential P4 Event - POI 525832_0 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41945 | 184.11 | Potential P4 Event - POI 525832_6 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41945 | 188.95 | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 1250 | 1250 | 0.41945 | 196.06 | Potential P4 Event - POI 560022_4 | Cumulative Impact | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.09794 | 114.16 | GEN-2023-237_POI_560022_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17246 | 109.42 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17246 | 109.42 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17265 | 108.86 | P12:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17265 | 108.86 | P12:345:MEC:SYCAMORE-BONDURANT-GDMEC | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17267 | 108.86 | 508585 TENRUSK7 345 509241 CROCKET7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17267 | 109.03 | 547501 RIV453 5 161 547503 RIV452T 5 161 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17267 | 109.24 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17268 | 109.4 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.77 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.83 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.84 | 508831 DIANA 4 138 509639 DIANASW4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.84 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 108.86 | 508351 PERDUE 4 138 509603 BIGSAND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.02 | 345610 4RIVMIN 2 138 345840 4TAUM S 2 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.02 | 346004 7GOSCK 345 348770 7GOOS_CRK 345 Z | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.07 | 588761 G17-033XFMR1 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.07 | 588765 G17-033XFMR2 34.5 588760 GEN-2017-033 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.08 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.17 | 345667 7RUSH 1 345 345670 1RUSH G1 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.19 | P13:138:EES:LC:T1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.19 | P13:138:EES:LC:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.25 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.27 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.27 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.27 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.29 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.31 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.31 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.36 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.36 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.41 | P11:18:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.51 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.52 | P11:HV:EES::1ISES U1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.52 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.53 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.54 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.54 | P11:26:EES:NINEMI:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.54 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.54 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.55 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.55 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.59 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.59 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.6 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.6 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.62 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.66 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.73 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.77 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.85 | P11:21:EES:RVB:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.85 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.85 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.85 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.85 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.89 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.89 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.9 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.95 | P11:25:EES:WATERF:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.95 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 109.95 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 110.17 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 110.17 | 776721 GEN-2023-237 345 776728 G23-237XFMR3 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 110.17 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 110.25 | 762460 GEN-2018-015 345 776541 GEN-2023-228 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 110.25 | GEN-2023-228_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 110.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 111.11 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 111.53 | 525828 TUCO_INT 3 115 3WXFMR DS F78800913 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 111.68 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17269 | 114.16 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17274 | 108.84 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17274 | 108.84 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17274 | 108.84 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17275 | 109.07 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17276 | 109.14 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17277 | 109.14 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17278 | 108.67 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17278 | 109.19 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17278 | 109.27 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17278 | 109.27 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1729 | 109.33 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1729 | 109.35 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17296 | 109.29 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17302 | 109.5 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17302 | 109.62 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17307 | 109.8 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17314 | 109.36 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17317 | 109.75 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17317 | 109.75 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1737 | 111.45 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1737 | 111.45 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17371 | 111.43 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17381 | 111 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17381 | 111 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17385 | 111.03 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17385 | 111.14 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17393 | 110.42 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17399 | 111.06 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17477 | 112.34 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17502 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17502 | 111.41 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17513 | 111.7 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17545 | 113.69 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17574 | 112.76 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17574 | 112.76 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1764 | 116 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17647 | 116.05 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17662 | 116.33 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17662 | 116.33 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.17781 | 116.57 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1792 | 111.13 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1796 | 117.18 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.1796 | 117.33 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18026 | 119.68 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18583 | 121.98 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.18583 | 122.9 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19662 | 124.63 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.19976 | 141.25 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 130.11 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 134.46 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 137.98 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 138.46 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 141.54 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 142.35 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 142.4 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.20069 | 143.16 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21243 | 118.53 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21243 | 120.63 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.21243 | 120.63 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 675 | 675 | 0.28614 | 182.77 | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15373 | 101.1 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15378 | 101.14 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15392 | 101.39 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15392 | 101.39 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15496 | 101.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 102.12 | POI 515800_22 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15652 | 102.26 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.15709 | 104.3 | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16195 | 106.31 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.16195 | 107.11 | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17135 | 108.62 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.17408 | 123.1 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 113.4 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 117.19 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 120.26 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 120.67 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 123.35 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 124.06 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 124.1 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.1749 | 124.76 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18512 | 103.3 | P42:345:SPS:CROSSROADS_6R45_SLG:::EHV: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18512 | 105.13 | 525549 TOLK 7 345 527656 CROSSROADS 7 345 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.18512 | 105.13 | P12:345:SPS:J15::1_XRDS_TOLK:: | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 675 | 675 | 0.27612 | 176.5 | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | Cumulative Impact | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08934 | 119.45 | Potential P4 Event - POI 525832_7 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08973 | 106.79 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08973 | 109.48 | Potential P4 Event - POI 764945_0 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08973 | 114.6 | Potential P4 Event - POI 764945_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08973 | 115.27 | Potential P4 Event - POI 764945_1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08973 | 119.86 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08973 | 120.54 | Potential P4 Event - POI 525832_2 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08973 | 120.55 | Potential P4 Event - POI 525832_9 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.08973 | 121.12 | P43:345:SPS:TUCO:NR50_SLG::EHV: | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.09089 | 111.33 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-195 | FROM->TO | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 426 | 426 | 0.10513 | 112.72 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1199 | 108.49 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1199 | 108.49 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08852 | 105.19 | 539803 IRONWOOD7 345 539815 IRONWOOD WF7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08859 | 106.48 | P45:345:UMZB:# 2507 #:: LRS IN NE. LRS BUS FAULT:EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0886 | 106.5 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08884 | 103.66 | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08886 | 106.75 | P11:24:NPPD:GENTLM2G:2:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08892 | 106.39 | P11:23:NPPD:GENTLM1G:1:757:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08893 | 104.31 | 539815 IRONWOOD WF7 345 539831 WESTPLN7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08909 | 103.96 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08914 | 103.86 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08927 | 103.86 | 652537 WHITE 3 345 659286 DEERCREK-BE3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 104.29 | 659101 ANTELOPE-BE3 345 659107 ANTELP_2-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08929 | 104.3 | 659101 ANTELOPE-BE3 345 659103 ANTELP_1-BEG 23.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08931 | 104.25 | P11:18:HAST::EGYCTR2G WEC2:LOSS OF WEC 2 GEN:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08931 | 104.25 | P13:18-115:HAST:::EGYCNTR7 XFMR G2WEC 2 GSU:HV:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08934 | 103.62 | 652568 GROTONSOUTH7 115 659275 GROTON_G-BE7 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08938 | 103.95 | 542957 IAT G1 1 24.0 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08942 | 104.21 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08947 | 103.7 | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.19 | 338471 2TRENTON! 69.0 337372 3TRENTON! 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.19 | P12:LV:EES::2MOSSVILLE!:2MAPLEWOOD:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.22 | 335280 4JENNINGS1! 138 3WXFMR 4JENNINGS1! 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.36 | P11:345:AMMO::CALLAWAY:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.65 | 659800 GRANTNB_-TS7 115 775041 GEN-2023-153 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.87 | 528025 RDRUNNER 3 115 528040 BATTLE_AXE 3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.87 | 659268 RCDC.DUM-BE4 230 659271 RCDC.E__-BE4 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.87 | 659271 RCDC.E__-BE4 230 659376 DRYCREEK-BE4 230 Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.87 | 774121 GEN-2023-107 345 774122 G23-107XFMR1 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.87 | 774121 GEN-2023-107 345 774125 G23-107XFMR2 34.5 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.94 | 672688 PASQUA 4 230 673390 FUT-PQ1X 18.0 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 103.95 | P21:115:XEL:AUTO-SINGLE:FARIBALTP7:FARIBALTGEN:Z | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.01 | P13:NBEC#1 GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.1 | P21:115:XEL:AUTO-SINGLE:COLVILL7:CANONFLSG7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.18 | P13:SH902T GSU | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.28 | P12:230:UMZW:# 3617 #:: FT IN SD. FT-BG2 BRANCH FAULT:HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.31 | GEN-2023-172_POI_531449_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.65 | GEN-2023-107_POI_531465_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.66 | 640252 KEYSTON3 345 774301 GEN-2023-116 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.71 | 531504 CIMWD2 7 345 3WXFMR CIMRNWND2 MPT 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.71 | GEN-2010-009_POI_531501_Generator_outage | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.75 | P11:115:XEL:HBR #6 7 8 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.75 | P13:20-230:OTP:AUTO-SINGLE:CENTER2G:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.75 | P21:230:OTP:AUTO-SINGLE:SQBUTTE4:YNG24:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.8 | 528025 RDRUNNER 3 115 528231 AGAVE_RHIL23 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.87 | P22:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 104.87 | P23:345:OPPD:S3458 NEBCTY1G:LT::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.04 | P11:22:XEL:AUTO-SINGLE:MNTCE31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.14 | P23:345:XEL:8N17 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC31G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.27 | P11:24:XEL:AUTO-SINGLE:SHERC32G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.33 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.37 | P13:345-24:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF33G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.37 | P23:345:MEC:CBEC 908 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.49 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.49 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.51 | P11:22:GRE:AUTO-SINGLE:GRE-COAL42G:2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.53 | P13:345-24:MEC:AUTO-SINGLE:RAUN3:NEAL4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.64 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.65 | P11:24:MEC:AUTO-SINGLE:NEAL4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.72 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.74 | P11:345:MEC-NPPD:COOPER 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.88 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 105.91 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0895 | 111.31 | 531447 HOLCGEN1 22.0 531448 HOLCOMB3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08951 | 103.2 | P12:HV:EES::6FR_BRANCH:6SLIDEL!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08951 | 104.74 | P23:345:XEL:8H17 PRI AS | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08951 | 105.15 | P23:345:XEL:8N22 SHC | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08951 | 105.63 | P23:345:MEC:CBEC 905 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08952 | 103.33 | P12:EHV:EES::8HARTBRG%:8RHODES%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08953 | 103.48 | P21:345:CE-ALTW:AUTO-SINGLE:QUAD13-11:ROCKCK3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 103.3 | 300950 5JASPER 161 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 103.41 | 506935 FLINTCR7 345 512750 TONECE7 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 103.46 | P12:EHV:EES::8STERLING%:8EL DORADO%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 103.48 | P12:EHV:EES::8WELLS%:8WEBRE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 103.92 | P12:500:EES-EMI:B_WLSN:PERVIL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 103.92 | P12:EHV:EES::8BXTRWILSON%:8PERRYVILLE%:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08955 | 103.97 | P23:500:EES-EMI:B_WLSN:J2233 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08956 | 103.26 | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08956 | 103.62 | P13:345-230:CLEC::DOLHILL7:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08957 | 104.56 | P23:345:MEC:LOUISA 964 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08958 | 103.43 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08961 | 103.92 | P12:EHV:EES::8W.MEMPHIS%:8BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08961 | 104.02 | P12:HV-EHV:EES::8W.MEMPHIS%:8FREEPORTTN%:4BHAM STEEL:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08962 | 103.51 | 345230 7MONTGMRY 345 345992 7SPENCER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08963 | 104.19 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08964 | 103.93 | P23:345:AMMO::MAYWOOD:V33:: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08964 | 104.29 | P23:500:EAI-TVA:NBF_WEST M~1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08966 | 104.28 | P23:500:EES-EAI:KEO:B4931 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08967 | 103.85 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08968 | 104.21 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08968 | 104.21 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08969 | 103.53 | P21:345:MEC:AUTO-SINGLE:BONDRNT3:MNTZUMA3:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08969 | 103.72 | P23:345:ITCM-MEC:MNTZUMA3 901-902-903:IA-SW | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0897 | 103.77 | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08972 | 104.04 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08975 | 103.96 | P12:EHV:EES::CLARKSV7!:MUSKOGE7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08976 | 105.27 | P23:500:EES-EAI:KEO:B4921 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08978 | 105.48 | P23:500:EES-EAI:KEO:B4941 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08979 | 103.57 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.08979 | 104.43 | P12:EHV:EES::CHAMSPR7!:CLARKSV7!:1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09002 | 103.64 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09004 | 104.27 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09008 | 104.71 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09008 | 104.71 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09011 | 104.64 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09012 | 104.3 | P12:345:WERE:VIOL-WICH-345:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09013 | 104.04 | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09047 | 104.44 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09067 | 104.54 | P12:345:AEPW-OKGE:PITTSB-7:SEMINOL7::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09068 | 104.7 | P13:138-230:AEPW:ELKCTY-4:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09068 | 104.71 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09079 | 111.68 | Potential P4 Event - POI 523823_1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09081 | 106 | P12:345:OKGE:BKRBKR357_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09096 | 104.05 | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0912 | 104.72 | 514881 SPRNGCK7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0912 | 104.73 | 514803 SOONER 7 345 587804 G16-119-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0913 | 104.85 | P23:345:AEPW:PITTSBURG CB 3425A NBTB:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.0913 | 104.85 | P42:345:AEPW:PITTSBURG CB 3425A NBTB+FAULT:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09132 | 104.84 | 515045 SEMINOL7 345 588839 FIREWHL-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09134 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09134 | 105.45 | 560100 CRAWFISH765 765 560104 CDSEMMID 765 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09134 | 105.45 | 560101 SEMINOLE765 765 560104 CDSEMMID 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09135 | 106.71 | 515543 RENFROW7 345 763421 G18-128-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09207 | 106.03 | P12:345:OKGE:BKRBKR44:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09215 | 105.86 | P12:345:OKGE:BKRBKR44_2:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09229 | 106.65 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 2 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09229 | 106.7 | 515375 WWRDEHV7 345 560071 G16-003-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09332 | 109.43 | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09372 | 107.32 | 531391 PIONEER3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09372 | 107.46 | P12:115:SUNC:PIONEER-HUGOTON:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09372 | 107.57 | 531481 HUGOTON3 115 531483 GRANTTP3 115 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09372 | 109.51 | P12:115:SUNC:HUGOTON-WALKEMEYER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09517 | 104.64 | 526936 YOAKUM 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09517 | 105.34 | 525832 TUCO_INT 7 345 764945 G20-067-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09541 | 108.97 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09803 | 111.96 | Potential P4 Event - POI 515852_5 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.09918 | 109.15 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10006 | 120.22 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10006 | 120.23 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10006 | 120.23 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10006 | 120.23 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.10006 | 120.23 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1092 | 124.48 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1092 | 124.48 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.1092 | 124.48 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11533 | 126.32 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11533 | 126.32 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11533 | 126.32 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11729 | 135.92 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 956.1 | 956.1 | 0.11729 | 135.92 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10267 | 106.45 | P12:115:SUNC:WALKEMEYER-HARBINGER:::HV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10267 | 106.46 | 531510 HARBNGR3 115 3WXFMR HARBGR345 1 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10267 | 106.46 | P12:345:SUNC:CARPENTER-HARBINGER::523823-531512(Z1):EHV: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10267 | 106.46 | Potential P4 Event - POI 523823_10 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.10267 | 106.46 | Potential P4 Event - POI 523823_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11181 | 110.51 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11181 | 110.51 | Potential P4 Event - POI 515554_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11181 | 110.51 | Potential P4 Event - POI 515677_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11794 | 112.81 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11794 | 112.81 | Potential P4 Event - POI 515375_23 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.11794 | 112.81 | Potential P4 Event - POI 515852_0 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1199 | 122.53 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 950 | 950 | 0.1199 | 122.53 | Potential P4 Event - POI 515852_9 | Cumulative Impact | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05687 | 188.65 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 516 | 559 | 0.05687 | 190.26 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | XFR-Potter County 345/230 kV Ckt1 & Ckt2
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 430 | 430 | 0.05993 | 111.79 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 456 | 456 | 0.07811 | 115.99 | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | Cumulative Impact | Rebuild the existing NEWHART to PLANTX 230 kV line
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06177 | 143.07 | 526935 YOAKUM 6 230 775140 G23-158-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06287 | 139.19 | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06313 | 138.87 | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06602 | 135.64 | P23:345:AEPW:RIVERSIDE CB 3429A NBTB:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06602 | 135.64 | P42:345:AEPW:RIVERSIDE CB 3429A NBTB+FAULT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06605 | 135.15 | 508298 LYDIA 7 345 776060 G23-204-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06609 | 135.16 | 508072 NWTXARK7 345 776220 G23-212-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06612 | 135.07 | 338056 CHALKBLUFFPV 500 338162 8W.MEMPHIS% 500 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.02 | 562727 LESBIA 115 562728 SANJONTAP 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.07 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.14 | P11:22:GRE:AUTO-SINGLE:GRE-COAL41G:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.14 | P11:26:XEL:AUTO-SINGLE:SHERC33G:3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL41G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.15 | P13:22-230:GRE:AUTO-SINGLE:GRE-COAL42G:GRE-COALCR4:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.15 | P13:26-345:XEL:AUTO-SINGLE:SHERC33G:SHERCO3:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.17 | P23:345:XEL:8N8 MNN | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.38 | P12:LV:EES::6CALPBOG:1ICALBOG2!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.44 | 336184 6STCHAR 1B 230 336187 1J396SCPS 1B 21.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.47 | P13:138:EES:LC:T1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.47 | P13:138:EES:LC:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.48 | P23:500:EES:PERRYVILLE:R7372::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.49 | 300046 7NEWMAD 345 301537 7NEWMADGSU2 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.52 | 336185 6STCHAR 1C 230 336188 1J396SCPS 1C 18.0 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.52 | 336185 6STCHAR 1C 230 336190 6GYPSY% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.52 | 338187 8DELL% 500 338340 8CC_DELL 500 Z1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.52 | P11:EHV:EES::1FRNTR 1!:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.55 | 335185 6NELSN_U7 ST 230 335182 1J484LCPS ST 18.0 3 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.55 | 335185 6NELSN_U7 ST 230 335190 6NELSON% 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.57 | P23:500:EES:SANS SOUCI:B3925::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.59 | P13:230,22:CLEC::G2RODEMR::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.62 | P11:18:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.62 | P23:500:EES:PERRYVILLE:R3779::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.7 | P11:EHV:EES::1ISES U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.7 | P11:EHV:EES::1TRACTBEL C1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.7 | P13:230,22:CLEC::G3MADISN::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.7 | P13:230:EES:NINEMI:AT4 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.72 | P11:26:EES:NINEMI:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.72 | P12:LV-HV:EES::69MILE%:1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.72 | P13:230:EES:NINEMI:AT5 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.73 | P11:22:CLEC:RODEMR1:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.73 | P11:26:EES:NINEMI:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.73 | P11:HV:EES::1NMIL U5!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.75 | P12:EHV:EES::8WHT BLUFF%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.75 | P13:500:EES-EAI:WH_BLF:ST2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.76 | P11:26:EES-EAI:WH_BLF:1:D388 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.77 | P12:EHV:EES::8STERLING2%:8OUACHITA%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.78 | P11:26:EES-EAI:WH_BLF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.83 | P13:345,24:CLEC::G1DOLHILL::1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.86 | P12:EHV:EES::8ANO%:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.89 | P11:22:EES-EAI:ARK_NU:1:D395 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.95 | P12:230-21:EES:FCY:RVB | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.95 | P12:EHV:EES::8ANO%:1(1) | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.95 | P12:HV:EES::6FANCY_PT%:6RIVER_BEND:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.95 | P12:LV-HV:EES::6FANCY_PT%:1RVR_BND_G1!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.95 | P13:500:EES-EAI:ARK_NU:T2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.98 | P11:22:EES-EAI:ARK_NU:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 135.98 | P11:EHV:EES::1ANO U2:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 136 | P11:HV:EES::1LEWIS_U3 ST:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 136.02 | P11:25:EES:WATERF:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 136.02 | P11:HV:EES::1WAT U3!:1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 136.02 | P13:230:EES:WATERF:T6:T7 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 136.24 | 776721 GEN-2023-237 345 776725 G23-237XFMR2 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 136.24 | 776721 GEN-2023-237 345 776731 G23-237XFMR4 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 136.3 | GEN-2018-015_POI_762467_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 136.47 | 768620 G23-008-TAP 230 768621 GEN-2023-008 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 136.47 | 768621 GEN-2023-008 230 772142 G23-008XFMR1 34.5 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 136.47 | GEN-2023-008_POI_768620_Generator_outage | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 137.36 | 762460 GEN-2018-015 345 762467 G18-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06613 | 139.3 | 560022 CRAWFISH_DR 345 776721 GEN-2023-237 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06614 | 135.15 | 542962 IAT G2 1 24.5 542982 IATAN 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06617 | 135.15 | P13:345:OPPD:NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06617 | 135.15 | P22:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06617 | 135.15 | P23:345:OPPD:S3458 NEBCTY1G:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06617 | 135.16 | 539815 IRONWOOD WF7 345 3WXFMR 345/34.5/13 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06617 | 135.39 | 539801 THISTLE7 345 3WXFMR THISTLE T1 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06617 | 135.44 | 542981 LACYGNE7 345 766261 G20-007-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06618 | 135.45 | 640065 AXTELL 3 345 640312 PAULINE3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06619 | 135.02 | 659118 LRS_1___-MBG 24.0 659131 LARAMIE_-MB3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06619 | 135.49 | 514788 GLASMTN4 138 520999 MOORLND4 138 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06619 | 135.56 | 539679 GRTBEND6 230 768280 G22-065-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06619 | 135.56 | 539695 SPEARVL6 230 763850 G19-053-TAP 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06625 | 135.63 | 514803 SOONER 7 345 560056 G15066_T 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06625 | 135.65 | P13:69-138:AEPW:SHAM 2WT:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06625 | 135.73 | 512107 SHAM 3WT 115 523811 MCLEAN 3 115 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06626 | 135.61 | P23:345:WERE:WICH-345-50:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06629 | 135.62 | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06634 | 136 | 560082 G16-050-TAP 345 640065 AXTELL 3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06638 | 135.63 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06641 | 135.96 | P23:345:WERE:BUFF-345-534:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06641 | 135.96 | P23:345:WERE:BUFF-345-543:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06669 | 137.43 | 531451 MINGO 7 345 531465 SETAB 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06669 | 137.43 | P12:345:SUNC:MINGO-SETAB::531451-531465(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0667 | 137.34 | 531501 BUCKNER7 345 765911 G21-068-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0667 | 137.9 | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06676 | 137.04 | P12:345:SUNC:HOLCOMB-BUCKNER::531449-531501(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06676 | 137.04 | P23:345:SUNC:BU_BRK482:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06677 | 137.06 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06677 | 137.16 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0668 | 137.41 | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0668 | 137.41 | P12:230:AEPW-SPS:SWEETWT6:WHEELER 6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06686 | 137.08 | P12:230:AEPW:ELKCITY6:CHISHOLM6::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06693 | 136.61 | 515800 GRACMNT7 345 560078 G16-037-TAP 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06707 | 139.39 | 525481 PLANT_X 6 230 3WXFMR WH ALM20171 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06734 | 138.33 | P42:345:OKGE:SB_DGSE7313:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06755 | 137.72 | P42:345:OKGE:SB_DGSE7385:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06785 | 137.58 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06786 | 137.59 | 516059 BECKHAM7 345 523961 POTTER_CO 7 345 2 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06818 | 141.34 | P23:345:SUNC:HLC_BRK188:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06821 | 141.38 | P12:345:SPS:FINNEY-HOLCOMB::523853-531449(1):EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0683 | 141.62 | P23:345:SUNC:HLC_BRK282:::EHV: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.0683 | 141.62 | Potential P4 Event - POI 531449_0 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.06902 | 141.59 | P42:345:OKGE:SB_BAER7314:::: | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07057 | 142.78 | POI 515800_22 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07057 | 142.94 | 511553 CHISHOLM7 345 560078 G16-037-TAP 345 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
Thermal | DISIS-2023-001 | 05ALL | 1 | 24SP | GEN-2023-201 | FROM->TO | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 478 | 478 | 0.07618 | 147.71 | 511553 CHISHOLM7 345 106 CHISHOLM_9 765 1 | Cumulative Impact | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1