## Executive Summary
Executive Summary: DISIS-2023-001 Phase 2 of Power Flow, Stability, and Short-Circuit
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study () for generation interconnection requests received during the Queue Cluster Window which closed on 1/29/2023. The primary objective of this is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The Manual Version 4.0 posted on http://opsportal.spp.org/Studies/Gen contains details about the process, methodology, definitions, and useful links. Please review the Manual or contact gistudies@spp.org for more information about the study process. -2023-001 Phase 2 includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest )
Manual Version 4.0
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20250225.pdf
This analyzes the impact of interconnecting new generation for total of:
28074.5 MW
The minimum cost of interconnecting all requests included in this is estimated at:
Total Network Upgrade $10,330,517,232.24 Steady State Network Upgrade $4,047,948,684.70 Stability Network Upgrade $1,119,545,487.00 Steady State/Stability Network Upgrade $3,429,375,400.00 Interconnection Costs: $1,733,647,660.54
Models Used in Steady State Study
2022 ITP Series
Winter: 2027
Summer: 2024, 2027
Light: 2027
Models Used in Stability Study
2020 MDWG
Winter: 2025, Summer: 2025
By: SPP Generator Interconnection Department
Published: July 25, 2025
Costs for Solar/Battery Requests were allocated using the 27SP (summer peak) model.
Costs for Wind Requests were allocated using the 27L (light load) model.
Short Circuit Ratio calculation is provided per group. A value of "N/A" means the request was offline for that scenario.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.
Refer to the 'Constraint Violation Criteria' column on the All Thermal tab for constraint identification per the Manual Section 4.2.2.2.
For CQ projects sharing a generation interconnection line, the Reactive Compensation required for the line was split proportionally based on MW between all connected CQ projects.
Identification of Contingent Upgrades added to this report per Attachment V, Section 3.8 of the Tariff. Refer to 'Contingent Upgrades - Screening' tab for list of contingent upgrades screened for an impact of 3% TDF and above.

## Revision History
Revision History
Date | Author | Change Description
2025-07-20 | SPP | Phase 2 Draft Report
2025-07-25 | SPP | Phase 2 Final Report

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
2025-07-25 | Cost Estimates | 1 | Executive Summary | Updated Interconnection, Steady State, Stability, Steady State / Stability, and Total Network Upgrade cost estimates
2025-07-25 | LOIS | 4,5 | Requests / Seasonal LOIS | Updated Seasonal LOIS value GEN-2023-050
2025-07-25 | Constraints, BC Loading, Upgrade Name | 6 | Constraints Summary | Updated Constraints, BC %Loadings, and Upgrade Names
2025-07-25 | Cost Estimates | 7,8 | Assigned Upgrade Costs / Upgrade Summary | Updated cost estimates and allocated upgrade costs
2025-07-25 | Upgrade Details | 9 | Constraint Upgrades - Screening | Updated details of network upgrades
2025-07-25 | Results and Upgrades | 10, 11, 12 | All Thermal / All Voltage / Staiblity Analysis Results | Updated results and corresponding network upgrades
2025-07-25 | SCRCCT and WSCR | 14, 15, 16 | SCRCCT Results / SCRCCT Screen / WSCR Screen | Results updated for SCRCCT analysis and WSCR screening

## Requests
LOIS Amount
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | April 1 - May 31 (Near Term) | April 1 - May 31 (Long Term) | June 1 - Sept 30 (Near Term) | June 1 - Sept 30 (Long Term) | Oct 1 - Nov 30 (Near Term) | Oct 1 - Nov 30 (Long Term) | Dec 1 - March 31 (Near Term) | Dec 1 - March 31 (Long Term) | Reactive Compensation Requirement (MVAR) | Service | Area | POI | Status
GEN-2023-012 | 01 NORTH | 25 | DIS-23-1 | Wind | 98.6 | 0 | 0 | 0 | 0 | 0 | 0 | 68.5238 | 68.5238 | -3.2365 | ER/NR | BEPC-SPP | Kingsbury County 115kV Substation | DISIS STAGE
GEN-2023-062 | 01 NORTH | 25 | DIS-23-1 | Thermal | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ER | BEPC-SPP | REN 115 kV Substation | DISIS STAGE
GEN-2023-082 | 01 NORTH | 25 | DIS-23-1 | Battery/Storage | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 175 | -0.21663 | ER/NR | WAPA | White 115 kV Substation | DISIS STAGE
GEN-2023-097 | 01 NORTH | 25 | DIS-23-1 | Battery/Storage | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.52887 | ER/NR | BEPC-SPP | Judson 345 kV Substation | DISIS STAGE
GEN-2023-105 | 01 NORTH | 25 | DIS-23-1 | Wind | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14.9381 | ER/NR | BEPC-SPP | Chappelle Creek 345 kV | DISIS STAGE
GEN-2023-154 | 01 NORTH | 25 | DIS-23-1 | Solar | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 116.152 | 116.152 | -1.5764 | ER | WAPA | Fort Thompson - Huron 230 kV Tap | DISIS STAGE
GEN-2023-182 | 01 NORTH | 25 | DIS-23-1 | Wind | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -18.4137 | ER | BEPC-SPP | Groton - Leland Olds 345 kV Line | DISIS STAGE
GEN-2023-011 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.6858 | ER | NPPD | Harbine 115 kV Substation | DISIS STAGE
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ER | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ER | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 303 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ER | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2023-116 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.35 | ER | NPPD | Keystone 345 kV Substation | DISIS STAGE
GEN-2023-117 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.6636 | ER | NPPD | Keystone 345 kV Substation | DISIS STAGE
GEN-2023-133 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -22.9 | ER | NPPD | Sweetwater 345 kV Substation | DISIS STAGE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Hybrid; Solar/Storage | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6337 | ER/NR | BEPC-SPP | Grant 115 kV Substation | DISIS STAGE
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Hybrid; Solar/Storage | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.0246 | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2023-216 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -27.57 | ER/NR | NPPD | Turtle Creek 345 kV Substation | DISIS STAGE
GEN-2023-217 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -32.86 | ER/NR | NPPD | Turtle Creek 345 kV Substation | DISIS STAGE
GEN-2023-218 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -27.57 | ER/NR | NPPD | Turtle Creek 345 kV Substation | DISIS STAGE
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.16619 | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.083097 | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.785 | ER | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.785 | ER | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2023-006 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.9 | ER | WERE | Wolf Creek- Blackberry 345 kV Line Break | DISIS STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.8 | ER/NR | SPS | Finney-Carpenter 345 KV line | DISIS STAGE
GEN-2023-023 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | -0.1 | ER/NR | KACY | Center City 161 kV Substation | DISIS STAGE
GEN-2023-032 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 200 | 175.2214 | 175.2214 | 200 | 199.7665 | 175.2214 | 175.2214 | 175.2214 | 175.2214 | -1.8 | ER/NR | KCPL | Odessa and Lexington 161 kV Line | DISIS STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 136.1997 | 147.8661 | 136.1997 | 169.7536 | 136.1997 | 147.8661 | 192.4741 | 192.4741 | -0.1 | ER/NR | KCPL | Liberty South 161 kV Substation | DISIS STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.5 | ER/NR | WERE | Clear Water - Waco 138 kV line | DISIS STAGE
GEN-2023-036 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | -0.4 | ER/NR | INDN | Eckles Road 161 kV Substation | DISIS STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | -0.2 | ER/NR | KACY | Nearman 161 kV Substation | DISIS STAGE
GEN-2023-050 | 03 CENTRAL | 25 | DIS-23-1 | Hybrid; Solar/Storage | 400 | 35.2818 | 102.5027 | 35.2818 | 172.6712 | 35.2818 | 102.5027 | 102.5027 | 102.5027 | -3.1 | ER/NR | WERE | Neosho 345 kV Substation | DISIS STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 100 | 58.2729 | 58.2729 | 100 | 100 | 58.2729 | 58.2729 | 58.2729 | 58.2729 | -0.2 | ER/NR | SWPA | Carthage 161 kV Substation | DISIS STAGE
GEN-2023-065 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.2 | ER/NR | WERE | Halstead 69 kV Substation | DISIS STAGE
GEN-2023-073 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4 | ER/NR | WERE | Rose Hill 345 kV Substation | DISIS STAGE
GEN-2023-085 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 150 | 113.6977 | 113.6977 | 150 | 150 | 113.6977 | 113.6977 | 150 | 150 | -0.3 | ER/NR | SWPA | Mansfield - Logan 161 kV Line | DISIS STAGE
GEN-2023-087 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 200 | 134.2712 | 0 | 134.2712 | 0 | 134.2712 | 0 | 147.8661 | 147.8661 | -2.9 | ER | KCPL | Archie 161 kV Substation | DISIS STAGE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | 0 | 24.2605 | 0 | 24.2605 | 0 | 24.2605 | 168.1873 | 168.1873 | -1.6 | ER | WERE | Jeffery Energy Center 345 kV Substation | DISIS STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -81.5 | ER | SUNC | Setab 345 kV | DISIS STAGE
GEN-2023-149 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 168.1873 | 168.1873 | -0.3 | ER/NR | KCPL | LaCygne - Stilwell 345 kV Line | DISIS STAGE
GEN-2023-169 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 125 | 85.1248 | 49.7876 | 85.1248 | 49.7876 | 85.1248 | 49.7876 | 120.2963 | 120.2963 | -0.6 | ER/NR | KCPL | Missouri City - Liberty South 161 kV Line | DISIS STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 150 | 132.7655 | 150 | 132.7655 | 150 | 132.7655 | 150 | 150 | 150 | -0.7 | ER | KCPL | Salisbury 161 kV Substation | DISIS STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | -0.7 | ER/NR | INDN | Sub M 161 kV Substation | DISIS STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.8 | ER/NR | SUNC | Holcomb 345 kV | DISIS STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.6 | ER/NR | SUNC | Holcomb 345 kV | DISIS STAGE
GEN-2023-194 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 225 | 0 | 3.7358 | 0 | 105.4292 | 0 | 3.7358 | 9.7723 | 9.7723 | -4.3 | ER/NR | EMDE | Riverton - Neosho 161 kV Line Tap | DISIS STAGE
GEN-2023-219 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.6 | ER/NR | WERE | Reading - Osage Jct 115 kV Line | DISIS STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | -2.9 | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | DISIS STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | -3 | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | DISIS STAGE
GEN-2023-231 | 03 CENTRAL | 25 | DIS-23-1 | Hybrid; Wind/Storage | 310 | 310 | 310 | 0 | 0 | 310 | 310 | 29.9496 | 29.9496 | -22.2 | ER | WERE | Neosho - LaCynge 345 kV Line | DISIS STAGE
GEN-2023-009 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.06 | ER/NR | WFEC | Hugo 138 kV Substation | DISIS STAGE
GEN-2023-022 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -27.41 | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2023-027 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Battery | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.56 | ER/NR | AEPW | Bird Hollow (Langley) - Pryor Junction 138 kV Line | DISIS STAGE
GEN-2023-028 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Battery | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.34 | ER/NR | GRDA | Dry Gulch - Pensacola 161 kV Line | DISIS STAGE
GEN-2023-030 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.87 | ER/NR | AEPW | Tap between 345 kV SW Shreveport to Dolet Hills Substations | DISIS STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.48 | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | DISIS STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -13.07 | ER/NR | OKGE | Lula 138 kV Substation | DISIS STAGE
GEN-2023-049 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.24 | ER/NR | GRDA | Dry Gulch - Pensacola 161 kV Line | DISIS STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.09 | ER/NR | GRDA | Kerr Grove 161 kV | DISIS STAGE
GEN-2023-056 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | ER/NR | SWPA | Van Buren 161 kV | DISIS STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.05 | ER/NR | GRDA | Pawnee Switch 138 kV | DISIS STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/RECIP Gas | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2 | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | DISIS STAGE
GEN-2023-063 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.99 | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | DISIS STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2 | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | DISIS STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.15 | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | DISIS STAGE
GEN-2023-075 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14.47 | ER/NR | WERE | Delaware to Neosho 345 kV | DISIS STAGE
GEN-2023-076 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -23.7 | ER/NR | WERE | Delaware - Neosho 345 kV | DISIS STAGE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24 | ER/NR | WFEC | Pharaoh 138 kV Substation | DISIS STAGE
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4 | ER/NR | WFEC | Unger - Frogville 138 kV line | DISIS STAGE
GEN-2023-100 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -10.23 | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2023-101 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -3.05 | ER/NR | SPS | Tap Stateline Demarc - Wheeler 230 kV Line | DISIS STAGE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.96 | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.15 | ER/NR | WFEC | Mooreland - Noel 138 kV Line | DISIS STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.28 | ER/NR | SWPA | Jonesboro - Independence 161 kV | DISIS STAGE
GEN-2023-134 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.28 | ER/NR | AEPW | Fixico Tap to Weleetka 138 kV Line | DISIS STAGE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.9 | ER/NR | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2023-138 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.09 | ER | GRDA | GRDA1 - Tonece7 345 kV Line | DISIS STAGE
GEN-2023-150 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.66 | ER/NR | OKGE | Gracemont 138 kV Substation | DISIS STAGE
GEN-2023-151 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.6 | ER/NR | AEPW | South Nashville - South Murfreesboro 138kV | DISIS STAGE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 74.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.18 | ER/NR | OKGE | Roman Nose 138 kV Substation | DISIS STAGE
GEN-2023-164 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.875 | ER/NR | OKGE | Gracemont 345 kV Substation | DISIS STAGE
GEN-2023-165 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.875 | ER/NR | OKGE | Gracemont 345 kV Substation | DISIS STAGE
GEN-2023-166 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88 | ER | OKGE | 84th Street - Tennessee Tap 138 kV Line | DISIS STAGE
GEN-2023-167 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.87 | ER/NR | OKGE | Washington Park 138 kV Substation | DISIS STAGE
GEN-2023-168 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.01 | ER/NR | OKGE | Classen 138 kV Substation | DISIS STAGE
GEN-2023-174 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97 | ER | WFEC | Paoli West 138 kV Substation | DISIS STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.27 | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | DISIS STAGE
GEN-2023-180 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.13 | ER/NR | AEPW | Hackett - N Huntington 161 kV Line Tap | DISIS STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.66 | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | DISIS STAGE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.04 | ER | AEPW | Welsh-Lydia 345kV Line | DISIS STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.61 | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | DISIS STAGE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.35 | ER/NR | OKGE | Battlefield BESS 161 kV Substation | DISIS STAGE
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.75 | ER/NR | WFEC | Prague - Chernicky 138 kV Line | DISIS STAGE
GEN-2023-211 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Battery/Wind | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -24.32 | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2023-212 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.04 | ER/NR | AEPW | Northwest Texarkana - Valliant 345 kV Line | DISIS STAGE
GEN-2023-213 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.08 | ER/NR | AEPW | Chamber Springs 161 kV Substation | DISIS STAGE
GEN-2023-227 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.98 | ER/NR | AEP | Petty to Chapel 138 kV Line | DISIS STAGE
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -19.91 | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | DISIS STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.23 | ER/NR | AEPW | Red Pointe 138 kV Substation | DISIS STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.09 | ER | AEPW | Winnsboro 138 kV Substation | DISIS STAGE
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.52 | ER/NR | SPS | Chevron Eddy 115 kV | DISIS STAGE
GEN-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -152.02 | ER/NR | SPS | T14 Circuit 115 V Line | DISIS STAGE
GEN-2023-005 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.94 | ER/NR | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2023-008 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.61 | ER | SPS | Tuco - Carlisle 230 kV line | DISIS STAGE
GEN-2023-010 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -9.38 | ER | SPS | Moore Co 230 kV Substation | DISIS STAGE
GEN-2023-060 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | ER/NR | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2023-081 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.82 | ER/NR | SPS | Crossroads - Hobbs 345 kV Line | DISIS STAGE
GEN-2023-086 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.645 | ER/NR | SPS | Potter - Newhart 230 kV line | DISIS STAGE
GEN-2023-110 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.16 | ER | SPS | Tap Border to Tuco 345 kV Line | DISIS STAGE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.89 | ER | SPS | Kress 115 kV Substation | DISIS STAGE
GEN-2023-123 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.89 | ER | SPS | Pringle Interchange 230 kV Substation | DISIS STAGE
GEN-2023-142 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5 | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2023-143 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.34 | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2023-158 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.21 | ER/NR | SPS | Needmore - Yoakum 230 kV Line | DISIS STAGE
GEN-2023-159 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.59 | ER/NR | SPS | Needmore - Yoakum 230 kV Line | DISIS STAGE
GEN-2023-176 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.59 | ER | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2023-178 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.05 | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2023-183 | 05 SOUTHWEST | 25 | DIS-23-1 | Thermal | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.92 | ER | SPS | Tuco 345kV | DISIS STAGE
GEN-2023-184 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.52 | ER | SPS | Phantom 115 kV Substation | DISIS STAGE
GEN-2023-188 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.52 | ER/NR | AEPW | Oklaunion - Lawton 345 kV Line | DISIS STAGE
GEN-2023-195 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -6.79 | ER/NR | SPS | Roosevelt - Tolk 230 kV line tap | DISIS STAGE
GEN-2023-201 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.15 | ER/NR | SPS | Crossroads - Hobbs 345 kV Line | DISIS STAGE
GEN-2023-203 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -5.2 | ER/NR | SPS | Hobbs - Ink Basin 230 kV Transmission Line | DISIS STAGE
GEN-2023-208 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ER | SPS | Rolling Hills 115 kV | DISIS STAGE
GEN-2023-209 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ER/NR | SPS | Amarillo South 115 kV | DISIS STAGE
GEN-2023-228 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11.2 | ER/NR | SPS | Tuco-Okalunion 345 kV line | DISIS STAGE
GEN-2023-236 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.5 | ER/NR | SPS | Hobbs - Yoakum 345 kV | DISIS STAGE
GEN-2023-237 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 500 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.5 | ER/NR | SPS | Crawfish Draw 345 kV Substation | DISIS STAGE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | [9 empty] | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | [9 empty] | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | [9 empty] | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2022-005 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Northeast Parsons 138kV Substation | DISIS STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | WERE | Neosho - N345 161 kV Substation | DISIS STAGE
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | [9 empty] | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | DISIS STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | [9 empty] | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | DISIS STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WERE | Wolf Creek - Blackberry 345 kV Tap | DISIS STAGE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | [9 empty] | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | DISIS STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER/NR | KCPL | Nashua 161 kV Substation | DISIS STAGE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | [9 empty] | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | DISIS STAGE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Hybrid; Solar/Storage | 80 | [9 empty] | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | DISIS STAGE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | KCPL | Liberty West 161 kV | DISIS STAGE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Shoal Creek 161 kV Substation | DISIS STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | KCPL | Blue Mills BESS 161kV Substation | DISIS STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 360 | [9 empty] | ER | WERE | Burns 345kV Substation | DISIS STAGE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | [9 empty] | ER | WERE | Gill - Viola 138 kV Line Break | DISIS STAGE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OGE | Woodward 345 kV Substation | DISIS STAGE
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | [9 empty] | ER/NR | OGE | Woodward 345kV Substation | DISIS STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OGE | Woodward 345kV Substation | DISIS STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 180 | [9 empty] | ER | AEP | Longwood to Scottville 138 kV line | DISIS STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER | WFEC | Sunshine North to Anadarko 138 kV | DISIS STAGE
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | [9 empty] | ER/NR | AEP | Talawanda to Canadian River 138 kV Line Tap | DISIS STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | OGE | Bison 345kV Substation | DISIS STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | [9 empty] | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | DISIS STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Hybrid; Solar/Storage | 150 | [9 empty] | ER/NR | AEP | Wilkes 345 kV Substation | DISIS STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OGE | Battlefield BESS 161kV | DISIS STAGE
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | WFEC | Colbert 138 kV Substation | DISIS STAGE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | [9 empty] | ER | AEP | Pirkey 345kV Substation | DISIS STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OGE | Caney Creek 138 kV Substation | DISIS STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 180 | [9 empty] | ER | AEP | Weatherford Jct. to Hinton 138 kV line | DISIS STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | WFEC | Canadian Switch 138 kV Substation | DISIS STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | [9 empty] | ER | OGE | Horseshoe Lake 138 kV Substation | DISIS STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Silver City 138 kV Substation | DISIS STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | [9 empty] | ER/NR | AEP | Northeastern - Delaware 345 kV transmission line | DISIS STAGE
GEN-2022-231 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 166 | [9 empty] | ER/NR | OGE | Crescent to Cottonwood Creek 138 kV Line | DISIS STAGE
GEN-2022-234 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | [9 empty] | ER/NR | AEP | Alluwe Tap â€“ Chelsea 138 kV line | DISIS STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WFEC | El Reno SW 138 kV | DISIS STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | [9 empty] | ER/NR | OGE | Maud 138 kV substation | DISIS STAGE
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | [9 empty] | ER | SPS | Tuco 345kV | DISIS STAGE
GEN-2021-008 | 01 NORTH | 23 | DIS-21-1 | Solar | 200 | [9 empty] | ER/NR | BEPC | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND | DISIS STAGE
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | [9 empty] | ER | NPPD | Olive Creek 115 kV Substation | DISIS STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | LES | Rokeby 115 kV Substation | DISIS STAGE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | DISIS STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | DISIS STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | [9 empty] | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | DISIS STAGE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 225 | [9 empty] | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-057 | 02 NEBRASKA | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | NPPD | Antelope 345kV substation | DISIS STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | [9 empty] | ER/NR | OPPD | OPPD 345KV Cass County Substation | DISIS STAGE
GEN-2021-005 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 350 | [9 empty] | ER/NR | WERE | Summit 345 kV substation in Saline County, KS | DISIS STAGE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | [9 empty] | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | DISIS STAGE
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | [9 empty] | ER | SUNC | Elm Creek 345 kV interconnection substation | DISIS STAGE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | [9 empty] | ER | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2021-023 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 306.18 | [9 empty] | ER | WERE | Wild Plains 345kV Substation | DISIS STAGE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | [9 empty] | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | DISIS STAGE
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | [9 empty] | ER/NR | INDN | Independence Power & Light, Blue Valley Substation, 161kV Bus | DISIS STAGE
GEN-2021-050 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 200 | [9 empty] | ER/NR | KCPL | 161kV Stilwell-Clinton Line | DISIS STAGE
GEN-2021-051 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER/NR | KCPL | 161kV Stilwell-Clinton Line | DISIS STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | [9 empty] | ER | WERE | Viola 345kV Substation | DISIS STAGE
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | [9 empty] | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-076 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | [9 empty] | ER/NR | MIDW | ITC Post Rock 345 kV Substation | DISIS STAGE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | DISIS STAGE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | [9 empty] | ER/NR | WERE | Wolf Creek - Benton 345 kV | DISIS STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | [9 empty] | ER/NR | WERE | Evergy's Midland Substation 115kV bus | DISIS STAGE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | [9 empty] | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | DISIS STAGE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | [9 empty] | ER | WERE | Evergy 345kV Jeffrey Energy Center | DISIS STAGE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | 138kV Brown Substation | DISIS STAGE
GEN-2021-015 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 74.9 | [9 empty] | ER | OKGE | Bobcat 345 kV interconnection substation | DISIS STAGE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | [9 empty] | ER | AEPW | Sunnyside-Johnston 345 kV | DISIS STAGE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | [9 empty] | ER | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | [9 empty] | ER/NR | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | [9 empty] | ER | WFEC | Western Farmers 138kV Mooreland Substation | DISIS STAGE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | [9 empty] | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | DISIS STAGE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Welsh 345kV Substation | DISIS STAGE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | [9 empty] | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | DISIS STAGE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | [9 empty] | ER | OKGE | Pecan Creek 345kV substation | DISIS STAGE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345 kV Substation | DISIS STAGE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid; Solar/Storage | 155 | [9 empty] | ER/NR | AEPW | Craig JCT 138kV | DISIS STAGE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid; Solar/Storage | 100 | [9 empty] | ER/NR | AEPW | Carnegie South 138kV | DISIS STAGE
GEN-2021-075 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid; Solar/Storage | 300 | [9 empty] | ER/NR | AEPW | CAMPCOR4 138kV Substation | DISIS STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | [9 empty] | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | DISIS STAGE
GEN-2021-098 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid; Solar/Storage | 160 | [9 empty] | ER/NR | OKGE | Dewey District 138 kV Substation | DISIS STAGE
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid | 50 | [9 empty] | ER/NR | SPS |  | DISIS STAGE
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid | 80 | [9 empty] | ER/NR | SPS |  | DISIS STAGE
GEN-2021-010 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 208 | [9 empty] | ER | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-012 | 05 SOUTHWEST | 23 | DIS-21-1 | Battery/Storage | 203 | [9 empty] | ER | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-014 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 208 | [9 empty] | ER | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid; Solar/Storage | 400 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
IR41 | 02 NEBRASKA | 22.5 | DIS-20-1-PQ | Solar | 50 | [9 empty] | ER/NR | ALTW |  | SIP
IR42 | 02 NEBRASKA | 22.5 | DIS-20-1-PQ | Solar | 50 | [9 empty] | ER/NR | ALTW |  | SIP
GIA-108 | 04 SOUTHEAST | 22.5 | DIS-20-1-PQ | Solar | 201.735 | [9 empty] | ER/NR | AECI
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | [9 empty] | ER/NR | BEPC | Lonesome Creek 115kV | FACILITY STUDY STAGE
GEN-2020-021 | 01 NORTH | 22 | DIS-20-1 | Wind | 235 | [9 empty] | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | FACILITY STUDY STAGE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid; Solar/Storage | 74.5 | [9 empty] | ER/NR | WAPA | Fairview 115kV Substation | FACILITY STUDY STAGE
GEN-2020-091 | 01 NORTH | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | BEPC | Patent Gate Substation 345 kV | FACILITY STUDY STAGE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | [9 empty] | ER | OPPD | 6846 Substation 69 kV | FACILITY STUDY STAGE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid; Solar/Storage | 320 | [9 empty] | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | FACILITY STUDY STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid; Solar/Storage | 215 | [9 empty] | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | FACILITY STUDY STAGE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | FACILITY STUDY STAGE
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | FACILITY STUDY STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 1363; 161kV Substation | FACILITY STUDY STAGE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 272.7 | [9 empty] | ER | OPPD | Substation 3740; 345kV | FACILITY STUDY STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | FACILITY STUDY STAGE
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | FACILITY STUDY STAGE
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | [9 empty] | ER | OPPD | Between Substation 1209 and 1252; 161kV | FACILITY STUDY STAGE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | [9 empty] | ER/NR | NPPD | Cody to Valentine 115kV line | FACILITY STUDY STAGE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | FACILITY STUDY STAGE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | [9 empty] | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | FACILITY STUDY STAGE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | [9 empty] | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | FACILITY STUDY STAGE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 45 | [9 empty] | ER | KCPL |  | STAGE
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 45 | [9 empty] | ER | KCPL |  | STAGE
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | [9 empty] | ER/NR | WERE | East Substation 69 kV | FACILITY STUDY STAGE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid; Solar/Storage | 650 | [9 empty] | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | FACILITY STUDY STAGE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid; Solar/Storage | 250 | [9 empty] | ER | SPS | Corporation Carpenter 345kV Substation | FACILITY STUDY STAGE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Russell 115 kV Substation | FACILITY STUDY STAGE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | FACILITY STUDY STAGE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | [9 empty] | ER/NR | KCPL | Atlantic 345 kV Substation | FACILITY STUDY STAGE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | [9 empty] | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | FACILITY STUDY STAGE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | [9 empty] | ER/NR | EDE | 4544 Stateline CC 161kV Substation | FACILITY STUDY STAGE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid; Solar/Storage | 150 | [9 empty] | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | FACILITY STUDY STAGE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid; Solar/Storage | 150 | [9 empty] | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | FACILITY STUDY STAGE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid; Solar/Storage | 225 | [9 empty] | ER/NR | EDE | Riverton-Neosho 161kV line | FACILITY STUDY STAGE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | [9 empty] | ER/NR | EDE | La Russell 161 kV Substation | FACILITY STUDY STAGE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 204.3 | [9 empty] | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | FACILITY STUDY STAGE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid; Solar/Storage | 140 | [9 empty] | ER/NR | WFEC | Seiling-Taloga Substations 138kV | FACILITY STUDY STAGE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid; Solar/Storage | 113 | [9 empty] | ER/NR | AEPW | Snyder â€“ Altus Jct. 138kV | FACILITY STUDY STAGE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid; Solar/Storage | 201.6 | [9 empty] | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | FACILITY STUDY STAGE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | [9 empty] | ER/NR | AEPW | Lydia 345 kV Station | FACILITY STUDY STAGE
GEN-2020-074 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Lawton to Sunnyside 345 kV Substation | FACILITY STUDY STAGE
GEN-2020-075 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | STAGE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER/NR | AEPW | Tenaska Switching Substation 345kV | FACILITY STUDY STAGE
GEN-2020-085 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Lawton to Sunnyside 345 kV Line | FACILITY STUDY STAGE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | [9 empty] | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | FACILITY STUDY STAGE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | [9 empty] | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | FACILITY STUDY STAGE
GEN-2020-009 | 05 SOUTHWEST | 22 | DIS-20-1 | Hybrid; Solar/Storage | 300 | [9 empty] | ER/NR | AEPW | Lawton East Side to Oklaunion 345kV | STAGE
GEN-2020-017 | 05 SOUTHWEST | 22 | DIS-20-1 | Solar | 74.88 | [9 empty] | ER/NR | SPS | 230kV Lamb County Interchange | STAGE
GEN-2020-059 | 05 SOUTHWEST | 22 | DIS-20-1 | Hybrid; Solar/Storage | 250 | [9 empty] | ER | SPS | Tuco-Yoakum-Hobbs 345 kV | STAGE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | [9 empty] | ER | SPS | Lubbock East Substation 230 kV | FACILITY STUDY STAGE
GEN-2020-062 | 05 SOUTHWEST | 22 | DIS-20-1 | Solar | 256 | [9 empty] | ER | SPS | OASIS 230kV Substation | STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | [9 empty] | ER | SPS | Hobbs-Andrews 345 kV Line | FACILITY STUDY STAGE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GEN-2020-068 | 05 SOUTHWEST | 22 | DIS-20-1 | Solar | 400 | [9 empty] | ER | SPS | Tuco to Yoakum 345kV line | FACILITY STUDY STAGE
GIA-106 | 03 CENTRAL | 21.5 | DIS-19-1 PQ | Solar | 118.696 | [9 empty] | ER/NR | AECI
GIA-107 | 03 CENTRAL | 21.5 | DIS-19-1 PQ | Solar | 125 | [9 empty] | ER/NR | AECI
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | [9 empty] | ER | BEPC-SPP | 115kV Strandahl sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | Wind | 125 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA PENDING
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA PENDING
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal | 15.15 | [9 empty] | ER/NR | BEPC-SPP | Siouxland 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | Hybrid; Solar/Storage | 110 | [9 empty] | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | IA PENDING
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | BEPC-SPP | Leland Olds 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-065 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 19.8 | [9 empty] | ER/NR | NPPD | Antelope 345 kV Substation | STAGE
GEN-2018-068 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 302.4 | [9 empty] | ER/NR | NPPD | Antelope 345 kV Substation | STAGE
GEN-2018-083 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 250 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | IA PENDING
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | [9 empty] | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA PENDING
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | [9 empty] | ER/NR | NPPD | Antelope - Hoskins 345 kV | IA PENDING
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | OPPD | S1263 Brock 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | [9 empty] | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | [9 empty] | ER/NR | NPPD | 115kV Monolith Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2019-069 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kV Line | IA PENDING
GEN-2019-070 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 50 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line | IA PENDING
GEN-2019-073 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | NPPD | Shell Creek-Hoskins 345kv Line | IA PENDING
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | [9 empty] | ER | SUNC | Thistle 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | [9 empty] | ER/NR | WERE | Renfrow-Viola 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | [9 empty] | ER | EMDE | Dadeville 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal | 15.56 | [9 empty] | ER/NR | MIDW | Saxman 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | [9 empty] | ER/NR | SUNC | Spearville to Clark County 345 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | [9 empty] | ER | SUNC | North Fort Dodge 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend- Circle 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Great Bend-Spearville 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Clark County 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | [9 empty] | ER/NR | SUNC | Great Bend - Circle 230kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | [9 empty] | ER/NR | GRDA | Tonnece Substation 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | [9 empty] | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | [9 empty] | ER | AEPW | Farmland-Delaware 138kV line | IA PENDING
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | [9 empty] | ER | AEPW | Pittsburg 345kV Substation | IA PENDING
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | [9 empty] | ER | AEPW | Longwood 345kV substation | IA PENDING
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid; Solar/Storage | 250 | [9 empty] | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | IA PENDING
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | [9 empty] | ER | GRDA | Maid 161kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 200 | [9 empty] | ER/NR | OKGE | Woodward 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | [9 empty] | ER | OKGE | DeGrasse 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | [9 empty] | ER | AEPW | Overton-Northwest Henderson 138kV | IA PENDING
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | [9 empty] | ER | SPS | Newhart 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | [9 empty] | ER/NR | SPS | Yoakum 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | [9 empty] | ER/NR | SPS | Roosevelt 230kV Substation | IA PENDING
MPC04300 | 01 NORTH | 20.5 | DIS-18-2-PQ | Wind | 200 | [9 empty] | ER/NR | OTP
GIA-100 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 40 | [9 empty] | ER/NR | AECI
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 460 | [9 empty] | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 75 | [9 empty] | ER/NR | AECI
GIA-99 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 470 | [9 empty] | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | [9 empty] | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | [9 empty] | ER/NR | AECI
GIA-105 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | [9 empty] | ER/NR | AECI
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | [9 empty] | ER | WAPA |  | STAGE
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | BEPC-SPP | Neset 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Fort Calhoun 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | OPPD | Cass County 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | [9 empty] | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL |  | STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL |  | STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | [9 empty] | ER | KCPL |  | STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL |  | STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | [9 empty] | ER | KCPL |  | STAGE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | [9 empty] | ER | SUNC | Cimarron 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | [9 empty] | ER | INDN | Blue Valley 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | [9 empty] | ER | WERE | Neosho 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | [9 empty] | ER | SUNC | Thistle 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-060 | 02 NEBRASKA | 20 | DIS-18-1 | Wind | 50 | [9 empty] | ER/NR | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | [9 empty] | ER/NR | AEPW | North Boston-Bann 138kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | [9 empty] | ER/NR | WFEC | Dover 138 kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | [9 empty] | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | IA PENDING
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Mustang 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | AEPW | Tulsa Power Station 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | [9 empty] | ER | AEPW | Tulsa North 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | [9 empty] | ER | OKGE | Horseshoe Lake 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | [9 empty] | ER | OKGE | Pecan Creek 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | [9 empty] | ER | AEPW | Longwood 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | [9 empty] | ER | SPS | T14 Circuit 115kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | [9 empty] | ER/NR | SPS | Tuco-Oklaunion 345kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | [9 empty] | ER | SPS | Roadrunner 115kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER/NR | MDU |  | Done: Phase 3
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery | 20 | [9 empty] | ER/NR | XEL |  | Done: Phase 3
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | XEL |  | Done: Phase 3
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL |  | Done: Phase 3
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL |  | Done: Phase 3
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER | ALTW |  | Done: Phase 3
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | XEL |  | Done: Phase 3
J1221 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | GRE |  | Active: Phase 3
J1312 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | XEL |  | Done: Phase 3
J1314 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | DPC |  | Done: Phase 3
J1325 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW |  | Done: Phase 3
J1426 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL |  | Done: Phase 3
J1445 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL |  | Done: Phase 3
J1474 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL |  | IA PENDING
J1485 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER | OTP |  | Active: Phase 3
J1503 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW |  | Active: Phase 3
J1504 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW |  | Active: Phase 3
J1534 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL |  | Active: Phase 3
J1566 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | ALTW |  | Active: Phase 3
J1572 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | XEL |  | Active: Phase 3
J1575 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 70 | [9 empty] | ER/NR | OTP |  | Active: Phase 3
J1581 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL |  | Active: Phase 3
J1588 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL |  | Active: Phase 3
J1605 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | XEL |  | Active: Phase 3
J1611 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 174 | [9 empty] | ER/NR | XEL |  | Active: Phase 3
J1620 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER/NR | XEL |  | Active: Phase 3
J1657 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | XEL |  | Active: Phase 3
J1730 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | XEL |  | Active: Phase 3
J1769 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 120 | [9 empty] | ER/NR | DPC |  | Active: Phase 3
J1808 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | DPC |  | Active: Phase 3
J1826 | 01 NORTH | 19.5 | DIS-18-1-PQ | Hydro | 4 | [9 empty] | ER/NR | XEL |  | Done: Phase 3
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [9 empty] | ER/NR | XEL |  | Done: Phase 3
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER | OTP |  | STAGE
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 75 | [9 empty] | ER | OTP |  | STAGE
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | [9 empty] | ER/NR | OTP |  | STAGE
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 151.2 | [9 empty] | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | [9 empty] | ER/NR | OTP
IR39 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 151.88 | [9 empty] | ER/NR | ALTW
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 | [9 empty] | ER/NR | ALTW |  | Done: Phase 3
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | ALTW |  | Done: Phase 3
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | ALTW |  | Done: Phase 3
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 | [9 empty] | ER | ALTW |  | Done: Phase 3
J1181 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | ALTW |  | Done: Phase 3
J1270 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC |  | Done: Phase 3
J1313 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | ALTW |  | Done: Phase 3
J1359 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Gas | 95 | [9 empty] | ER/NR | ALTW |  | Active: Phase 3
J1365 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 169.4 | [9 empty] | ER/NR | ALTW |  | Active: Phase 3
J1444 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | ALTW |  | Active: Phase 3
J1520 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | ALTW |  | Active: Phase 3
J1529 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC |  | Active: Phase 3
J1530 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC |  | Active: Phase 3
J1532 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | MEC |  | Active: Phase 3
J1590 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC |  | Active: Phase 3
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER | MEC |  | Done: Phase 3
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 300 | [9 empty] | ER/NR | AMMO |  | Done: GIA
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 400 | [9 empty] | ER/NR | AMMO |  | Done: GIA
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO |  | Done: GIA
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMMO |  | Done: GIA
J1191 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 64 | [9 empty] | ER/NR | CWLD |  | Active
J1202 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 68.4 | [9 empty] | ER/NR | AMIL |  | Done
J1208 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL |  | Done
J1209 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 80 | [9 empty] | ER/NR | AMIL |  | Done
J1213 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Hydro | 60 | [9 empty] | ER/NR | AMMO |  | Done
J1216 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | AMIL |  | Active
J1241 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL |  | Done
J1268 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMMO |  | Done
J1303 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | SIPC |  | Done
J1306 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMIL |  | Active
J1311 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | AMIL |  | Active
J1488 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 500 | [9 empty] | ER/NR | AMMO |  | Active
J1490 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 1000 | [9 empty] | ER/NR | AMMO |  | Active
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO |  | Done: GIA
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | AMMO |  | Done: GIA
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO |  | Done: GIA
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | AMMO |  | Done: GIA
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 97.5 | [9 empty] | ER | AECI
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI |  | Done: GIA
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES |  | Done: GIA
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 | [9 empty] | ER/NR | AMMO |  | Done: GIA
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 500 | [9 empty] | ER/NR | EES-EAI |  | Done: GIA
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO |  | Done: GIA
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO |  | Done: GIA
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI |  | Done: GIA
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI |  | Done: GIA
J1205 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER | CLEC |  | Done: Phase 3
J1215 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI |  | Done: Phase 3
J1231 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 125 | [9 empty] | ER/NR | BREC |  | Done: Study Not Started
J1239 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER | EES |  | Done: Phase 3
J1258 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 50 | [9 empty] | ER/NR | EES-EAI |  | Done: Phase 3
J1281 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 75 | [9 empty] | ER/NR | EES-EAI |  | Done: Phase 3
J1299 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | AMMO |  | Done
J1373 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 95 | [9 empty] | ER/NR | EES-EAI |  | Done: Phase 3
J1402 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 0 | [9 empty] | ER/NR | EES-EAI |  | Done: Phase 3
J1415 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 250 | [9 empty] | ER/NR | EES-EAI |  | Done: Phase 3
J1424 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER | CLEC |  | Done: Phase 3
J1434 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI |  | Done: Phase 3
J1436 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER | EES |  | Done: Phase 3
J1437 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 180 | [9 empty] | ER/NR | EES-EAI |  | Done: Phase 3
J1442 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES |  | Done: Phase 3
J1509 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EMI |  | Not Started
J1514 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EAI |  | Active: Phase 3
J1558 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI |  | Active: Phase 3
J1559 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI |  | Active: Phase 3
J1562 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | EES-EAI |  | Active: Phase 3
J1577 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI |  | Done: Phase 3
J1598 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 325 | [9 empty] | ER/NR | EES |  | Active: Phase 3
J1602 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 25 | [9 empty] | ER/NR | EES |  | Active: Phase 3
J1612 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI |  | Active: Phase 3
J1669 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER | EES |  | Active: Phase 3
J1670 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 165 | [9 empty] | ER/NR | EES-EAI |  | Active: Phase 3
J1671 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER | EES |  | Active: Phase 3
J1672 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 | [9 empty] | ER/NR | EES-EMI |  | Active: Phase 3
J1673 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 | [9 empty] | ER/NR | CLEC |  | Active: Phase 3
J1709 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 100 | [9 empty] | ER | EES |  | Active: Phase 3
J1710 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 300 | [9 empty] | ER/NR | EES-EAI |  | Active: Phase 3
J1723 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Battery | 10 | [9 empty] | ER/NR | EES-EAI |  | Not Started
J1747 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 50 | [9 empty] | ER/NR | EES-EMI |  | Active: Phase 3
J1748 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EMI |  | Active: Phase 3
J1760 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 205 | [9 empty] | ER/NR | EES |  | Active: Phase 3
J1816 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 | [9 empty] | ER/NR | EES-EAI |  | Active: Phase 3
J1820 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 100 | [9 empty] | ER/NR | EES-EAI |  | Active: Phase 3
J1827 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 90 | [9 empty] | ER/NR | EES |  | Active: Phase 3
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 126 | [9 empty] | ER/NR | EES |  | Active: Phase 3
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | [9 empty] | ER | EES-EAI |  | Active: Phase 3
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | WAPA | Vfodnes-Utica Jct. 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP | Logan 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | WAPA | Denison 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | [9 empty] | ER/NR | OPPD | Tekamah - Raun 161 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER | NPPD | Holt County 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | [9 empty] | ER | OPPD | Jones St. No 1201 69kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | NPPD | Hoskins 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Hybrid; Solar/Storage | 310 | [9 empty] | ER | NPPD | McCool 345kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | [9 empty] | ER | NPPD | Spalding to North Loup 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Stillwell - Clinton 161kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | [9 empty] | ER | KCPL | Holt County 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | [9 empty] | ER | SUNC | Elm Creek 345kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | [9 empty] | ER | WERE | Abilene Energy Center-Northview 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | WERE | Sumner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-131 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 29.6 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | [9 empty] | ER/NR | KCPL | Nashua-St. Joe 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | [9 empty] | ER | EMDE | Asbury 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | [9 empty] | ER/NR | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | [9 empty] | ER/NR | WERE | Buffalo Flats 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | [9 empty] | ER/NR | WFEC | El Reno SW 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | [9 empty] | ER/NR | OKGE | Arcadia 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | [9 empty] | ER/NR | AEPW | Clarksville 345kV Switching Station | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | [9 empty] | ER/NR | OKGE | Johnson County 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | [9 empty] | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | [9 empty] | ER/NR | OKGE | Woodring 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | Hybrid; Solar/Storage | 210 | [9 empty] | ER | OKGE | Renfrow 345kV Substation | STAGE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Tryon 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | [9 empty] | ER/NR | OKGE | Branch 161kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | [9 empty] | ER/NR | OKGE | Brown 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | [9 empty] | ER/NR | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | [9 empty] | ER | SPS | Deaf Smith-Plant X 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | [9 empty] | ER | SPS | TUCO-Oklaunion 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | [9 empty] | ER | SPS | Tolk 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | [9 empty] | ER | SPS | Flatland 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | [9 empty] | ER | SPS | Mahoney 230kV Substation | IA FULLY EXECUTED/ON SCHEDULE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | [9 empty] | ER | XEL |  | Done: Phase 3
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | OTP |  | Done: Phase 3
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | [9 empty] | ER | DPC |  | Done: Phase 3
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | [9 empty] | ER/NR | XEL |  | Done: Phase 3
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | [9 empty] | ER | DPC |  | Done: Phase 3
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 101.28 | [9 empty] | ER | XEL |  | Done: Phase 3
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 | [9 empty] | ER/NR | ALTW |  | IA PENDING
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | [9 empty] | ER | ALTW |  | Done: Phase 3
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 | [9 empty] | ER/NR | MEC |  | Done: Phase 3
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | [9 empty] | ER/NR | AECI
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | [9 empty] | ER/NR | AECI
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | [9 empty] | ER/NR | AECI
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | [9 empty] | ER/NR | AECI
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | [9 empty] | ER/NR | AECI
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 | [9 empty] | ER/NR | AECI
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | [9 empty] | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | WAPA | Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | BEPC-SPP | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | [9 empty] | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | [9 empty] | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | [9 empty] | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | [9 empty] | ER | EMDE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | [9 empty] | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | [9 empty] | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | [9 empty] | ER/NR | WERE | Gordon Evans 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | [9 empty] | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | [9 empty] | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | [9 empty] | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | [9 empty] | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | [9 empty] | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | [9 empty] | ER | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | [9 empty] | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-076 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | [9 empty] | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | [9 empty] | ER | AEPW | Explorer Claremore Tap COOYYAH4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | [9 empty] | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | [9 empty] | ER | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | [9 empty] | ER/NR | SPS | Bull Creek 115 kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | [9 empty] | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | [9 empty] | ER | BEPC-SPP
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC-SPP
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | [9 empty] | ER | BEPC-SPP
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | [9 empty] | ER | BEPC-SPP
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | [9 empty] | ER | BEPC-SPP
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 49.98 | [9 empty] | ER/NR | DPC |  | Done: GIA
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | [9 empty] | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | [9 empty] | ER | WAPA
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 200 | [9 empty] | ER/NR | MEC |  | Done: GIA
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | [9 empty] | ER | NPPD
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | [9 empty] | ER | SWPA
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | [9 empty] | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | [9 empty] | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-151 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | [9 empty] | ER | BEPC-SPP | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | [9 empty] | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | [9 empty] | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | [9 empty] | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | [9 empty] | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | [9 empty] | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | [9 empty] | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | [9 empty] | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | [9 empty] | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | [9 empty] | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | [9 empty] | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | [9 empty] | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | [9 empty] | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | [9 empty] | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 298 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-124 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 150 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 74 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal | 17 | [9 empty] | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | Wind | 100 | [9 empty] | ER/NR | XEL
ASGI-2017-006GIA-53 | 03 CENTRAL | 16.5 | Dis-16-2-PQ | Wind | 238 | [9 empty] | ER/NR | AECI
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | Wind | 246 | [9 empty] | ER/NR | AMMO
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.4 | [9 empty] | ER | SWPA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.73 | [9 empty] | ER | SWPA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | [9 empty] | ER | WFEC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | BEPC-SPP | Utica 230 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | [9 empty] | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | [9 empty] | ER | BEPC-SPP | Chappelle Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | [9 empty] | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 15.8 | [9 empty] | ER | KCPL |  | IA PENDING
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 29 | [9 empty] | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 10 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | [9 empty] | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | [9 empty] | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | [9 empty] | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 148.4 | [9 empty] | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | [9 empty] | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | [9 empty] | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-047 | 04 SOUTHEAST | 16 | DIS-16-1 | Thermal | 24 | [9 empty] | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | [9 empty] | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | [9 empty] | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | [9 empty] | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 169.2 | [9 empty] | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 57 | [9 empty] | ER | OKGE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | Thermal | 5 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | [9 empty] | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | BEPC-SPP | Tande 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-096 | 01 NORTH | 15 | DIS-15-2 | Wind | 150 | [9 empty] | ER | BEPC-SPP | Brady 230kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-064 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 197.8 | [9 empty] | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | [9 empty] | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 200.1 | [9 empty] | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-034 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 10.3 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | [9 empty] | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-057 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 100 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | [9 empty] | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 | [9 empty] | ER | WAPA
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC-SPP
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | [9 empty] | ER/NR | BEPC-SPP
GEN-2005-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | BEPC-SPP
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 53 | [9 empty] | ER/NR | WAPA
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | [9 empty] | ER/NR | XEL
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER/NR | BEPC-SPP
GEN-2007-013IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP
GEN-2007-014IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 50 | [9 empty] | ER/NR | BEPC-SPP
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | [9 empty] | ER/NR | BEPC-SPP
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 16 | [9 empty] | ER/NR | BEPC-SPP
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | [9 empty] | ER/NR | WAPA
GEN-2009-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 200 | [9 empty] | ER/NR | BEPC-SPP
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 | [9 empty] | ER | BEPC-SPP
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 80 | [9 empty] | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 | [9 empty] | ER/NR | BEPC-SPP
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | [9 empty] | ER/NR | BEPC-SPP
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 34 | [9 empty] | ER/NR | BEPC-SPP
GEN-2013-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 19.5 | [9 empty] | ER | WAPA
GEN-2014-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 103.24 | [9 empty] | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Gas | 125 | [9 empty] | ER/NR | BEPC-SPP
GEN-2014-010IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 150 | [9 empty] | ER/NR | BEPC-SPP
GEN-2014-014IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 150 | [9 empty] | ER/NR | BEPC-SPP
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | [9 empty] | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | [9 empty] | ER/NR | OPPD
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | [9 empty] | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | [9 empty] | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | [9 empty] | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | [9 empty] | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | [9 empty] | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | [9 empty] | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-004 | 04 SOUTHEAST | 14 | DIS-15-1 | Thermal | 56.4 | [9 empty] | ER | GRDA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | [9 empty] | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | [9 empty] | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | [9 empty] | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | [9 empty] | ER | SPS | Tap Cochran - Lehman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | [9 empty] | ER/NR | GRIS | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | [9 empty] | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-017 | 03 CENTRAL | 13 | DIS-14-2 | Thermal | 250 | [9 empty] | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 300 | [9 empty] | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | Thermal | 50 | [9 empty] | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2014-014 | 04 SOUTHEAST | 13 | DIS-14-2 | Thermal | 56.4 | [9 empty] | ER | GRDA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 100 | [9 empty] | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | [9 empty] | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | [9 empty] | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | [9 empty] | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | [9 empty] | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | [9 empty] | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 4 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | [9 empty] | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | [9 empty] | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | [9 empty] | ER | NPPD | Antelope 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-004 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 36.6 | [9 empty] | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Thermal | 75.6 | [9 empty] | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Thermal | 28 | [9 empty] | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 04 SOUTHEAST | 11 | DIS-13-2 | Thermal | 538 | [9 empty] | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | [9 empty] | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | [9 empty] | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 50.6 | [9 empty] | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | [9 empty] | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-010 | 04 SOUTHEAST | 10 | DIS-13-1 | Thermal | 620 | [9 empty] | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | [9 empty] | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 04 SOUTHEAST | 10 | DIS-13-1 | Thermal | 30 | [9 empty] | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 04 SOUTHEAST | 10 | DIS-13-1 | Thermal | 147 | [9 empty] | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | [9 empty] | ER | SPS
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | [9 empty] | ER | SPS
GEN-2013-016 | 05 SOUTHWEST | 10 | DIS-13-1 | Thermal | 203 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Thermal | 4.8 | [9 empty] | ER | LES | Terry Bundy Generating Station 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | [9 empty] | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | [9 empty] | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | [9 empty] | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 9 | DIS-12-2 | Thermal | 121.5 | [9 empty] | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 7 | [9 empty] | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 7 | [9 empty] | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 7 | [9 empty] | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 203 | [9 empty] | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | [9 empty] | ER | NPPD | Ainsworth Wind Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Thermal | 75 | [9 empty] | ER | NPPD | Columbus Co 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | [9 empty] | ER | NPPD | Petersburg North 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | [9 empty] | ER | NPPD | Bloomfield 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | [9 empty] | ER | OPPD | S1399 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBrokenBow | 02 NEBRASKA | 8 | PQ | Heat | 7.3 | [9 empty] | ER | NPPD
NPPDBuffaloCountySolar | 02 NEBRASKA | 8 | PQ | Solar | 10 | [9 empty] | ER | NPPD
NPPDBurtCountyWind | 02 NEBRASKA | 8 | PQ | Wind | 20 | [9 empty] | ER | NPPD
NPPDBurwell | 02 NEBRASKA | 8 | PQ | Heat | 3.3 | [9 empty] | ER | NPPD
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 15 | [9 empty] | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | [9 empty] | ER | NPPD
NPPDStuart | 02 NEBRASKA | 8 | PQ | Heat | 1.8 | [9 empty] | ER | NPPD
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | [9 empty] | ER | SUNC
ASGI-2012-008 | 03 CENTRAL | 8 | PQ | Gas | 3.655 | [9 empty] | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 03 CENTRAL | 8 | PQ | Thermal | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | [9 empty] | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | [9 empty] | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | Thermal | 50 | [9 empty] | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | [9 empty] | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 CENTRAL | 8 | PQ | Wind | 100.5 | [9 empty] | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | [9 empty] | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | [9 empty] | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 152 | [9 empty] | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | [9 empty] | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | [9 empty] | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 8 | DIS-12-1 | Thermal | 120 | [9 empty] | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GrayCountyWindMontezuma | 03 CENTRAL | 8 | PQ | Wind | 110 | [9 empty] | ER | SUNC
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | [9 empty] | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | [9 empty] | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | [9 empty] | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 04 SOUTHEAST | 8 | PQ | Wind | 100 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 04 SOUTHEAST | 8 | PQ | Wind | 20.6 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 30.6 | [9 empty] | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | [9 empty] | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | [9 empty] | ER | AEP | Arsenal Hill 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | [9 empty] | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | [9 empty] | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | [9 empty] | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | Wind | 40.8 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 05 SOUTHWEST | 8 | PQ | Wind | 120 | [9 empty] | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | [9 empty] | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | [9 empty] | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 05 SOUTHWEST | 8 | PQ | Wind | 159.1 | [9 empty] | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 05 SOUTHWEST | 8 | PQ | Thermal | 150 | [9 empty] | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 05 SOUTHWEST | 8 | PQ | Thermal | 150 | [9 empty] | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | Thermal | 168.1 | [9 empty] | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | [9 empty] | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 05 SOUTHWEST | 8 | PQ | Thermal | 604 | [9 empty] | ER | SPS | Hobbs 230kV & Hobbs 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | [9 empty] | ER | SPS | Tap Grassland Â- Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | [9 empty] | ER | SPS
SPSCarson | 05 SOUTHWEST | 8 | PQ | Wind | 10 | [9 empty] | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 10 | [9 empty] | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 10 | [9 empty] | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 10 | [9 empty] | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | [9 empty] | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 10 | [9 empty] | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | [9 empty] | ER | SPS
GEN-2011-056 | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | Jeffrey 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | [9 empty] | ER | NPPD | John 1 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 18 | [9 empty] | ER | NPPD
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | [9 empty] | ER | NPPD | John 2 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 18 | [9 empty] | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | [9 empty] | ER | NPPD
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | [9 empty] | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | [9 empty] | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 111 | [9 empty] | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | [9 empty] | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | [9 empty] | ER | SPS
GEN-2011-045 | 05 SOUTHWEST | 7 | DIS-11-2 | Thermal | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 05 SOUTHWEST | 7 | DIS-11-2 | Thermal | 23 | [9 empty] | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 05 SOUTHWEST | 7 | DIS-11-2 | Thermal | 175 | [9 empty] | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 6 | DIS-11-1 | Wind | 73.6 | [9 empty] | ER/NR | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-027 | 02 NEBRASKA | 6 | DIS-11-1 | Wind | 120 | [9 empty] | ER/NR | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-008 | 03 CENTRAL | 6 | DIS-11-1 | Thermal | 850 | [9 empty] | ER | KCPL |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | [9 empty] | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | [9 empty] | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 6 | DIS-11-1 | Thermal | 4.5 | [9 empty] | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | [9 empty] | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | [9 empty] | ER | SPS
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | [9 empty] | ER | SPS
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | [9 empty] | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-025 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | [9 empty] | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 5 | DIS-10-2 | Wind | 200 | [9 empty] | ER | NPPD | Wakefield 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | [9 empty] | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.757 | [9 empty] | ER | WERE
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | [9 empty] | ER | SPS
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | [9 empty] | ER | SPS
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | [9 empty] | ER | SPS
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | [9 empty] | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | [9 empty] | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 48.3 | [9 empty] | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 72 | [9 empty] | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | [9 empty] | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-009 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 165.6 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | [9 empty] | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 197.8 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 29.7 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 46.5 | [9 empty] | ER | SPS
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | [9 empty] | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | [9 empty] | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-006 | 05 SOUTHWEST | 4 | DIS-10-1 | Thermal | 205 | [9 empty] | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | [9 empty] | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-037N1 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 75 | [9 empty] | ER | NPPD | Broken Bow 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | [9 empty] | ER | OPPD | North Petersburg 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | [9 empty] | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-040 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 131.1 | [9 empty] | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | [9 empty] | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.5 | [9 empty] | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 | [9 empty] | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 CENTRAL | 3 | DIS-09-1 | Thermal | 72 | [9 empty] | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | [9 empty] | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | [9 empty] | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | [9 empty] | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | [9 empty] | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 04 SOUTHEAST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | [9 empty] | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 04 SOUTHEAST | 2 | ICS1 | Thermal | 150 | [9 empty] | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 2 | ICS1 | Wind | 424 | [9 empty] | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 2 | ICS1 | Wind | 101.2 | [9 empty] | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | [9 empty] | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | [9 empty] | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Seasonal LOIS
Gen Number | Group | Fuel Type | LOIS Time Period | MW Amount | LOIS Granted | Limiting Element | Limiting Upgrade | ERIS 24SP | ERIS 27SP | ERIS 27L | ERIS 27WP | NRIS 24SP | NRIS 27SP | NRIS 27L | NRIS 27WP | Stability 25SP | Stability 25WP
GEN-2023-012 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 98.6 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 68.5238 | 98.6 | 98.6 | 98.6 | 46.7469 | 98.6 | 98.6
GEN-2023-012 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 98.6 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 68.5238 | 98.6 | 98.6 | 98.6 | 46.7469 | 98.6 | 98.6
GEN-2023-012 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 98.6 | 68.5238 | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 ftlo POI 652532_1 | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1 | 0 | 0 | 0 | 68.5238 | 98.6 | 98.6 | 98.6 | 46.7469 | 98.6 | 98.6
GEN-2023-012 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 98.6 | 68.5238 | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 ftlo POI 652532_1 | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1 | 0 | 0 | 0 | 68.5238 | 98.6 | 98.6 | 98.6 | 46.7469 | 98.6 | 98.6
GEN-2023-012 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 98.6 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 0 | 68.5238 | 98.6 | 98.6 | 98.6 | 46.7469 | 98.6 | 98.6
GEN-2023-012 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 98.6 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 0 | 68.5238 | 98.6 | 98.6 | 98.6 | 46.7469 | 98.6 | 98.6
GEN-2023-012 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 98.6 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 68.5238 | 98.6 | 98.6 | 98.6 | 46.7469 | 98.6 | 98.6
GEN-2023-012 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 98.6 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 68.5238 | 98.6 | 98.6 | 98.6 | 46.7469 | 98.6 | 98.6
GEN-2023-062 | 01 NORTH | Thermal | April 1 - May 31 (Long Term) | 98 | 0 | Stability | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 98 | 97.4069 | 98 | 61.7344 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-062 | 01 NORTH | Thermal | April 1 - May 31 (Near Term) | 98 | 0 | Stability | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 98 | 97.4069 | 98 | 61.7344 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-062 | 01 NORTH | Thermal | Dec 1 - March 31 (Long Term) | 98 | 0 | Stability | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 98 | 97.4069 | 98 | 61.7344 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-062 | 01 NORTH | Thermal | Dec 1 - March 31 (Near Term) | 98 | 0 | Stability | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 98 | 97.4069 | 98 | 61.7344 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-062 | 01 NORTH | Thermal | June 1 - Sept 30 (Long Term) | 98 | 0 | Stability | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 98 | 97.4069 | 98 | 61.7344 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-062 | 01 NORTH | Thermal | June 1 - Sept 30 (Near Term) | 98 | 0 | Stability | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 98 | 97.4069 | 98 | 61.7344 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-062 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Long Term) | 98 | 0 | Stability | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 98 | 97.4069 | 98 | 61.7344 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-062 | 01 NORTH | Thermal | Oct 1 - Nov 30 (Near Term) | 98 | 0 | Stability | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 98 | 97.4069 | 98 | 61.7344 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-082 | 01 NORTH | Battery/Storage | April 1 - May 31 (Long Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 152.7996 | 175 | 175 | N/A | 175 | 175 | 175
GEN-2023-082 | 01 NORTH | Battery/Storage | April 1 - May 31 (Near Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 152.7996 | 175 | 175 | N/A | 175 | 175 | 175
GEN-2023-082 | 01 NORTH | Battery/Storage | Dec 1 - March 31 (Long Term) | 175 | 175 | none | none | 0 | 0 | 175 | 152.7996 | 175 | 175 | N/A | 175 | 175 | 175
GEN-2023-082 | 01 NORTH | Battery/Storage | Dec 1 - March 31 (Near Term) | 175 | 175 | none | none | 0 | 0 | 175 | 152.7996 | 175 | 175 | N/A | 175 | 175 | 175
GEN-2023-082 | 01 NORTH | Battery/Storage | June 1 - Sept 30 (Long Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 152.7996 | 175 | 175 | N/A | 175 | 175 | 175
GEN-2023-082 | 01 NORTH | Battery/Storage | June 1 - Sept 30 (Near Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 152.7996 | 175 | 175 | N/A | 175 | 175 | 175
GEN-2023-082 | 01 NORTH | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 152.7996 | 175 | 175 | N/A | 175 | 175 | 175
GEN-2023-082 | 01 NORTH | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 152.7996 | 175 | 175 | N/A | 175 | 175 | 175
GEN-2023-097 | 01 NORTH | Battery/Storage | April 1 - May 31 (Long Term) | 250 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 250 | 0 | 250 | 250 | N/A | 0 | 0 | 0
GEN-2023-097 | 01 NORTH | Battery/Storage | April 1 - May 31 (Near Term) | 250 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 250 | 0 | 250 | 250 | N/A | 0 | 0 | 0
GEN-2023-097 | 01 NORTH | Battery/Storage | Dec 1 - March 31 (Long Term) | 250 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 250 | 0 | 250 | 250 | N/A | 0 | 0 | 0
GEN-2023-097 | 01 NORTH | Battery/Storage | Dec 1 - March 31 (Near Term) | 250 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 250 | 0 | 250 | 250 | N/A | 0 | 0 | 0
GEN-2023-097 | 01 NORTH | Battery/Storage | June 1 - Sept 30 (Long Term) | 250 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 250 | 0 | 250 | 250 | N/A | 0 | 0 | 0
GEN-2023-097 | 01 NORTH | Battery/Storage | June 1 - Sept 30 (Near Term) | 250 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 250 | 0 | 250 | 250 | N/A | 0 | 0 | 0
GEN-2023-097 | 01 NORTH | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 250 | 0 | 250 | 250 | N/A | 0 | 0 | 0
GEN-2023-097 | 01 NORTH | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 250 | 0 | 250 | 250 | N/A | 0 | 0 | 0
GEN-2023-105 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 249 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 0 | 249 | 249 | 249 | 118.0526 | 0 | 0
GEN-2023-105 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 249 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 0 | 249 | 249 | 249 | 118.0526 | 0 | 0
GEN-2023-105 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 249 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 0 | 0 | 249 | 249 | 249 | 118.0526 | 0 | 0
GEN-2023-105 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 249 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 0 | 0 | 249 | 249 | 249 | 118.0526 | 0 | 0
GEN-2023-105 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 249 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 0 | 0 | 249 | 249 | 249 | 118.0526 | 0 | 0
GEN-2023-105 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 249 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 0 | 0 | 249 | 249 | 249 | 118.0526 | 0 | 0
GEN-2023-105 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 249 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 0 | 249 | 249 | 249 | 118.0526 | 0 | 0
GEN-2023-105 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 249 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 0 | 249 | 249 | 249 | 118.0526 | 0 | 0
GEN-2023-154 | 01 NORTH | Solar | April 1 - May 31 (Long Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 116.152 | N/A | N/A | N/A | N/A | 175 | 175
GEN-2023-154 | 01 NORTH | Solar | April 1 - May 31 (Near Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 116.152 | N/A | N/A | N/A | N/A | 175 | 175
GEN-2023-154 | 01 NORTH | Solar | Dec 1 - March 31 (Long Term) | 175 | 116.152 | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 ftlo POI 652532_1 | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | 0 | 0 | 175 | 116.152 | N/A | N/A | N/A | N/A | 175 | 175
GEN-2023-154 | 01 NORTH | Solar | Dec 1 - March 31 (Near Term) | 175 | 116.152 | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 ftlo POI 652532_1 | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | 0 | 0 | 175 | 116.152 | N/A | N/A | N/A | N/A | 175 | 175
GEN-2023-154 | 01 NORTH | Solar | June 1 - Sept 30 (Long Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 116.152 | N/A | N/A | N/A | N/A | 175 | 175
GEN-2023-154 | 01 NORTH | Solar | June 1 - Sept 30 (Near Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 116.152 | N/A | N/A | N/A | N/A | 175 | 175
GEN-2023-154 | 01 NORTH | Solar | Oct 1 - Nov 30 (Long Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 116.152 | N/A | N/A | N/A | N/A | 175 | 175
GEN-2023-154 | 01 NORTH | Solar | Oct 1 - Nov 30 (Near Term) | 175 | 0 | Voltage: 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 0 | 0 | 175 | 116.152 | N/A | N/A | N/A | N/A | 175 | 175
GEN-2023-182 | 01 NORTH | Wind | April 1 - May 31 (Long Term) | 300 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-182 | 01 NORTH | Wind | April 1 - May 31 (Near Term) | 300 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-182 | 01 NORTH | Wind | Dec 1 - March 31 (Long Term) | 300 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-182 | 01 NORTH | Wind | Dec 1 - March 31 (Near Term) | 300 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-182 | 01 NORTH | Wind | June 1 - Sept 30 (Long Term) | 300 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-182 | 01 NORTH | Wind | June 1 - Sept 30 (Near Term) | 300 | 0 | Non-Converged: 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-182 | 01 NORTH | Wind | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-182 | 01 NORTH | Wind | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Non-Converged: 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-011 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 190 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 157.3958 | 157.2125 | 65.4198 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-011 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 190 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 157.3958 | 157.2125 | 65.4198 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-011 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 190 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 157.3958 | 157.2125 | 65.4198 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-011 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 190 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 157.3958 | 157.2125 | 65.4198 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-011 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 190 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 157.3958 | 157.2125 | 65.4198 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-011 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 190 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 157.3958 | 157.2125 | 65.4198 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-011 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 190 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 157.3958 | 157.2125 | 65.4198 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-011 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 190 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 157.3958 | 157.2125 | 65.4198 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-077 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-077 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-077 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-077 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-077 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-077 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-077 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-077 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-078 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-078 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-078 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-078 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-078 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-078 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-078 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-078 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 255 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 159.3982 | 159.4319 | 255 | 160.6355 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-079 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 303 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 189.4026 | 189.4426 | 303 | 190.8728 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-079 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 303 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 189.4026 | 189.4426 | 303 | 190.8728 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-079 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 303 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 189.4026 | 189.4426 | 303 | 190.8728 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-079 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 303 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 189.4026 | 189.4426 | 303 | 190.8728 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-079 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 303 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 189.4026 | 189.4426 | 303 | 190.8728 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-079 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 303 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 189.4026 | 189.4426 | 303 | 190.8728 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-079 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 303 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 189.4026 | 189.4426 | 303 | 190.8728 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-079 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 303 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 189.4026 | 189.4426 | 303 | 190.8728 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-116 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 500 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-116 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 500 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-116 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 500 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-116 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 500 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-116 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 500 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-116 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 500 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-116 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 500 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-116 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 500 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-117 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 300 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-117 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 300 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-117 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 300 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-117 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 300 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-117 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 300 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-117 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 300 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-117 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-117 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-133 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 240.2706 | 233.899 | 162.3838 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-133 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 240.2706 | 233.899 | 162.3838 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-133 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 240.2706 | 233.899 | 162.3838 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-133 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 240.2706 | 233.899 | 162.3838 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-133 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 240.2706 | 233.899 | 162.3838 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-133 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 240.2706 | 233.899 | 162.3838 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-133 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 240.2706 | 233.899 | 162.3838 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-133 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 240.2706 | 233.899 | 162.3838 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-153 | 02 NEBRASKA | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 120 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 120 | 0 | 120 | 120 | N/A | 56.8928 | 0 | 0
GEN-2023-153 | 02 NEBRASKA | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 120 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 120 | 0 | 120 | 120 | N/A | 56.8928 | 0 | 0
GEN-2023-153 | 02 NEBRASKA | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 120 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 120 | 0 | 120 | 120 | N/A | 56.8928 | 0 | 0
GEN-2023-153 | 02 NEBRASKA | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 120 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 120 | 0 | 120 | 120 | N/A | 56.8928 | 0 | 0
GEN-2023-153 | 02 NEBRASKA | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 120 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 120 | 0 | 120 | 120 | N/A | 56.8928 | 0 | 0
GEN-2023-153 | 02 NEBRASKA | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 120 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 120 | 0 | 120 | 120 | N/A | 56.8928 | 0 | 0
GEN-2023-153 | 02 NEBRASKA | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 120 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 120 | 0 | 120 | 120 | N/A | 56.8928 | 0 | 0
GEN-2023-153 | 02 NEBRASKA | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 120 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 120 | 0 | 120 | 120 | N/A | 56.8928 | 0 | 0
GEN-2023-199 | 02 NEBRASKA | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 250 | 0 | 208.033 | 174.3241 | N/A | 0 | 0 | 0
GEN-2023-199 | 02 NEBRASKA | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 250 | 0 | 208.033 | 174.3241 | N/A | 0 | 0 | 0
GEN-2023-199 | 02 NEBRASKA | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 250 | 0 | 208.033 | 174.3241 | N/A | 0 | 0 | 0
GEN-2023-199 | 02 NEBRASKA | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 250 | 0 | 208.033 | 174.3241 | N/A | 0 | 0 | 0
GEN-2023-199 | 02 NEBRASKA | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 250 | 0 | 208.033 | 174.3241 | N/A | 0 | 0 | 0
GEN-2023-199 | 02 NEBRASKA | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 250 | 0 | 208.033 | 174.3241 | N/A | 0 | 0 | 0
GEN-2023-199 | 02 NEBRASKA | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 250 | 0 | 208.033 | 174.3241 | N/A | 0 | 0 | 0
GEN-2023-199 | 02 NEBRASKA | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 250 | 0 | 208.033 | 174.3241 | N/A | 0 | 0 | 0
GEN-2023-216 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-216 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-216 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-216 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-216 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-216 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-216 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-216 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-217 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-217 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-217 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-217 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-217 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-217 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-217 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-217 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-218 | 02 NEBRASKA | Wind | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-218 | 02 NEBRASKA | Wind | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-218 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-218 | 02 NEBRASKA | Wind | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-218 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-218 | 02 NEBRASKA | Wind | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-218 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-218 | 02 NEBRASKA | Wind | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 0 | 0 | 0 | 0 | 24.0661 | 5.7479 | 200 | 0 | 0 | 0
GEN-2023-222 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 478 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 241.9735 | 249.593 | 478 | 0 | 195.3982 | 189.306 | N/A | 0 | 0 | 0
GEN-2023-222 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 478 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 241.9735 | 249.593 | 478 | 0 | 195.3982 | 189.306 | N/A | 0 | 0 | 0
GEN-2023-222 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 478 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 241.9735 | 249.593 | 478 | 0 | 195.3982 | 189.306 | N/A | 0 | 0 | 0
GEN-2023-222 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 478 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 241.9735 | 249.593 | 478 | 0 | 195.3982 | 189.306 | N/A | 0 | 0 | 0
GEN-2023-222 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 478 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 241.9735 | 249.593 | 478 | 0 | 195.3982 | 189.306 | N/A | 0 | 0 | 0
GEN-2023-222 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 478 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 241.9735 | 249.593 | 478 | 0 | 195.3982 | 189.306 | N/A | 0 | 0 | 0
GEN-2023-222 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 478 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 241.9735 | 249.593 | 478 | 0 | 195.3982 | 189.306 | N/A | 0 | 0 | 0
GEN-2023-222 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 478 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 241.9735 | 249.593 | 478 | 0 | 195.3982 | 189.306 | N/A | 0 | 0 | 0
GEN-2023-223 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 239 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 120.9868 | 124.7965 | 239 | 0 | 97.6991 | 94.653 | N/A | 0 | 0 | 0
GEN-2023-223 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 239 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 120.9868 | 124.7965 | 239 | 0 | 97.6991 | 94.653 | N/A | 0 | 0 | 0
GEN-2023-223 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 239 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 120.9868 | 124.7965 | 239 | 0 | 97.6991 | 94.653 | N/A | 0 | 0 | 0
GEN-2023-223 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 239 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 120.9868 | 124.7965 | 239 | 0 | 97.6991 | 94.653 | N/A | 0 | 0 | 0
GEN-2023-223 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 239 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 120.9868 | 124.7965 | 239 | 0 | 97.6991 | 94.653 | N/A | 0 | 0 | 0
GEN-2023-223 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 239 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 120.9868 | 124.7965 | 239 | 0 | 97.6991 | 94.653 | N/A | 0 | 0 | 0
GEN-2023-223 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 239 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 120.9868 | 124.7965 | 239 | 0 | 97.6991 | 94.653 | N/A | 0 | 0 | 0
GEN-2023-223 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 239 | 0 | Stability | Build a new G23-222-POI to MONOLITH 3 345 kV line 1 | 120.9868 | 124.7965 | 239 | 0 | 97.6991 | 94.653 | N/A | 0 | 0 | 0
GEN-2023-224 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 478 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 298.909 | 305.2666 | 478 | 301.1129 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-224 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 478 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 298.909 | 305.2666 | 478 | 301.1129 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-224 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 478 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 298.909 | 305.2666 | 478 | 301.1129 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-224 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 478 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 298.909 | 305.2666 | 478 | 301.1129 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-224 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 478 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 298.909 | 305.2666 | 478 | 301.1129 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-224 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 478 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 298.909 | 305.2666 | 478 | 301.1129 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-224 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 478 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 298.909 | 305.2666 | 478 | 301.1129 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-224 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 478 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 298.909 | 305.2666 | 478 | 301.1129 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-225 | 02 NEBRASKA | Thermal | April 1 - May 31 (Long Term) | 217 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 135.6972 | 138.5834 | 217 | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-225 | 02 NEBRASKA | Thermal | April 1 - May 31 (Near Term) | 217 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 135.6972 | 138.5834 | 217 | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-225 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Long Term) | 217 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 135.6972 | 138.5834 | 217 | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-225 | 02 NEBRASKA | Thermal | Dec 1 - March 31 (Near Term) | 217 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 135.6972 | 138.5834 | 217 | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-225 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Long Term) | 217 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 135.6972 | 138.5834 | 217 | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-225 | 02 NEBRASKA | Thermal | June 1 - Sept 30 (Near Term) | 217 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 135.6972 | 138.5834 | 217 | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-225 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Long Term) | 217 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 135.6972 | 138.5834 | 217 | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-225 | 02 NEBRASKA | Thermal | Oct 1 - Nov 30 (Near Term) | 217 | 0 | Stability | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 135.6972 | 138.5834 | 217 | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-006 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 202 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 202 | 0 | 202 | 19.5156 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-006 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 202 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 202 | 0 | 202 | 19.5156 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-006 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 202 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 202 | 0 | 202 | 19.5156 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-006 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 202 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 202 | 0 | 202 | 19.5156 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-006 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 202 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 202 | 0 | 202 | 19.5156 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-006 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 202 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 202 | 0 | 202 | 19.5156 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-006 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 202 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 202 | 0 | 202 | 19.5156 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-006 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 202 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 202 | 0 | 202 | 19.5156 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-015 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 330 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 330 | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-015 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 330 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 330 | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-015 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 330 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 330 | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-015 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 330 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 330 | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-015 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 330 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 330 | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-015 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 330 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 330 | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-015 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 330 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 330 | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-015 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 330 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 330 | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-023 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-023 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-023 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-023 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-023 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-023 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-023 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-023 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-032 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 200 | 175.2214 | 541264 LEX69 2 69.0 541232 LEX161 5 161 1 ftlo 541229 ODESSA 5 161 772620 G23-032-TAP 161 1 | Upgrade the existing LEX161 5 161/69 kV Transformer | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 199.7665 | N/A | 175.2214 | 200 | 200
GEN-2023-032 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 200 | 175.2214 | 541264 LEX69 2 69.0 541232 LEX161 5 161 1 ftlo 541229 ODESSA 5 161 772620 G23-032-TAP 161 1 | Upgrade the existing LEX161 5 161/69 kV Transformer | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 199.7665 | N/A | 175.2214 | 200 | 200
GEN-2023-032 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 200 | 175.2214 | 541264 LEX69 2 69.0 541232 LEX161 5 161 1 ftlo 541229 ODESSA 5 161 772620 G23-032-TAP 161 1 | Upgrade the existing LEX161 5 161/69 kV Transformer | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 199.7665 | N/A | 175.2214 | 200 | 200
GEN-2023-032 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 200 | 175.2214 | 541264 LEX69 2 69.0 541232 LEX161 5 161 1 ftlo 541229 ODESSA 5 161 772620 G23-032-TAP 161 1 | Upgrade the existing LEX161 5 161/69 kV Transformer | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 199.7665 | N/A | 175.2214 | 200 | 200
GEN-2023-032 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 200 | 199.7665 | 541264 LEX69 2 69.0 541232 LEX161 5 161 1 ftlo 541229 ODESSA 5 161 772620 G23-032-TAP 161 1 | Upgrade the existing LEX161 5 161/69 kV Transformer | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 199.7665 | N/A | 175.2214 | 200 | 200
GEN-2023-032 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 199.7665 | N/A | 175.2214 | 200 | 200
GEN-2023-032 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 175.2214 | 541264 LEX69 2 69.0 541232 LEX161 5 161 1 ftlo 541229 ODESSA 5 161 772620 G23-032-TAP 161 1 | Upgrade the existing LEX161 5 161/69 kV Transformer | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 199.7665 | N/A | 175.2214 | 200 | 200
GEN-2023-032 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 175.2214 | 541264 LEX69 2 69.0 541232 LEX161 5 161 1 ftlo 541229 ODESSA 5 161 772620 G23-032-TAP 161 1 | Upgrade the existing LEX161 5 161/69 kV Transformer | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 199.7665 | N/A | 175.2214 | 200 | 200
GEN-2023-033 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 147.8661 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 ftlo: 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | 134.2712 | 169.7536 | 200 | 147.8661 | 136.1997 | 79.1592 | N/A | 192.4741 | 200 | 200
GEN-2023-033 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 136.1997 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 ftlo 541198 PECULR 7 345 542968 STILWEL7 345 1 | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | 134.2712 | 169.7536 | 200 | 147.8661 | 136.1997 | 79.1592 | N/A | 192.4741 | 200 | 200
GEN-2023-033 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 192.4741 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 ftlo 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | 134.2712 | 169.7536 | 200 | 147.8661 | 136.1997 | 79.1592 | N/A | 192.4741 | 200 | 200
GEN-2023-033 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 192.4741 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 ftlo 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | 134.2712 | 169.7536 | 200 | 147.8661 | 136.1997 | 79.1592 | N/A | 192.4741 | 200 | 200
GEN-2023-033 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 169.7536 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 ftlo: 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | 134.2712 | 169.7536 | 200 | 147.8661 | 136.1997 | 79.1592 | N/A | 192.4741 | 200 | 200
GEN-2023-033 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 136.1997 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 ftlo 541198 PECULR 7 345 542968 STILWEL7 345 1 | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | 134.2712 | 169.7536 | 200 | 147.8661 | 136.1997 | 79.1592 | N/A | 192.4741 | 200 | 200
GEN-2023-033 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 147.8661 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 ftlo: 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | 134.2712 | 169.7536 | 200 | 147.8661 | 136.1997 | 79.1592 | N/A | 192.4741 | 200 | 200
GEN-2023-033 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 136.1997 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 ftlo 541198 PECULR 7 345 542968 STILWEL7 345 1 | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | 134.2712 | 169.7536 | 200 | 147.8661 | 136.1997 | 79.1592 | N/A | 192.4741 | 200 | 200
GEN-2023-034 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 130 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 90.2823 | 130 | 72.8812 | 130 | 130 | N/A | 130 | 0 | 0
GEN-2023-034 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 130 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 90.2823 | 130 | 72.8812 | 130 | 130 | N/A | 130 | 0 | 0
GEN-2023-034 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 130 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 90.2823 | 130 | 72.8812 | 130 | 130 | N/A | 130 | 0 | 0
GEN-2023-034 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 130 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 90.2823 | 130 | 72.8812 | 130 | 130 | N/A | 130 | 0 | 0
GEN-2023-034 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 130 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 90.2823 | 130 | 72.8812 | 130 | 130 | N/A | 130 | 0 | 0
GEN-2023-034 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 130 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 90.2823 | 130 | 72.8812 | 130 | 130 | N/A | 130 | 0 | 0
GEN-2023-034 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 130 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 90.2823 | 130 | 72.8812 | 130 | 130 | N/A | 130 | 0 | 0
GEN-2023-034 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 130 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 90.2823 | 130 | 72.8812 | 130 | 130 | N/A | 130 | 0 | 0
GEN-2023-036 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 165 | 165 | none | none | 110.7737 | 154.6673 | 165 | 121.9895 | 165 | 165 | N/A | 165 | 165 | 165
GEN-2023-036 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 165 | 165 | none | none | 110.7737 | 154.6673 | 165 | 121.9895 | 165 | 165 | N/A | 165 | 165 | 165
GEN-2023-036 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 165 | 165 | none | none | 110.7737 | 154.6673 | 165 | 121.9895 | 165 | 165 | N/A | 165 | 165 | 165
GEN-2023-036 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 165 | 165 | none | none | 110.7737 | 154.6673 | 165 | 121.9895 | 165 | 165 | N/A | 165 | 165 | 165
GEN-2023-036 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 165 | 165 | none | none | 110.7737 | 154.6673 | 165 | 121.9895 | 165 | 165 | N/A | 165 | 165 | 165
GEN-2023-036 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 165 | 165 | none | none | 110.7737 | 154.6673 | 165 | 121.9895 | 165 | 165 | N/A | 165 | 165 | 165
GEN-2023-036 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 165 | 165 | none | none | 110.7737 | 154.6673 | 165 | 121.9895 | 165 | 165 | N/A | 165 | 165 | 165
GEN-2023-036 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 165 | 165 | none | none | 110.7737 | 154.6673 | 165 | 121.9895 | 165 | 165 | N/A | 165 | 165 | 165
GEN-2023-037 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-037 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-037 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-037 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-037 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-037 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-037 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-037 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 200 | none | none | 134.2712 | 187.4756 | 200 | 147.8661 | 200 | 200 | N/A | 200 | 200 | 200
GEN-2023-050 | 03 CENTRAL | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 400 | 102.5027 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 ftlo Potential P4 Event - POI 532793_1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 0 | 400 | 38.6447 | 35.2818 | 172.6712 | N/A | 102.5027 | 400 | 400
GEN-2023-050 | 03 CENTRAL | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 400 | 35.2818 | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 ftlo 547469 RIV4525 161 764310 G20-079-TAP 161 1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 0 | 400 | 38.6447 | 35.2818 | 172.6712 | N/A | 102.5027 | 400 | 400
GEN-2023-050 | 03 CENTRAL | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 400 | 102.5027 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 ftlo Potential P4 Event - POI 532793_1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 0 | 400 | 38.6447 | 35.2818 | 172.6712 | N/A | 102.5027 | 400 | 400
GEN-2023-050 | 03 CENTRAL | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 400 | 102.5027 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 ftlo Potential P4 Event - POI 532793_1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 0 | 400 | 38.6447 | 35.2818 | 172.6712 | N/A | 102.5027 | 400 | 400
GEN-2023-050 | 03 CENTRAL | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 400 | 172.6712 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 ftlo Potential P4 Event - POI 532793_1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 0 | 400 | 38.6447 | 35.2818 | 172.6712 | N/A | 102.5027 | 400 | 400
GEN-2023-050 | 03 CENTRAL | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 400 | 35.2818 | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 ftlo 547469 RIV4525 161 764310 G20-079-TAP 161 1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 0 | 400 | 38.6447 | 35.2818 | 172.6712 | N/A | 102.5027 | 400 | 400
GEN-2023-050 | 03 CENTRAL | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 400 | 102.5027 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 ftlo Potential P4 Event - POI 532793_1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 0 | 400 | 38.6447 | 35.2818 | 172.6712 | N/A | 102.5027 | 400 | 400
GEN-2023-050 | 03 CENTRAL | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 400 | 35.2818 | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 ftlo 547469 RIV4525 161 764310 G20-079-TAP 161 1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 0 | 400 | 38.6447 | 35.2818 | 172.6712 | N/A | 102.5027 | 400 | 400
GEN-2023-061 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 100 | 58.2729 | 508359 WELSH 7 345 508841 WILKES 7 345 1 ftlo P23:345:AEPW:WELSH CB 11990 NBTB:::: | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line | 100 | 100 | 100 | 0 | 71.7541 | 86.5492 | N/A | 58.2729 | 100 | 100
GEN-2023-061 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 100 | 58.2729 | 508359 WELSH 7 345 508841 WILKES 7 345 1 ftlo P23:345:AEPW:WELSH CB 11990 NBTB:::: | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line | 100 | 100 | 100 | 0 | 71.7541 | 86.5492 | N/A | 58.2729 | 100 | 100
GEN-2023-061 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 100 | 58.2729 | 508359 WELSH 7 345 508841 WILKES 7 345 1 ftlo P23:345:AEPW:WELSH CB 11990 NBTB:::: | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line | 100 | 100 | 100 | 0 | 71.7541 | 86.5492 | N/A | 58.2729 | 100 | 100
GEN-2023-061 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 100 | 58.2729 | 508359 WELSH 7 345 508841 WILKES 7 345 1 ftlo P23:345:AEPW:WELSH CB 11990 NBTB:::: | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line | 100 | 100 | 100 | 0 | 71.7541 | 86.5492 | N/A | 58.2729 | 100 | 100
GEN-2023-061 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 100 | 100 | none | none | 100 | 100 | 100 | 0 | 71.7541 | 86.5492 | N/A | 58.2729 | 100 | 100
GEN-2023-061 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 100 | 100 | none | none | 100 | 100 | 100 | 0 | 71.7541 | 86.5492 | N/A | 58.2729 | 100 | 100
GEN-2023-061 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 58.2729 | 508359 WELSH 7 345 508841 WILKES 7 345 1 ftlo P23:345:AEPW:WELSH CB 11990 NBTB:::: | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line | 100 | 100 | 100 | 0 | 71.7541 | 86.5492 | N/A | 58.2729 | 100 | 100
GEN-2023-061 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 58.2729 | 508359 WELSH 7 345 508841 WILKES 7 345 1 ftlo P23:345:AEPW:WELSH CB 11990 NBTB:::: | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line | 100 | 100 | 100 | 0 | 71.7541 | 86.5492 | N/A | 58.2729 | 100 | 100
GEN-2023-065 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 140 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 97.2271 | 140 | 127.8993 | 140 | 140 | N/A | 140 | 0 | 0
GEN-2023-065 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 140 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 97.2271 | 140 | 127.8993 | 140 | 140 | N/A | 140 | 0 | 0
GEN-2023-065 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 140 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 97.2271 | 140 | 127.8993 | 140 | 140 | N/A | 140 | 0 | 0
GEN-2023-065 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 140 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 97.2271 | 140 | 127.8993 | 140 | 140 | N/A | 140 | 0 | 0
GEN-2023-065 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 140 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 97.2271 | 140 | 127.8993 | 140 | 140 | N/A | 140 | 0 | 0
GEN-2023-065 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 140 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 97.2271 | 140 | 127.8993 | 140 | 140 | N/A | 140 | 0 | 0
GEN-2023-065 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 140 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 97.2271 | 140 | 127.8993 | 140 | 140 | N/A | 140 | 0 | 0
GEN-2023-065 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 140 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 97.2271 | 140 | 127.8993 | 140 | 140 | N/A | 140 | 0 | 0
GEN-2023-073 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-073 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-073 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-073 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-073 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-073 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-073 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-073 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-085 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 150 | 113.6977 | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 ftlo 300042 7HUBEN 345 300045 7MORGAN 345 1 | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 | 150 | 150 | 71.1319 | 150 | 133.8277 | 146.9299 | 113.6977 | 87.4093 | 150 | 150
GEN-2023-085 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 150 | 113.6977 | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 ftlo 300042 7HUBEN 345 300045 7MORGAN 345 1 | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 | 150 | 150 | 71.1319 | 150 | 133.8277 | 146.9299 | 113.6977 | 87.4093 | 150 | 150
GEN-2023-085 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | 150 | 150 | 71.1319 | 150 | 133.8277 | 146.9299 | 113.6977 | 87.4093 | 150 | 150
GEN-2023-085 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | 150 | 150 | 71.1319 | 150 | 133.8277 | 146.9299 | 113.6977 | 87.4093 | 150 | 150
GEN-2023-085 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | 150 | 150 | 71.1319 | 150 | 133.8277 | 146.9299 | 113.6977 | 87.4093 | 150 | 150
GEN-2023-085 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 150 | 150 | None | None | 150 | 150 | 71.1319 | 150 | 133.8277 | 146.9299 | 113.6977 | 87.4093 | 150 | 150
GEN-2023-085 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 150 | 113.6977 | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 ftlo 300042 7HUBEN 345 300045 7MORGAN 345 1 | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 | 150 | 150 | 71.1319 | 150 | 133.8277 | 146.9299 | 113.6977 | 87.4093 | 150 | 150
GEN-2023-085 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 150 | 113.6977 | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 ftlo 300042 7HUBEN 345 300045 7MORGAN 345 1 | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 | 150 | 150 | 71.1319 | 150 | 133.8277 | 146.9299 | 113.6977 | 87.4093 | 150 | 150
GEN-2023-087 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 200 | 0 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | 134.2712 | 0 | 200 | 147.8661 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2023-087 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 200 | 134.2712 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 ftlo: P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | 134.2712 | 0 | 200 | 147.8661 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2023-087 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 200 | 147.8661 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 ftlo: 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | 134.2712 | 0 | 200 | 147.8661 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2023-087 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 200 | 147.8661 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 ftlo: 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | 134.2712 | 0 | 200 | 147.8661 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2023-087 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | 134.2712 | 0 | 200 | 147.8661 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2023-087 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 200 | 134.2712 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 ftlo: P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | 134.2712 | 0 | 200 | 147.8661 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2023-087 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | 134.2712 | 0 | 200 | 147.8661 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2023-087 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 134.2712 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 ftlo: P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | 134.2712 | 0 | 200 | 147.8661 | N/A | N/A | N/A | N/A | 200 | 200
GEN-2023-099 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 300 | 24.2605 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: POI 532772_9 | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 24.2605 | 300 | 168.1873 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2023-099 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 300 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 24.2605 | 300 | 168.1873 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2023-099 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 300 | 168.1873 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 24.2605 | 300 | 168.1873 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2023-099 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 300 | 168.1873 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 24.2605 | 300 | 168.1873 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2023-099 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 300 | 24.2605 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: POI 532772_9 | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 24.2605 | 300 | 168.1873 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2023-099 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 300 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 24.2605 | 300 | 168.1873 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2023-099 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 300 | 24.2605 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: POI 532772_9 | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 24.2605 | 300 | 168.1873 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2023-099 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 300 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 24.2605 | 300 | 168.1873 | N/A | N/A | N/A | N/A | 300 | 300
GEN-2023-107 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 300 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-107 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 300 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-107 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 300 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-107 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 300 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-107 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 300 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-107 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 300 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-107 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-107 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-149 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 300 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 0 | 300 | 168.1873 | 0 | 0 | N/A | 0 | 300 | 300
GEN-2023-149 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 300 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 0 | 300 | 168.1873 | 0 | 0 | N/A | 0 | 300 | 300
GEN-2023-149 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 300 | 168.1873 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 0 | 300 | 168.1873 | 0 | 0 | N/A | 0 | 300 | 300
GEN-2023-149 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 300 | 168.1873 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 0 | 300 | 168.1873 | 0 | 0 | N/A | 0 | 300 | 300
GEN-2023-149 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 300 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 0 | 300 | 168.1873 | 0 | 0 | N/A | 0 | 300 | 300
GEN-2023-149 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 300 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 0 | 300 | 168.1873 | 0 | 0 | N/A | 0 | 300 | 300
GEN-2023-149 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 300 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 0 | 300 | 168.1873 | 0 | 0 | N/A | 0 | 300 | 300
GEN-2023-149 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 300 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 0 | 300 | 168.1873 | 0 | 0 | N/A | 0 | 300 | 300
GEN-2023-169 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 125 | 49.7876 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 ftlo: P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | 79.1797 | 49.7876 | 125 | 92.4163 | 85.1248 | 49.4745 | N/A | 120.2963 | 125 | 125
GEN-2023-169 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 125 | 85.1248 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 ftlo 541198 PECULR 7 345 542968 STILWEL7 345 1 | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | 79.1797 | 49.7876 | 125 | 92.4163 | 85.1248 | 49.4745 | N/A | 120.2963 | 125 | 125
GEN-2023-169 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 125 | 120.2963 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 ftlo 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | 79.1797 | 49.7876 | 125 | 92.4163 | 85.1248 | 49.4745 | N/A | 120.2963 | 125 | 125
GEN-2023-169 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 125 | 120.2963 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 ftlo 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | 79.1797 | 49.7876 | 125 | 92.4163 | 85.1248 | 49.4745 | N/A | 120.2963 | 125 | 125
GEN-2023-169 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 125 | 49.7876 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 ftlo: P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | 79.1797 | 49.7876 | 125 | 92.4163 | 85.1248 | 49.4745 | N/A | 120.2963 | 125 | 125
GEN-2023-169 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 125 | 85.1248 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 ftlo 541198 PECULR 7 345 542968 STILWEL7 345 1 | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | 79.1797 | 49.7876 | 125 | 92.4163 | 85.1248 | 49.4745 | N/A | 120.2963 | 125 | 125
GEN-2023-169 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 125 | 49.7876 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 ftlo: P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | 79.1797 | 49.7876 | 125 | 92.4163 | 85.1248 | 49.4745 | N/A | 120.2963 | 125 | 125
GEN-2023-169 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 125 | 85.1248 | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 ftlo 541198 PECULR 7 345 542968 STILWEL7 345 1 | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | 79.1797 | 49.7876 | 125 | 92.4163 | 85.1248 | 49.4745 | N/A | 120.2963 | 125 | 125
GEN-2023-170 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 150 | 150 | None | None | 132.7655 | 150 | 150 | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2023-170 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 150 | 132.7655 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 ftlo POI 532793_12 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | 132.7655 | 150 | 150 | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2023-170 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 150 | 150 | None | None | 132.7655 | 150 | 150 | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2023-170 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 150 | 150 | None | None | 132.7655 | 150 | 150 | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2023-170 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 150 | 150 | None | None | 132.7655 | 150 | 150 | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2023-170 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 150 | 132.7655 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 ftlo POI 532793_12 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | 132.7655 | 150 | 150 | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2023-170 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 150 | None | None | 132.7655 | 150 | 150 | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2023-170 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 132.7655 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 ftlo POI 532793_12 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | 132.7655 | 150 | 150 | 150 | N/A | N/A | N/A | N/A | 150 | 150
GEN-2023-171 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Long Term) | 150 | 150 | none | none | 100.7034 | 140.6067 | 150 | 110.8996 | 150 | 150 | N/A | 150 | 150 | 150
GEN-2023-171 | 03 CENTRAL | Battery/Storage | April 1 - May 31 (Near Term) | 150 | 150 | none | none | 100.7034 | 140.6067 | 150 | 110.8996 | 150 | 150 | N/A | 150 | 150 | 150
GEN-2023-171 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Long Term) | 150 | 150 | none | none | 100.7034 | 140.6067 | 150 | 110.8996 | 150 | 150 | N/A | 150 | 150 | 150
GEN-2023-171 | 03 CENTRAL | Battery/Storage | Dec 1 - March 31 (Near Term) | 150 | 150 | none | none | 100.7034 | 140.6067 | 150 | 110.8996 | 150 | 150 | N/A | 150 | 150 | 150
GEN-2023-171 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Long Term) | 150 | 150 | none | none | 100.7034 | 140.6067 | 150 | 110.8996 | 150 | 150 | N/A | 150 | 150 | 150
GEN-2023-171 | 03 CENTRAL | Battery/Storage | June 1 - Sept 30 (Near Term) | 150 | 150 | none | none | 100.7034 | 140.6067 | 150 | 110.8996 | 150 | 150 | N/A | 150 | 150 | 150
GEN-2023-171 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 150 | none | none | 100.7034 | 140.6067 | 150 | 110.8996 | 150 | 150 | N/A | 150 | 150 | 150
GEN-2023-171 | 03 CENTRAL | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 150 | none | none | 100.7034 | 140.6067 | 150 | 110.8996 | 150 | 150 | N/A | 150 | 150 | 150
GEN-2023-172 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 200 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 45.2433 | 66.26 | 200 | 18.955 | 0 | 0
GEN-2023-172 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 200 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 45.2433 | 66.26 | 200 | 18.955 | 0 | 0
GEN-2023-172 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 45.2433 | 66.26 | 200 | 18.955 | 0 | 0
GEN-2023-172 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 45.2433 | 66.26 | 200 | 18.955 | 0 | 0
GEN-2023-172 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 45.2433 | 66.26 | 200 | 18.955 | 0 | 0
GEN-2023-172 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 45.2433 | 66.26 | 200 | 18.955 | 0 | 0
GEN-2023-172 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 45.2433 | 66.26 | 200 | 18.955 | 0 | 0
GEN-2023-172 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 45.2433 | 66.26 | 200 | 18.955 | 0 | 0
GEN-2023-173 | 03 CENTRAL | Wind | April 1 - May 31 (Long Term) | 100 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 22.6217 | 33.13 | 100 | 9.4775 | 0 | 0
GEN-2023-173 | 03 CENTRAL | Wind | April 1 - May 31 (Near Term) | 100 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 22.6217 | 33.13 | 100 | 9.4775 | 0 | 0
GEN-2023-173 | 03 CENTRAL | Wind | Dec 1 - March 31 (Long Term) | 100 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 22.6217 | 33.13 | 100 | 9.4775 | 0 | 0
GEN-2023-173 | 03 CENTRAL | Wind | Dec 1 - March 31 (Near Term) | 100 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 22.6217 | 33.13 | 100 | 9.4775 | 0 | 0
GEN-2023-173 | 03 CENTRAL | Wind | June 1 - Sept 30 (Long Term) | 100 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 22.6217 | 33.13 | 100 | 9.4775 | 0 | 0
GEN-2023-173 | 03 CENTRAL | Wind | June 1 - Sept 30 (Near Term) | 100 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 22.6217 | 33.13 | 100 | 9.4775 | 0 | 0
GEN-2023-173 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Long Term) | 100 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 22.6217 | 33.13 | 100 | 9.4775 | 0 | 0
GEN-2023-173 | 03 CENTRAL | Wind | Oct 1 - Nov 30 (Near Term) | 100 | 0 | Stability/Non-Converged | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | 0 | 0 | 0 | 0 | 22.6217 | 33.13 | 100 | 9.4775 | 0 | 0
GEN-2023-194 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 225 | 3.7358 | 533758 CRAWFOR2 69.0 533772 SE1GREE2 69.0 1 ftlo 547469 RIV4525 161 764310 G20-079-TAP 161 1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 105.4292 | 225 | 0 | 0 | 3.7358 | N/A | 9.7723 | 225 | 225
GEN-2023-194 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 225 | 0 | 547467 ORO110 5 161 547469 RIV4525 161 1 ftlo: 547469 RIV4525 161 547498 STL439 5 161 1 | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | 0 | 105.4292 | 225 | 0 | 0 | 3.7358 | N/A | 9.7723 | 225 | 225
GEN-2023-194 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 225 | 9.7723 | 533758 CRAWFOR2 69.0 533772 SE1GREE2 69.0 1 ftlo 547469 RIV4525 161 764310 G20-079-TAP 161 1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 105.4292 | 225 | 0 | 0 | 3.7358 | N/A | 9.7723 | 225 | 225
GEN-2023-194 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 225 | 9.7723 | 533758 CRAWFOR2 69.0 533772 SE1GREE2 69.0 1 ftlo 547469 RIV4525 161 764310 G20-079-TAP 161 1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 105.4292 | 225 | 0 | 0 | 3.7358 | N/A | 9.7723 | 225 | 225
GEN-2023-194 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 225 | 105.4292 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 ftlo: 532937 NEOSHO 5 161 547469 RIV4525 161 2 | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line | 0 | 105.4292 | 225 | 0 | 0 | 3.7358 | N/A | 9.7723 | 225 | 225
GEN-2023-194 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 225 | 0 | 547467 ORO110 5 161 547469 RIV4525 161 1 ftlo: 547469 RIV4525 161 547498 STL439 5 161 1 | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | 0 | 105.4292 | 225 | 0 | 0 | 3.7358 | N/A | 9.7723 | 225 | 225
GEN-2023-194 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 225 | 3.7358 | 533758 CRAWFOR2 69.0 533772 SE1GREE2 69.0 1 ftlo 547469 RIV4525 161 764310 G20-079-TAP 161 1 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | 0 | 105.4292 | 225 | 0 | 0 | 3.7358 | N/A | 9.7723 | 225 | 225
GEN-2023-194 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 225 | 0 | 547467 ORO110 5 161 547469 RIV4525 161 1 ftlo: 547469 RIV4525 161 547498 STL439 5 161 1 | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | 0 | 105.4292 | 225 | 0 | 0 | 3.7358 | N/A | 9.7723 | 225 | 225
GEN-2023-219 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 125 | 0 | Stability/Non-Converged | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | 0 | 0 | 125 | 70.0781 | 0 | 0 | N/A | 125 | 0 | 0
GEN-2023-219 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 125 | 0 | Stability/Non-Converged | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | 0 | 0 | 125 | 70.0781 | 0 | 0 | N/A | 125 | 0 | 0
GEN-2023-219 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 125 | 0 | Stability/Non-Converged | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | 0 | 0 | 125 | 70.0781 | 0 | 0 | N/A | 125 | 0 | 0
GEN-2023-219 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 125 | 0 | Stability/Non-Converged | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | 0 | 0 | 125 | 70.0781 | 0 | 0 | N/A | 125 | 0 | 0
GEN-2023-219 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 125 | 0 | Stability/Non-Converged | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | 0 | 0 | 125 | 70.0781 | 0 | 0 | N/A | 125 | 0 | 0
GEN-2023-219 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 125 | 0 | Stability/Non-Converged | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | 0 | 0 | 125 | 70.0781 | 0 | 0 | N/A | 125 | 0 | 0
GEN-2023-219 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 125 | 0 | Stability/Non-Converged | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | 0 | 0 | 125 | 70.0781 | 0 | 0 | N/A | 125 | 0 | 0
GEN-2023-219 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 125 | 0 | Stability/Non-Converged | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | 0 | 0 | 125 | 70.0781 | 0 | 0 | N/A | 125 | 0 | 0
GEN-2023-220 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-220 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-220 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-220 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-220 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-220 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-220 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-220 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-221 | 03 CENTRAL | Solar | April 1 - May 31 (Long Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-221 | 03 CENTRAL | Solar | April 1 - May 31 (Near Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-221 | 03 CENTRAL | Solar | Dec 1 - March 31 (Long Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-221 | 03 CENTRAL | Solar | Dec 1 - March 31 (Near Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-221 | 03 CENTRAL | Solar | June 1 - Sept 30 (Long Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-221 | 03 CENTRAL | Solar | June 1 - Sept 30 (Near Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-221 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Long Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-221 | 03 CENTRAL | Solar | Oct 1 - Nov 30 (Near Term) | 250 | 250 | none | none | 0 | 0 | 250 | 140.1561 | 250 | 250 | N/A | 250 | 250 | 250
GEN-2023-231 | 03 CENTRAL | Hybrid; Wind/Storage | April 1 - May 31 (Long Term) | 310 | 310 | None | None | 0 | 0 | 310 | 29.9496 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2023-231 | 03 CENTRAL | Hybrid; Wind/Storage | April 1 - May 31 (Near Term) | 310 | 310 | None | None | 0 | 0 | 310 | 29.9496 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2023-231 | 03 CENTRAL | Hybrid; Wind/Storage | Dec 1 - March 31 (Long Term) | 310 | 29.9496 | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 ftlo: 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Reconfigure the Neosho Transformers | 0 | 0 | 310 | 29.9496 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2023-231 | 03 CENTRAL | Hybrid; Wind/Storage | Dec 1 - March 31 (Near Term) | 310 | 29.9496 | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 ftlo: 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Reconfigure the Neosho Transformers | 0 | 0 | 310 | 29.9496 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2023-231 | 03 CENTRAL | Hybrid; Wind/Storage | June 1 - Sept 30 (Long Term) | 310 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 0 | 310 | 29.9496 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2023-231 | 03 CENTRAL | Hybrid; Wind/Storage | June 1 - Sept 30 (Near Term) | 310 | 0 | 541198 PECULR 7 345 541200 PHILL 7 345 1 ftlo: P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | 0 | 0 | 310 | 29.9496 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2023-231 | 03 CENTRAL | Hybrid; Wind/Storage | Oct 1 - Nov 30 (Long Term) | 310 | 310 | None | None | 0 | 0 | 310 | 29.9496 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2023-231 | 03 CENTRAL | Hybrid; Wind/Storage | Oct 1 - Nov 30 (Near Term) | 310 | 310 | None | None | 0 | 0 | 310 | 29.9496 | N/A | N/A | N/A | N/A | 310 | 310
GEN-2023-009 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 133.9971 | 164.8791 | N/A | 138.6536 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-009 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 133.9971 | 164.8791 | N/A | 138.6536 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-009 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 133.9971 | 164.8791 | N/A | 138.6536 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-009 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 133.9971 | 164.8791 | N/A | 138.6536 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-009 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 133.9971 | 164.8791 | N/A | 138.6536 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-009 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 133.9971 | 164.8791 | N/A | 138.6536 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-009 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 133.9971 | 164.8791 | N/A | 138.6536 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-009 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 133.9971 | 164.8791 | N/A | 138.6536 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-022 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 250 | 0 | 250 | 175.1181 | 0 | 0 | 250 | 0 | 0 | 0
GEN-2023-022 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 250 | 0 | 250 | 175.1181 | 0 | 0 | 250 | 0 | 0 | 0
GEN-2023-022 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 250 | 0 | 250 | 175.1181 | 0 | 0 | 250 | 0 | 0 | 0
GEN-2023-022 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 250 | 0 | 250 | 175.1181 | 0 | 0 | 250 | 0 | 0 | 0
GEN-2023-022 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 250 | 0 | 250 | 175.1181 | 0 | 0 | 250 | 0 | 0 | 0
GEN-2023-022 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 250 | 0 | 250 | 175.1181 | 0 | 0 | 250 | 0 | 0 | 0
GEN-2023-022 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 250 | 0 | 250 | 175.1181 | 0 | 0 | 250 | 0 | 0 | 0
GEN-2023-022 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 250 | 0 | 250 | 175.1181 | 0 | 0 | 250 | 0 | 0 | 0
GEN-2023-027 | 04 SOUTHEAST | Hybrid; Solar/Battery | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 4.3798 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-027 | 04 SOUTHEAST | Hybrid; Solar/Battery | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 4.3798 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-027 | 04 SOUTHEAST | Hybrid; Solar/Battery | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 4.3798 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-027 | 04 SOUTHEAST | Hybrid; Solar/Battery | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 4.3798 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-027 | 04 SOUTHEAST | Hybrid; Solar/Battery | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 4.3798 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-027 | 04 SOUTHEAST | Hybrid; Solar/Battery | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 4.3798 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-027 | 04 SOUTHEAST | Hybrid; Solar/Battery | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 4.3798 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-027 | 04 SOUTHEAST | Hybrid; Solar/Battery | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 4.3798 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-028 | 04 SOUTHEAST | Hybrid; Solar/Battery | April 1 - May 31 (Long Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 165.0345 | 182.6908 | N/A | 187.527 | 0 | 0
GEN-2023-028 | 04 SOUTHEAST | Hybrid; Solar/Battery | April 1 - May 31 (Near Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 165.0345 | 182.6908 | N/A | 187.527 | 0 | 0
GEN-2023-028 | 04 SOUTHEAST | Hybrid; Solar/Battery | Dec 1 - March 31 (Long Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 165.0345 | 182.6908 | N/A | 187.527 | 0 | 0
GEN-2023-028 | 04 SOUTHEAST | Hybrid; Solar/Battery | Dec 1 - March 31 (Near Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 165.0345 | 182.6908 | N/A | 187.527 | 0 | 0
GEN-2023-028 | 04 SOUTHEAST | Hybrid; Solar/Battery | June 1 - Sept 30 (Long Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 165.0345 | 182.6908 | N/A | 187.527 | 0 | 0
GEN-2023-028 | 04 SOUTHEAST | Hybrid; Solar/Battery | June 1 - Sept 30 (Near Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 165.0345 | 182.6908 | N/A | 187.527 | 0 | 0
GEN-2023-028 | 04 SOUTHEAST | Hybrid; Solar/Battery | Oct 1 - Nov 30 (Long Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 165.0345 | 182.6908 | N/A | 187.527 | 0 | 0
GEN-2023-028 | 04 SOUTHEAST | Hybrid; Solar/Battery | Oct 1 - Nov 30 (Near Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 165.0345 | 182.6908 | N/A | 187.527 | 0 | 0
GEN-2023-030 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 25 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 25 | 25 | N/A | 25 | 25 | 25 | N/A | 25 | 0 | 0
GEN-2023-030 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 25 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 25 | 25 | N/A | 25 | 25 | 25 | N/A | 25 | 0 | 0
GEN-2023-030 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 25 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 25 | 25 | N/A | 25 | 25 | 25 | N/A | 25 | 0 | 0
GEN-2023-030 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 25 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 25 | 25 | N/A | 25 | 25 | 25 | N/A | 25 | 0 | 0
GEN-2023-030 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 25 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 25 | 25 | N/A | 25 | 25 | 25 | N/A | 25 | 0 | 0
GEN-2023-030 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 25 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 25 | 25 | N/A | 25 | 25 | 25 | N/A | 25 | 0 | 0
GEN-2023-030 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 25 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 25 | 25 | N/A | 25 | 25 | 25 | N/A | 25 | 0 | 0
GEN-2023-030 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 25 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 25 | 25 | N/A | 25 | 25 | 25 | N/A | 25 | 0 | 0
GEN-2023-035 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 68.8504 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-035 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 68.8504 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-035 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 68.8504 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-035 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 68.8504 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-035 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 68.8504 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-035 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 68.8504 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-035 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 68.8504 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-035 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 68.8504 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-038 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 110.9229 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-038 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 110.9229 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-038 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 110.9229 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-038 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 110.9229 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-038 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 110.9229 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-038 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 110.9229 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-038 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 110.9229 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-038 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 110.9229 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-049 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 107.6312 | 119.1462 | N/A | 122.3002 | 0 | 0
GEN-2023-049 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 107.6312 | 119.1462 | N/A | 122.3002 | 0 | 0
GEN-2023-049 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 107.6312 | 119.1462 | N/A | 122.3002 | 0 | 0
GEN-2023-049 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 107.6312 | 119.1462 | N/A | 122.3002 | 0 | 0
GEN-2023-049 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 107.6312 | 119.1462 | N/A | 122.3002 | 0 | 0
GEN-2023-049 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 107.6312 | 119.1462 | N/A | 122.3002 | 0 | 0
GEN-2023-049 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 107.6312 | 119.1462 | N/A | 122.3002 | 0 | 0
GEN-2023-049 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 107.6312 | 119.1462 | N/A | 122.3002 | 0 | 0
GEN-2023-055 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 71.7541 | 100 | N/A | 100 | 0 | 0
GEN-2023-055 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 71.7541 | 100 | N/A | 100 | 0 | 0
GEN-2023-055 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 71.7541 | 100 | N/A | 100 | 0 | 0
GEN-2023-055 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 71.7541 | 100 | N/A | 100 | 0 | 0
GEN-2023-055 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 71.7541 | 100 | N/A | 100 | 0 | 0
GEN-2023-055 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 71.7541 | 100 | N/A | 100 | 0 | 0
GEN-2023-055 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 71.7541 | 100 | N/A | 100 | 0 | 0
GEN-2023-055 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 71.7541 | 100 | N/A | 100 | 0 | 0
GEN-2023-056 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 59.4789 | N/A | 134.7149 | 133.8277 | 129.8239 | N/A | 87.4093 | 0 | 0
GEN-2023-056 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 59.4789 | N/A | 134.7149 | 133.8277 | 129.8239 | N/A | 87.4093 | 0 | 0
GEN-2023-056 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 59.4789 | N/A | 134.7149 | 133.8277 | 129.8239 | N/A | 87.4093 | 0 | 0
GEN-2023-056 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 59.4789 | N/A | 134.7149 | 133.8277 | 129.8239 | N/A | 87.4093 | 0 | 0
GEN-2023-056 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 59.4789 | N/A | 134.7149 | 133.8277 | 129.8239 | N/A | 87.4093 | 0 | 0
GEN-2023-056 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 59.4789 | N/A | 134.7149 | 133.8277 | 129.8239 | N/A | 87.4093 | 0 | 0
GEN-2023-056 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 59.4789 | N/A | 134.7149 | 133.8277 | 129.8239 | N/A | 87.4093 | 0 | 0
GEN-2023-056 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 59.4789 | N/A | 134.7149 | 133.8277 | 129.8239 | N/A | 87.4093 | 0 | 0
GEN-2023-057 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | 104.8623 | 64.7517 | N/A | 38.4385 | 0 | 0
GEN-2023-057 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | 104.8623 | 64.7517 | N/A | 38.4385 | 0 | 0
GEN-2023-057 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | 104.8623 | 64.7517 | N/A | 38.4385 | 0 | 0
GEN-2023-057 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | 104.8623 | 64.7517 | N/A | 38.4385 | 0 | 0
GEN-2023-057 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | 104.8623 | 64.7517 | N/A | 38.4385 | 0 | 0
GEN-2023-057 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | 104.8623 | 64.7517 | N/A | 38.4385 | 0 | 0
GEN-2023-057 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | 104.8623 | 64.7517 | N/A | 38.4385 | 0 | 0
GEN-2023-057 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | 104.8623 | 64.7517 | N/A | 38.4385 | 0 | 0
GEN-2023-059 | 04 SOUTHEAST | Hybrid; Solar/RECIP Gas | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 200 | 198.7896 | N/A | 166.3634 | 200 | 200 | N/A | 200 | 0 | 0
GEN-2023-059 | 04 SOUTHEAST | Hybrid; Solar/RECIP Gas | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 200 | 198.7896 | N/A | 166.3634 | 200 | 200 | N/A | 200 | 0 | 0
GEN-2023-059 | 04 SOUTHEAST | Hybrid; Solar/RECIP Gas | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 200 | 198.7896 | N/A | 166.3634 | 200 | 200 | N/A | 200 | 0 | 0
GEN-2023-059 | 04 SOUTHEAST | Hybrid; Solar/RECIP Gas | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 200 | 198.7896 | N/A | 166.3634 | 200 | 200 | N/A | 200 | 0 | 0
GEN-2023-059 | 04 SOUTHEAST | Hybrid; Solar/RECIP Gas | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 200 | 198.7896 | N/A | 166.3634 | 200 | 200 | N/A | 200 | 0 | 0
GEN-2023-059 | 04 SOUTHEAST | Hybrid; Solar/RECIP Gas | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 200 | 198.7896 | N/A | 166.3634 | 200 | 200 | N/A | 200 | 0 | 0
GEN-2023-059 | 04 SOUTHEAST | Hybrid; Solar/RECIP Gas | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 200 | 198.7896 | N/A | 166.3634 | 200 | 200 | N/A | 200 | 0 | 0
GEN-2023-059 | 04 SOUTHEAST | Hybrid; Solar/RECIP Gas | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 200 | 198.7896 | N/A | 166.3634 | 200 | 200 | N/A | 200 | 0 | 0
GEN-2023-063 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 135 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.917 | 0 | N/A | 107.6454 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-063 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 135 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.917 | 0 | N/A | 107.6454 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-063 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 135 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.917 | 0 | N/A | 107.6454 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-063 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 135 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.917 | 0 | N/A | 107.6454 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-063 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 135 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.917 | 0 | N/A | 107.6454 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-063 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 135 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.917 | 0 | N/A | 107.6454 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-063 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 135 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.917 | 0 | N/A | 107.6454 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-063 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 135 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.917 | 0 | N/A | 107.6454 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-064 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 198.1791 | 196.8669 | N/A | 179.6198 | 178.437 | 173.0985 | N/A | 116.5458 | 0 | 0
GEN-2023-064 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 198.1791 | 196.8669 | N/A | 179.6198 | 178.437 | 173.0985 | N/A | 116.5458 | 0 | 0
GEN-2023-064 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 198.1791 | 196.8669 | N/A | 179.6198 | 178.437 | 173.0985 | N/A | 116.5458 | 0 | 0
GEN-2023-064 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 198.1791 | 196.8669 | N/A | 179.6198 | 178.437 | 173.0985 | N/A | 116.5458 | 0 | 0
GEN-2023-064 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 198.1791 | 196.8669 | N/A | 179.6198 | 178.437 | 173.0985 | N/A | 116.5458 | 0 | 0
GEN-2023-064 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 198.1791 | 196.8669 | N/A | 179.6198 | 178.437 | 173.0985 | N/A | 116.5458 | 0 | 0
GEN-2023-064 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 198.1791 | 196.8669 | N/A | 179.6198 | 178.437 | 173.0985 | N/A | 116.5458 | 0 | 0
GEN-2023-064 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 198.1791 | 196.8669 | N/A | 179.6198 | 178.437 | 173.0985 | N/A | 116.5458 | 0 | 0
GEN-2023-069 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 17.4504 | 0 | N/A | 55.4614 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-069 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 17.4504 | 0 | N/A | 55.4614 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-069 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 17.4504 | 0 | N/A | 55.4614 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-069 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 17.4504 | 0 | N/A | 55.4614 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-069 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 17.4504 | 0 | N/A | 55.4614 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-069 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 17.4504 | 0 | N/A | 55.4614 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-069 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 17.4504 | 0 | N/A | 55.4614 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-069 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 17.4504 | 0 | N/A | 55.4614 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-075 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 2.84 | 140.5666 | 200 | 200 | 17.6409 | 86.3356 | 200 | 51.2514 | 0 | 0
GEN-2023-075 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 2.84 | 140.5666 | 200 | 200 | 17.6409 | 86.3356 | 200 | 51.2514 | 0 | 0
GEN-2023-075 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 2.84 | 140.5666 | 200 | 200 | 17.6409 | 86.3356 | 200 | 51.2514 | 0 | 0
GEN-2023-075 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 2.84 | 140.5666 | 200 | 200 | 17.6409 | 86.3356 | 200 | 51.2514 | 0 | 0
GEN-2023-075 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 2.84 | 140.5666 | 200 | 200 | 17.6409 | 86.3356 | 200 | 51.2514 | 0 | 0
GEN-2023-075 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 2.84 | 140.5666 | 200 | 200 | 17.6409 | 86.3356 | 200 | 51.2514 | 0 | 0
GEN-2023-075 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 2.84 | 140.5666 | 200 | 200 | 17.6409 | 86.3356 | 200 | 51.2514 | 0 | 0
GEN-2023-075 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 2.84 | 140.5666 | 200 | 200 | 17.6409 | 86.3356 | 200 | 51.2514 | 0 | 0
GEN-2023-076 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.42 | 70.2833 | 100 | 100 | 8.8204 | 43.1678 | 100 | 25.6257 | 0 | 0
GEN-2023-076 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.42 | 70.2833 | 100 | 100 | 8.8204 | 43.1678 | 100 | 25.6257 | 0 | 0
GEN-2023-076 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.42 | 70.2833 | 100 | 100 | 8.8204 | 43.1678 | 100 | 25.6257 | 0 | 0
GEN-2023-076 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.42 | 70.2833 | 100 | 100 | 8.8204 | 43.1678 | 100 | 25.6257 | 0 | 0
GEN-2023-076 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.42 | 70.2833 | 100 | 100 | 8.8204 | 43.1678 | 100 | 25.6257 | 0 | 0
GEN-2023-076 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.42 | 70.2833 | 100 | 100 | 8.8204 | 43.1678 | 100 | 25.6257 | 0 | 0
GEN-2023-076 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.42 | 70.2833 | 100 | 100 | 8.8204 | 43.1678 | 100 | 25.6257 | 0 | 0
GEN-2023-076 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 1.42 | 70.2833 | 100 | 100 | 8.8204 | 43.1678 | 100 | 25.6257 | 0 | 0
GEN-2023-088 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 117 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 85.3127 | 105.0776 | 0 | 0 | 117 | 0 | 0 | 0
GEN-2023-088 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 117 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 85.3127 | 105.0776 | 0 | 0 | 117 | 0 | 0 | 0
GEN-2023-088 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 117 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 85.3127 | 105.0776 | 0 | 0 | 117 | 0 | 0 | 0
GEN-2023-088 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 117 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 85.3127 | 105.0776 | 0 | 0 | 117 | 0 | 0 | 0
GEN-2023-088 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 117 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 85.3127 | 105.0776 | 0 | 0 | 117 | 0 | 0 | 0
GEN-2023-088 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 117 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 85.3127 | 105.0776 | 0 | 0 | 117 | 0 | 0 | 0
GEN-2023-088 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 117 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 85.3127 | 105.0776 | 0 | 0 | 117 | 0 | 0 | 0
GEN-2023-088 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 117 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 85.3127 | 105.0776 | 0 | 0 | 117 | 0 | 0 | 0
GEN-2023-092 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 125 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 66.9986 | 82.4396 | N/A | 69.3268 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-092 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 125 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 66.9986 | 82.4396 | N/A | 69.3268 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-092 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 125 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 66.9986 | 82.4396 | N/A | 69.3268 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-092 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 125 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 66.9986 | 82.4396 | N/A | 69.3268 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-092 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 125 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 66.9986 | 82.4396 | N/A | 69.3268 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-092 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 125 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 66.9986 | 82.4396 | N/A | 69.3268 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-092 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 125 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 66.9986 | 82.4396 | N/A | 69.3268 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-092 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 125 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 66.9986 | 82.4396 | N/A | 69.3268 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-100 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 300 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-100 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 300 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-100 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 300 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-100 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 300 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-100 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 300 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-100 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 300 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-100 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-100 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-101 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-101 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-101 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-101 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-101 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-101 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-101 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-101 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-102 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 475 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-102 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 475 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-102 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 475 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-102 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 475 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-102 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 475 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-102 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 475 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-102 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 475 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-102 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 475 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-104 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 100 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-104 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 100 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-104 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 100 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-104 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 100 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-104 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 100 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-104 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 100 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-104 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 100 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-104 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 100 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-132 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 140.6213 | 138.2432 | N/A | 150 | 134.461 | 129.6435 | N/A | 150 | 0 | 0
GEN-2023-132 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 140.6213 | 138.2432 | N/A | 150 | 134.461 | 129.6435 | N/A | 150 | 0 | 0
GEN-2023-132 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 140.6213 | 138.2432 | N/A | 150 | 134.461 | 129.6435 | N/A | 150 | 0 | 0
GEN-2023-132 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 140.6213 | 138.2432 | N/A | 150 | 134.461 | 129.6435 | N/A | 150 | 0 | 0
GEN-2023-132 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 140.6213 | 138.2432 | N/A | 150 | 134.461 | 129.6435 | N/A | 150 | 0 | 0
GEN-2023-132 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 140.6213 | 138.2432 | N/A | 150 | 134.461 | 129.6435 | N/A | 150 | 0 | 0
GEN-2023-132 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 140.6213 | 138.2432 | N/A | 150 | 134.461 | 129.6435 | N/A | 150 | 0 | 0
GEN-2023-132 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 140.6213 | 138.2432 | N/A | 150 | 134.461 | 129.6435 | N/A | 150 | 0 | 0
GEN-2023-134 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 252 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 183.7504 | 247.4156 | 138.8802 | 0 | 252 | 146.8477 | 0 | 0
GEN-2023-134 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 252 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 183.7504 | 247.4156 | 138.8802 | 0 | 252 | 146.8477 | 0 | 0
GEN-2023-134 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 252 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 183.7504 | 247.4156 | 138.8802 | 0 | 252 | 146.8477 | 0 | 0
GEN-2023-134 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 252 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 183.7504 | 247.4156 | 138.8802 | 0 | 252 | 146.8477 | 0 | 0
GEN-2023-134 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 252 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 183.7504 | 247.4156 | 138.8802 | 0 | 252 | 146.8477 | 0 | 0
GEN-2023-134 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 252 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 183.7504 | 247.4156 | 138.8802 | 0 | 252 | 146.8477 | 0 | 0
GEN-2023-134 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 252 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 183.7504 | 247.4156 | 138.8802 | 0 | 252 | 146.8477 | 0 | 0
GEN-2023-134 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 252 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 183.7504 | 247.4156 | 138.8802 | 0 | 252 | 146.8477 | 0 | 0
GEN-2023-135 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 52 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 27.8714 | 34.2949 | N/A | 28.8399 | 0 | 37.6275 | N/A | 30.3019 | 0 | 0
GEN-2023-135 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 52 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 27.8714 | 34.2949 | N/A | 28.8399 | 0 | 37.6275 | N/A | 30.3019 | 0 | 0
GEN-2023-135 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 52 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 27.8714 | 34.2949 | N/A | 28.8399 | 0 | 37.6275 | N/A | 30.3019 | 0 | 0
GEN-2023-135 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 52 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 27.8714 | 34.2949 | N/A | 28.8399 | 0 | 37.6275 | N/A | 30.3019 | 0 | 0
GEN-2023-135 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 52 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 27.8714 | 34.2949 | N/A | 28.8399 | 0 | 37.6275 | N/A | 30.3019 | 0 | 0
GEN-2023-135 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 52 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 27.8714 | 34.2949 | N/A | 28.8399 | 0 | 37.6275 | N/A | 30.3019 | 0 | 0
GEN-2023-135 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 52 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 27.8714 | 34.2949 | N/A | 28.8399 | 0 | 37.6275 | N/A | 30.3019 | 0 | 0
GEN-2023-135 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 52 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 27.8714 | 34.2949 | N/A | 28.8399 | 0 | 37.6275 | N/A | 30.3019 | 0 | 0
GEN-2023-138 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 101.7711 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-138 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 101.7711 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-138 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 101.7711 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-138 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 101.7711 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-138 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 101.7711 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-138 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 101.7711 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-138 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 101.7711 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-138 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 101.7711 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-150 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 59.585 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-150 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 59.585 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-150 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 59.585 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-150 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 59.585 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-150 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 59.585 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-150 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 59.585 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-150 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 59.585 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-150 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 59.585 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-151 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 53.5988 | 65.9516 | N/A | 55.4614 | 89.2185 | 72.3605 | N/A | 58.2729 | 0 | 0
GEN-2023-151 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 53.5988 | 65.9516 | N/A | 55.4614 | 89.2185 | 72.3605 | N/A | 58.2729 | 0 | 0
GEN-2023-151 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 53.5988 | 65.9516 | N/A | 55.4614 | 89.2185 | 72.3605 | N/A | 58.2729 | 0 | 0
GEN-2023-151 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 53.5988 | 65.9516 | N/A | 55.4614 | 89.2185 | 72.3605 | N/A | 58.2729 | 0 | 0
GEN-2023-151 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 53.5988 | 65.9516 | N/A | 55.4614 | 89.2185 | 72.3605 | N/A | 58.2729 | 0 | 0
GEN-2023-151 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 53.5988 | 65.9516 | N/A | 55.4614 | 89.2185 | 72.3605 | N/A | 58.2729 | 0 | 0
GEN-2023-151 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 53.5988 | 65.9516 | N/A | 55.4614 | 89.2185 | 72.3605 | N/A | 58.2729 | 0 | 0
GEN-2023-151 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 53.5988 | 65.9516 | N/A | 55.4614 | 89.2185 | 72.3605 | N/A | 58.2729 | 0 | 0
GEN-2023-161 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 74.9 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 74.9 | 0 | 0 | N/A | 74.9 | 0 | 0
GEN-2023-161 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 74.9 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 74.9 | 0 | 0 | N/A | 74.9 | 0 | 0
GEN-2023-161 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 74.9 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 74.9 | 0 | 0 | N/A | 74.9 | 0 | 0
GEN-2023-161 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 74.9 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 74.9 | 0 | 0 | N/A | 74.9 | 0 | 0
GEN-2023-161 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 74.9 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 74.9 | 0 | 0 | N/A | 74.9 | 0 | 0
GEN-2023-161 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 74.9 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 74.9 | 0 | 0 | N/A | 74.9 | 0 | 0
GEN-2023-161 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 74.9 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 74.9 | 0 | 0 | N/A | 74.9 | 0 | 0
GEN-2023-161 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 74.9 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 74.9 | 0 | 0 | N/A | 74.9 | 0 | 0
GEN-2023-164 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-164 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-164 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-164 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-164 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-164 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-164 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-164 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-165 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-165 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-165 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-165 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-165 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-165 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-165 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-165 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 210 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 83.4189 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-166 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-166 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-166 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-166 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-166 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-166 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-166 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-166 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 150 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-167 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 250 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-167 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 250 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-167 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 250 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-167 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 250 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-167 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 250 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-167 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 250 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-167 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 250 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-167 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 250 | 250 | 250 | N/A | 250 | 0 | 0
GEN-2023-168 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 173.5015 | 55.5301 | 57.5362 | N/A | 175 | 0 | 0
GEN-2023-168 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 173.5015 | 55.5301 | 57.5362 | N/A | 175 | 0 | 0
GEN-2023-168 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 173.5015 | 55.5301 | 57.5362 | N/A | 175 | 0 | 0
GEN-2023-168 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 173.5015 | 55.5301 | 57.5362 | N/A | 175 | 0 | 0
GEN-2023-168 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 173.5015 | 55.5301 | 57.5362 | N/A | 175 | 0 | 0
GEN-2023-168 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 173.5015 | 55.5301 | 57.5362 | N/A | 175 | 0 | 0
GEN-2023-168 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 173.5015 | 55.5301 | 57.5362 | N/A | 175 | 0 | 0
GEN-2023-168 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 173.5015 | 55.5301 | 57.5362 | N/A | 175 | 0 | 0
GEN-2023-174 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 141.8896 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-174 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 141.8896 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-174 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 141.8896 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-174 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 141.8896 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-174 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 141.8896 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-174 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 141.8896 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-174 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 141.8896 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-174 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 141.8896 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-177 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 140.0945 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-177 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 140.0945 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-177 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 140.0945 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-177 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 140.0945 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-177 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 140.0945 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-177 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 140.0945 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-177 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 140.0945 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-177 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 140.0945 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-180 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 148.6343 | 147.6502 | N/A | 150 | 133.8277 | 146.9299 | N/A | 87.4093 | 0 | 0
GEN-2023-180 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 148.6343 | 147.6502 | N/A | 150 | 133.8277 | 146.9299 | N/A | 87.4093 | 0 | 0
GEN-2023-180 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 148.6343 | 147.6502 | N/A | 150 | 133.8277 | 146.9299 | N/A | 87.4093 | 0 | 0
GEN-2023-180 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 148.6343 | 147.6502 | N/A | 150 | 133.8277 | 146.9299 | N/A | 87.4093 | 0 | 0
GEN-2023-180 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 148.6343 | 147.6502 | N/A | 150 | 133.8277 | 146.9299 | N/A | 87.4093 | 0 | 0
GEN-2023-180 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 148.6343 | 147.6502 | N/A | 150 | 133.8277 | 146.9299 | N/A | 87.4093 | 0 | 0
GEN-2023-180 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 148.6343 | 147.6502 | N/A | 150 | 133.8277 | 146.9299 | N/A | 87.4093 | 0 | 0
GEN-2023-180 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 148.6343 | 147.6502 | N/A | 150 | 133.8277 | 146.9299 | N/A | 87.4093 | 0 | 0
GEN-2023-193 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 175 | 175 | N/A | 175 | 175 | 175 | N/A | 175 | 0 | 0
GEN-2023-193 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 175 | 175 | N/A | 175 | 175 | 175 | N/A | 175 | 0 | 0
GEN-2023-193 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 175 | 175 | N/A | 175 | 175 | 175 | N/A | 175 | 0 | 0
GEN-2023-193 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 175 | 175 | N/A | 175 | 175 | 175 | N/A | 175 | 0 | 0
GEN-2023-193 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 175 | 175 | N/A | 175 | 175 | 175 | N/A | 175 | 0 | 0
GEN-2023-193 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 175 | 175 | N/A | 175 | 175 | 175 | N/A | 175 | 0 | 0
GEN-2023-193 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 175 | 175 | N/A | 175 | 175 | 175 | N/A | 175 | 0 | 0
GEN-2023-193 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 175 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 175 | 175 | N/A | 175 | 175 | 175 | N/A | 175 | 0 | 0
GEN-2023-204 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Long Term) | 953 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 893.5459 | 945.3223 | N/A | 792.7217 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-204 | 04 SOUTHEAST | Thermal | April 1 - May 31 (Near Term) | 953 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 893.5459 | 945.3223 | N/A | 792.7217 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-204 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Long Term) | 953 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 893.5459 | 945.3223 | N/A | 792.7217 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-204 | 04 SOUTHEAST | Thermal | Dec 1 - March 31 (Near Term) | 953 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 893.5459 | 945.3223 | N/A | 792.7217 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-204 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Long Term) | 953 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 893.5459 | 945.3223 | N/A | 792.7217 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-204 | 04 SOUTHEAST | Thermal | June 1 - Sept 30 (Near Term) | 953 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 893.5459 | 945.3223 | N/A | 792.7217 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-204 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Long Term) | 953 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 893.5459 | 945.3223 | N/A | 792.7217 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-204 | 04 SOUTHEAST | Thermal | Oct 1 - Nov 30 (Near Term) | 953 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 893.5459 | 945.3223 | N/A | 792.7217 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-205 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 180 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 180 | 157.8643 | 147.2916 | N/A | 104.8912 | 0 | 0
GEN-2023-205 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 180 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 180 | 157.8643 | 147.2916 | N/A | 104.8912 | 0 | 0
GEN-2023-205 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 180 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 180 | 157.8643 | 147.2916 | N/A | 104.8912 | 0 | 0
GEN-2023-205 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 180 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 180 | 157.8643 | 147.2916 | N/A | 104.8912 | 0 | 0
GEN-2023-205 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 180 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 180 | 157.8643 | 147.2916 | N/A | 104.8912 | 0 | 0
GEN-2023-205 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 180 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 180 | 157.8643 | 147.2916 | N/A | 104.8912 | 0 | 0
GEN-2023-205 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 180 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 180 | 157.8643 | 147.2916 | N/A | 104.8912 | 0 | 0
GEN-2023-205 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 180 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 180 | 157.8643 | 147.2916 | N/A | 104.8912 | 0 | 0
GEN-2023-206 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 50 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 50 | 50 | N/A | 50 | 50 | 50 | N/A | 50 | 0 | 0
GEN-2023-206 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 50 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 50 | 50 | N/A | 50 | 50 | 50 | N/A | 50 | 0 | 0
GEN-2023-206 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 50 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 50 | 50 | N/A | 50 | 50 | 50 | N/A | 50 | 0 | 0
GEN-2023-206 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 50 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 50 | 50 | N/A | 50 | 50 | 50 | N/A | 50 | 0 | 0
GEN-2023-206 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 50 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 50 | 50 | N/A | 50 | 50 | 50 | N/A | 50 | 0 | 0
GEN-2023-206 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 50 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 50 | 50 | N/A | 50 | 50 | 50 | N/A | 50 | 0 | 0
GEN-2023-206 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 50 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 50 | 50 | N/A | 50 | 50 | 50 | N/A | 50 | 0 | 0
GEN-2023-206 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 50 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 50 | 50 | N/A | 50 | 50 | 50 | N/A | 50 | 0 | 0
GEN-2023-210 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 191 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 191 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-210 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 191 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 191 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-210 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 191 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 191 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-210 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 191 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 191 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-210 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 191 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 191 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-210 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 191 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 191 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-210 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 191 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 191 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-210 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 191 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | N/A | 191 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-211 | 04 SOUTHEAST | Hybrid; Solar/Battery/Wind | April 1 - May 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 120.2405 | 215.3885 | 202.178 | 250 | 169.379 | 0 | 0
GEN-2023-211 | 04 SOUTHEAST | Hybrid; Solar/Battery/Wind | April 1 - May 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 120.2405 | 215.3885 | 202.178 | 250 | 169.379 | 0 | 0
GEN-2023-211 | 04 SOUTHEAST | Hybrid; Solar/Battery/Wind | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 120.2405 | 215.3885 | 202.178 | 250 | 169.379 | 0 | 0
GEN-2023-211 | 04 SOUTHEAST | Hybrid; Solar/Battery/Wind | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 120.2405 | 215.3885 | 202.178 | 250 | 169.379 | 0 | 0
GEN-2023-211 | 04 SOUTHEAST | Hybrid; Solar/Battery/Wind | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 120.2405 | 215.3885 | 202.178 | 250 | 169.379 | 0 | 0
GEN-2023-211 | 04 SOUTHEAST | Hybrid; Solar/Battery/Wind | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 120.2405 | 215.3885 | 202.178 | 250 | 169.379 | 0 | 0
GEN-2023-211 | 04 SOUTHEAST | Hybrid; Solar/Battery/Wind | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 120.2405 | 215.3885 | 202.178 | 250 | 169.379 | 0 | 0
GEN-2023-211 | 04 SOUTHEAST | Hybrid; Solar/Battery/Wind | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 250 | 120.2405 | 215.3885 | 202.178 | 250 | 169.379 | 0 | 0
GEN-2023-212 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 400 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 138.0865 | 89.9653 | N/A | 135.2907 | 0 | 282.3528 | N/A | 233.0916 | 0 | 0
GEN-2023-212 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 400 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 138.0865 | 89.9653 | N/A | 135.2907 | 0 | 282.3528 | N/A | 233.0916 | 0 | 0
GEN-2023-212 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 400 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 138.0865 | 89.9653 | N/A | 135.2907 | 0 | 282.3528 | N/A | 233.0916 | 0 | 0
GEN-2023-212 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 400 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 138.0865 | 89.9653 | N/A | 135.2907 | 0 | 282.3528 | N/A | 233.0916 | 0 | 0
GEN-2023-212 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 400 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 138.0865 | 89.9653 | N/A | 135.2907 | 0 | 282.3528 | N/A | 233.0916 | 0 | 0
GEN-2023-212 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 400 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 138.0865 | 89.9653 | N/A | 135.2907 | 0 | 282.3528 | N/A | 233.0916 | 0 | 0
GEN-2023-212 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 400 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 138.0865 | 89.9653 | N/A | 135.2907 | 0 | 282.3528 | N/A | 233.0916 | 0 | 0
GEN-2023-212 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 400 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 138.0865 | 89.9653 | N/A | 135.2907 | 0 | 282.3528 | N/A | 233.0916 | 0 | 0
GEN-2023-213 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 74.78 | 92.9693 | N/A | 40.7085 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-213 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 74.78 | 92.9693 | N/A | 40.7085 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-213 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 74.78 | 92.9693 | N/A | 40.7085 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-213 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 74.78 | 92.9693 | N/A | 40.7085 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-213 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 74.78 | 92.9693 | N/A | 40.7085 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-213 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 74.78 | 92.9693 | N/A | 40.7085 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-213 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 74.78 | 92.9693 | N/A | 40.7085 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-213 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 100 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 74.78 | 92.9693 | N/A | 40.7085 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-227 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 107.1977 | 131.9033 | N/A | 110.9229 | 0 | 143.0477 | N/A | 200 | 0 | 0
GEN-2023-227 | 04 SOUTHEAST | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 107.1977 | 131.9033 | N/A | 110.9229 | 0 | 143.0477 | N/A | 200 | 0 | 0
GEN-2023-227 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 107.1977 | 131.9033 | N/A | 110.9229 | 0 | 143.0477 | N/A | 200 | 0 | 0
GEN-2023-227 | 04 SOUTHEAST | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 107.1977 | 131.9033 | N/A | 110.9229 | 0 | 143.0477 | N/A | 200 | 0 | 0
GEN-2023-227 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 107.1977 | 131.9033 | N/A | 110.9229 | 0 | 143.0477 | N/A | 200 | 0 | 0
GEN-2023-227 | 04 SOUTHEAST | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 107.1977 | 131.9033 | N/A | 110.9229 | 0 | 143.0477 | N/A | 200 | 0 | 0
GEN-2023-227 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 107.1977 | 131.9033 | N/A | 110.9229 | 0 | 143.0477 | N/A | 200 | 0 | 0
GEN-2023-227 | 04 SOUTHEAST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 107.1977 | 131.9033 | N/A | 110.9229 | 0 | 143.0477 | N/A | 200 | 0 | 0
GEN-2023-229 | 04 SOUTHEAST | Wind | April 1 - May 31 (Long Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 0 | 91.3636 | 0 | 0 | 230 | 0 | 0 | 0
GEN-2023-229 | 04 SOUTHEAST | Wind | April 1 - May 31 (Near Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 0 | 91.3636 | 0 | 0 | 230 | 0 | 0 | 0
GEN-2023-229 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Long Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 0 | 91.3636 | 0 | 0 | 230 | 0 | 0 | 0
GEN-2023-229 | 04 SOUTHEAST | Wind | Dec 1 - March 31 (Near Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 0 | 91.3636 | 0 | 0 | 230 | 0 | 0 | 0
GEN-2023-229 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Long Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 0 | 91.3636 | 0 | 0 | 230 | 0 | 0 | 0
GEN-2023-229 | 04 SOUTHEAST | Wind | June 1 - Sept 30 (Near Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 0 | 91.3636 | 0 | 0 | 230 | 0 | 0 | 0
GEN-2023-229 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Long Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 0 | 91.3636 | 0 | 0 | 230 | 0 | 0 | 0
GEN-2023-229 | 04 SOUTHEAST | Wind | Oct 1 - Nov 30 (Near Term) | 230 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 0 | 0 | 0 | 91.3636 | 0 | 0 | 230 | 0 | 0 | 0
GEN-2023-230 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 150 | N/A | 150 | 150 | 150 | N/A | 150 | 0 | 0
GEN-2023-230 | 04 SOUTHEAST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 150 | N/A | 150 | 150 | 150 | N/A | 150 | 0 | 0
GEN-2023-230 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 150 | N/A | 150 | 150 | 150 | N/A | 150 | 0 | 0
GEN-2023-230 | 04 SOUTHEAST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 150 | N/A | 150 | 150 | 150 | N/A | 150 | 0 | 0
GEN-2023-230 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 150 | N/A | 150 | 150 | 150 | N/A | 150 | 0 | 0
GEN-2023-230 | 04 SOUTHEAST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 150 | N/A | 150 | 150 | 150 | N/A | 150 | 0 | 0
GEN-2023-230 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 150 | N/A | 150 | 150 | 150 | N/A | 150 | 0 | 0
GEN-2023-230 | 04 SOUTHEAST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 150 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 150 | 150 | N/A | 150 | 150 | 150 | N/A | 150 | 0 | 0
GEN-2023-241 | 04 SOUTHEAST | Solar | April 1 - May 31 (Long Term) | 93 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 93 | 93 | N/A | 93 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-241 | 04 SOUTHEAST | Solar | April 1 - May 31 (Near Term) | 93 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 93 | 93 | N/A | 93 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-241 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Long Term) | 93 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 93 | 93 | N/A | 93 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-241 | 04 SOUTHEAST | Solar | Dec 1 - March 31 (Near Term) | 93 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 93 | 93 | N/A | 93 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-241 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Long Term) | 93 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 93 | 93 | N/A | 93 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-241 | 04 SOUTHEAST | Solar | June 1 - Sept 30 (Near Term) | 93 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 93 | 93 | N/A | 93 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-241 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Long Term) | 93 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 93 | 93 | N/A | 93 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-241 | 04 SOUTHEAST | Solar | Oct 1 - Nov 30 (Near Term) | 93 | 0 | Stability | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | 93 | 93 | N/A | 93 | N/A | N/A | N/A | N/A | 0 | 0
ASGI-2023-001 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 20 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
ASGI-2023-001 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 20 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
ASGI-2023-001 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 20 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
ASGI-2023-001 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 20 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
ASGI-2023-001 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 20 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
ASGI-2023-001 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 20 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
ASGI-2023-001 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 20 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
ASGI-2023-001 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 20 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-001 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 230 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-001 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 230 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-001 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 230 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-001 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 230 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-001 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 230 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-001 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 230 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-001 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 230 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-001 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 230 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-005 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-005 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-005 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-005 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-005 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-005 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-005 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-005 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-008 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 75 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-008 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 75 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-008 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 75 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-008 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 75 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-008 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 75 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-008 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 75 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-008 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 75 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-008 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 75 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-010 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 280 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 273.3082 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-010 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 280 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 273.3082 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-010 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 280 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 273.3082 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-010 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 280 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 273.3082 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-010 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 280 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 273.3082 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-010 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 280 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 273.3082 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-010 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 280 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 273.3082 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-010 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 280 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 273.3082 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-060 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-060 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-060 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-060 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-060 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-060 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-060 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-060 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 256 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-081 | 05 SOUTHWEST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 625 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-081 | 05 SOUTHWEST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 625 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-081 | 05 SOUTHWEST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 625 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-081 | 05 SOUTHWEST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 625 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-081 | 05 SOUTHWEST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 625 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-081 | 05 SOUTHWEST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 625 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-081 | 05 SOUTHWEST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 625 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-081 | 05 SOUTHWEST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 625 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-086 | 05 SOUTHWEST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 253.7818 | 0 | 0
GEN-2023-086 | 05 SOUTHWEST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 253.7818 | 0 | 0
GEN-2023-086 | 05 SOUTHWEST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 253.7818 | 0 | 0
GEN-2023-086 | 05 SOUTHWEST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 253.7818 | 0 | 0
GEN-2023-086 | 05 SOUTHWEST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 253.7818 | 0 | 0
GEN-2023-086 | 05 SOUTHWEST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 253.7818 | 0 | 0
GEN-2023-086 | 05 SOUTHWEST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 253.7818 | 0 | 0
GEN-2023-086 | 05 SOUTHWEST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 253.7818 | 0 | 0
GEN-2023-110 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-110 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-110 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-110 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-110 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-110 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-110 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-110 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-120 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 130 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-120 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 130 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-120 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 130 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-120 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 130 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-120 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 130 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-120 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 130 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-120 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 130 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-120 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 130 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-123 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 285 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 241.3144 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-123 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 285 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 241.3144 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-123 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 285 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 241.3144 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-123 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 285 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 241.3144 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-123 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 285 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 241.3144 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-123 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 285 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 241.3144 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-123 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 285 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 241.3144 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-123 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 285 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 241.3144 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-142 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 275 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-142 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 275 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-142 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 275 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-142 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 275 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-142 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 275 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-142 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 275 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-142 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 275 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-142 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 275 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-143 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-143 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-143 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-143 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-143 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-143 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-143 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-143 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-158 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 335 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-158 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 335 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-158 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 335 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-158 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 335 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-158 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 335 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-158 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 335 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-158 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 335 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-158 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 335 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-159 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Long Term) | 170 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-159 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Near Term) | 170 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-159 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Long Term) | 170 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-159 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Near Term) | 170 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-159 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Long Term) | 170 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-159 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Near Term) | 170 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-159 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 170 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-159 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 170 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-176 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 292.8302 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-176 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 292.8302 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-176 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 292.8302 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-176 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 292.8302 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-176 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 292.8302 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-176 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 292.8302 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-176 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 292.8302 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-176 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 292.8302 | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-178 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-178 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-178 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-178 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-178 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-178 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-178 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-178 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-183 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Long Term) | 217 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 203.4622 | 215.6868 | N/A | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-183 | 05 SOUTHWEST | Thermal | April 1 - May 31 (Near Term) | 217 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 203.4622 | 215.6868 | N/A | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-183 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Long Term) | 217 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 203.4622 | 215.6868 | N/A | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-183 | 05 SOUTHWEST | Thermal | Dec 1 - March 31 (Near Term) | 217 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 203.4622 | 215.6868 | N/A | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-183 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Long Term) | 217 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 203.4622 | 215.6868 | N/A | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-183 | 05 SOUTHWEST | Thermal | June 1 - Sept 30 (Near Term) | 217 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 203.4622 | 215.6868 | N/A | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-183 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Long Term) | 217 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 203.4622 | 215.6868 | N/A | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-183 | 05 SOUTHWEST | Thermal | Oct 1 - Nov 30 (Near Term) | 217 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 203.4622 | 215.6868 | N/A | 136.6977 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-184 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-184 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-184 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-184 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-184 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-184 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-184 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-184 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-188 | 05 SOUTHWEST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 160 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-188 | 05 SOUTHWEST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 160 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-188 | 05 SOUTHWEST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 160 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-188 | 05 SOUTHWEST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 160 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-188 | 05 SOUTHWEST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 160 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-188 | 05 SOUTHWEST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 160 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-188 | 05 SOUTHWEST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 160 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-188 | 05 SOUTHWEST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 160 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-195 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 51.5591 | 86.0379 | N/A | 0 | 0 | 0
GEN-2023-195 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 51.5591 | 86.0379 | N/A | 0 | 0 | 0
GEN-2023-195 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 51.5591 | 86.0379 | N/A | 0 | 0 | 0
GEN-2023-195 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 51.5591 | 86.0379 | N/A | 0 | 0 | 0
GEN-2023-195 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 51.5591 | 86.0379 | N/A | 0 | 0 | 0
GEN-2023-195 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 51.5591 | 86.0379 | N/A | 0 | 0 | 0
GEN-2023-195 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 51.5591 | 86.0379 | N/A | 0 | 0 | 0
GEN-2023-195 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 51.5591 | 86.0379 | N/A | 0 | 0 | 0
GEN-2023-201 | 05 SOUTHWEST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-201 | 05 SOUTHWEST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-201 | 05 SOUTHWEST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-201 | 05 SOUTHWEST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-201 | 05 SOUTHWEST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-201 | 05 SOUTHWEST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-201 | 05 SOUTHWEST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-201 | 05 SOUTHWEST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-203 | 05 SOUTHWEST | Hybrid; Solar/Storage | April 1 - May 31 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-203 | 05 SOUTHWEST | Hybrid; Solar/Storage | April 1 - May 31 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-203 | 05 SOUTHWEST | Hybrid; Solar/Storage | Dec 1 - March 31 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-203 | 05 SOUTHWEST | Hybrid; Solar/Storage | Dec 1 - March 31 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-203 | 05 SOUTHWEST | Hybrid; Solar/Storage | June 1 - Sept 30 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-203 | 05 SOUTHWEST | Hybrid; Solar/Storage | June 1 - Sept 30 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-203 | 05 SOUTHWEST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Long Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-203 | 05 SOUTHWEST | Hybrid; Solar/Storage | Oct 1 - Nov 30 (Near Term) | 300 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-208 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-208 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-208 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-208 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-208 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-208 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-208 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-208 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 200 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | N/A | N/A | N/A | N/A | 0 | 0
GEN-2023-209 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Long Term) | 125 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 109.5777 | 0 | 0
GEN-2023-209 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Near Term) | 125 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 109.5777 | 0 | 0
GEN-2023-209 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Long Term) | 125 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 109.5777 | 0 | 0
GEN-2023-209 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Near Term) | 125 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 109.5777 | 0 | 0
GEN-2023-209 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Long Term) | 125 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 109.5777 | 0 | 0
GEN-2023-209 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Near Term) | 125 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 109.5777 | 0 | 0
GEN-2023-209 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 125 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 109.5777 | 0 | 0
GEN-2023-209 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 125 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 109.5777 | 0 | 0
GEN-2023-228 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-228 | 05 SOUTHWEST | Battery/Storage | April 1 - May 31 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-228 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-228 | 05 SOUTHWEST | Battery/Storage | Dec 1 - March 31 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-228 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-228 | 05 SOUTHWEST | Battery/Storage | June 1 - Sept 30 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-228 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Long Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-228 | 05 SOUTHWEST | Battery/Storage | Oct 1 - Nov 30 (Near Term) | 250 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-236 | 05 SOUTHWEST | Solar | April 1 - May 31 (Long Term) | 400 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-236 | 05 SOUTHWEST | Solar | April 1 - May 31 (Near Term) | 400 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-236 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Long Term) | 400 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-236 | 05 SOUTHWEST | Solar | Dec 1 - March 31 (Near Term) | 400 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-236 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Long Term) | 400 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-236 | 05 SOUTHWEST | Solar | June 1 - Sept 30 (Near Term) | 400 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-236 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Long Term) | 400 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-236 | 05 SOUTHWEST | Solar | Oct 1 - Nov 30 (Near Term) | 400 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | N/A | 0 | 0 | 0 | N/A | 0 | 0 | 0
GEN-2023-237 | 05 SOUTHWEST | Wind | April 1 - May 31 (Long Term) | 500 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 500 | 0 | 500 | 500 | 500 | 500 | 0 | 0
GEN-2023-237 | 05 SOUTHWEST | Wind | April 1 - May 31 (Near Term) | 500 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 500 | 0 | 500 | 500 | 500 | 500 | 0 | 0
GEN-2023-237 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Long Term) | 500 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 500 | 0 | 500 | 500 | 500 | 500 | 0 | 0
GEN-2023-237 | 05 SOUTHWEST | Wind | Dec 1 - March 31 (Near Term) | 500 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 500 | 0 | 500 | 500 | 500 | 500 | 0 | 0
GEN-2023-237 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Long Term) | 500 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 500 | 0 | 500 | 500 | 500 | 500 | 0 | 0
GEN-2023-237 | 05 SOUTHWEST | Wind | June 1 - Sept 30 (Near Term) | 500 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 500 | 0 | 500 | 500 | 500 | 500 | 0 | 0
GEN-2023-237 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Long Term) | 500 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 500 | 0 | 500 | 500 | 500 | 500 | 0 | 0
GEN-2023-237 | 05 SOUTHWEST | Wind | Oct 1 - Nov 30 (Near Term) | 500 | 0 | Stability/Non-Converged: System Intact | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line | 0 | 0 | 500 | 0 | 500 | 500 | 500 | 500 | 0 | 0

## Constraints Summary
Group | Study Name | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00ALL | DISIS-2023-001 | ERIS | Non-Converged | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00ALL | DISIS-2023-001 | ERIS | Thermal | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: | 219 | 219 | <90% | 103.99 |  |  |  | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
00ALL | DISIS-2023-001 | ERIS | Thermal | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 27WP | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | 500 | 550 | 99.41 | 107.86 |  |  |  | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
00ALL | DISIS-2023-001 | ERIS | Thermal | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 27WP | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | 400 | 440 | 103.88 | 112.49 |  |  |  | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
00ALL | DISIS-2023-001 | ERIS | Thermal | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 27WP | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | 500 | 550 | 97.2 | 105.16 |  |  |  | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
00ALL | DISIS-2023-001 | ERIS | Thermal | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 27WP | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | 400 | 440 | 103.88 | 108.51 |  |  |  | Upgrade the Neosho 345/161 kV Transformer; Reconfigure the Neosho Transformers
00ALL | DISIS-2023-001 | ERIS | Thermal | 547467 ORO110 5 161 547469 RIV4525 161 1 | 27WP | 547469 RIV4525 161 547498 STL439 5 161 1 | 404 | 420 | 109.19 | 106.9 |  |  |  | ORO11505 to RIV4525 Ckt 1 Rating Update
00ALL | DISIS-2023-001 | ERIS | Thermal | 547469 RIV4525 161 547498 STL439 5 161 1 | 24SP,27SP,27WP | 547467 ORO110 5 161 547469 RIV4525 161 1 | 461 | 461 | 92.48 | 100.35 |  |  |  | RIV4525 to STL439 Ckt 1 Rating Update
00ALL | DISIS-2023-001 | ERIS | Thermal | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 24SP,27SP,27WP | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | <90% | 140.8 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 24SP,27SP,27WP | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | <90% | 141.4 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 99 | 99 | <90% | 200.2 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640076 BEATRCE7 115 640361 STEINER7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 121 | 121 | <90% | 105.68 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 140 | 140 | <90% | 249.59 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 24SP,27SP,27WP | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 193 | 193 | <90% | 198.98 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640088 BPS SUB7 115 996909 BPS_345_115 115 1 | 27SP,27WP | System-Intact | 417 | 417 | <90% | 174.4 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640088 BPS SUB7 115 996911 BPS_345_115 115 1 | 24SP | System-Intact | 417 | 417 | <90% | 174.4 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 137 | 137 | <90% | 248.32 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 99 | 99 | <90% | 117.05 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640234 HUMBOLT5 161 996840 HUMBOLDT T2 115 1 | 27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 126 | 126 | <90% | 101.7 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640234 HUMBOLT5 161 996842 HUMBOLDT T2 115 1 | 24SP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 126 | 126 | <90% | 100.58 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640235 HUMBOLT7 115 640361 STEINER7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 121 | 121 | <90% | 103.74 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 640278 SHELDON7 115 650246 SW7&BENNET7 115 1 | 24SP,27SP | Potential P4 Event - POI 640590_0 | 240 | 240 | <90% | 103.19 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 645455 S3455 3 345 645740 S3740 3 345 1 | 24SP,27SP,27WP | Potential P4 Event - POI 645740_1 | 1195 | 1195 | <90% | 140.66 |  |  |  | Line - S3454 - S3740 345 kV
00ALL | DISIS-2023-001 | ERIS | Thermal | 645458 S3458 3 345 645740 S3740 3 345 1 | 24SP,27SP,27WP | P12:345:OPPD:S3455-S3740:::EHV: | 1073 | 1073 | <90% | 156.81 |  |  |  | S3458 to S3740 345 kV Ckt 2 New Line
00ALL | DISIS-2023-001 | ERIS | Thermal | 771999 G23-222-POI 345 996909 BPS_345_115 115 1 | 27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 417 | 417 | <90% | 171.47 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Thermal | 771999 G23-222-POI 345 996911 BPS_345_115 115 1 | 24SP | System-Intact | 417 | 417 | <90% | 170.93 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 | ERIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
01ALL | DISIS-2023-001 | ERIS | Non-Converged | None | 24SP, 27SP, 27WP | None | [7 empty] | None
01ALL | DISIS-2023-001 | ERIS | Non-Converged | Non-Converged | 27L | 640510 HOLT.CO3 345 652832 GRPRAR1-LNX3 345 1 | [7 empty] | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1
01ALL | DISIS-2023-001 | ERIS | Non-Converged | Non-Converged | 27L | 652532 GR PRAIRIE 3 345 652832 GRPRAR1-LNX3 345 Z | [7 empty] | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 589324 G17-094-TAP 230 652507 FTTHOMP4 230 1 | 24SP, 27SP | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | <90% | 107.79 |  |  |  | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
01ALL | DISIS-2023-001 | ERIS | Thermal | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 24SP, 27SP | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 352 | 352 | <90% | 112.28 |  |  |  | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
01ALL | DISIS-2023-001 | ERIS | Thermal | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 27L | System Intact | 387 | 387 | 108.41 | 106.94 |  |  |  | Rebuild the COLMBUS4 to MEADOWGROVE4 230kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 640540 MEADOWGROVE4 230 652509 FTRANDL4 230 1 | 24SP, 27SP, 27WP | POI 652532_1 | 320 | 320 | 103.5 | 120.34 |  |  |  | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652499 CAMPBELL 4 230 661038 GLENHAM4 230 1 | 27L | System Intact | 240 | 264 | 112.57 | 101.32 |  |  |  | Rebuild the CAMPBELL 4 to GLENHAM4 230kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 24SP, 27L, 27SP | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | 760 | 760 | <90% | 119.71 |  |  |  | Rebuild the FTTHOM to GRPRAR 345kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 24SP, 27L, 27SP | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | 760 | 760 | 95.24 | 120.47 |  |  |  | FTTHOMP3 to FTTHOM1-LNX3 345 kV Line Z Rating Update
01ALL | DISIS-2023-001 | ERIS | Thermal | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 24SP, 27L, 27SP | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 844 | 844 | 104.57 | 124.26 |  |  |  | Rebuild the FTTHOM to GRPRAR 345kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 24SP, 27L, 27SP | System Intact | 844 | 844 | 99.68 | 116.2 |  |  |  | Rebuild the FTTHOM to GRPRAR 345kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 24SP, 27SP, 27WP | POI 652532_1 | 318 | 318 | 114.05 | 134.18 |  |  |  | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 24SP, 27SP | POI 652532_1 | 352 | 352 | 103.39 | 121.44 |  |  |  | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 24SP, 27SP, 27WP | POI 652532_1 | 320 | 320 | 109.17 | 128.67 |  |  |  | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 24SP, 27L, 27SP | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV: | 120 | 120 | 108.91 | 119.89 |  |  |  | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 24SP, 27L, 27SP | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV: | 120 | 120 | 105.26 | 116.21 |  |  |  | Rebuild the SUMMIT-7 to BRISTOL-ER7 115kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 24SP, 27SP | P23:345:XEL:396 BKR SPK | 342 | 343 | 100.59 | 116.54 |  |  |  | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 24SP, 27L, 27SP | System Intact | 844 | 844 | 98.95 | 115.42 |  |  |  | Rebuild the FTTHOM to GRPRAR 345kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 24SP, 27L, 27SP | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 844 | 844 | 103.89 | 123.39 |  |  |  | Rebuild the FTTHOM to GRPRAR 345kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 24SP, 27L, 27SP | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 844 | 844 | 102.86 | 121.89 |  |  |  | Rebuild the FTTHOM to GRPRAR 345kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 24SP, 27L, 27SP | System Intact | 844 | 844 | 97.74 | 114.16 |  |  |  | Rebuild the FTTHOM to GRPRAR 345kV Line 1
01ALL | DISIS-2023-001 | ERIS | Thermal | 655048 LAKECNTY-ER8 69.0 655119 LAKECNTY-ER7 115 1 | 24SP | P12:115:UMZ:# 20008 #:: PROPER N-1 FOR TAP ARLNGTN-ER7:HV: | 56 | 56 | <90% | 119.54 |  |  |  | Multi - Madison, SD Area 115 kV System Voltage Conversion
01ALL | DISIS-2023-001 | ERIS | Thermal | 655048 LAKECNTY-ER8 69.0 655223 WENTWRTH-ER8 69.0 1 | 24SP | P12:115:UMZW:# 1521 #:: AG IN SD. AG-BR BRANCH FAULT (AG IS A TAP):HV: | 35 | 35 | <90% | 130.76 |  |  |  | Multi - Madison, SD Area 115 kV System Voltage Conversion
01ALL | DISIS-2023-001 | ERIS | Thermal | 659311 PAHOJA__-BE4 230 659900 EAGLE___-NI4 230 1 | 24SP, 27SP | P23:345:XEL:396 BKR SPK | 373 | 373 | <90% | 102.86 |  |  |  | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1
01ALL | DISIS-2023-001 | ERIS | Voltage | CHMBRLAN-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8814 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | COLTON-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8635 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | DAYTON__-ER7 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.892 | 0.9 | 1.05 | Multi - Sioux Falls 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | DOLTON-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8373 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | EMERY-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8754 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | FARMER-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8779 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | GRNDMEAD-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.866 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | HANLON1-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8748 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | HANLON2-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8748 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | HILLTOP-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8769 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | HRRISBRG-ER7 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8907 | 0.9 | 1.05 | Multi - Sioux Falls 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | HUMBOLT-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8713 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | HURLEY-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8843 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | INDMARIN-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8249 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | LAKPLAT-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8926 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | LINCOLN-ER7 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8906 | 0.9 | 1.05 | Multi - Sioux Falls 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | LYONS-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8633 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | MARION-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8293 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MARIONRD-ER7 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8961 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MENNO-ER8 | 24SP, 27SP | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 |  |  |  |  | 0.8872 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MITCHELL-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8849 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MONTROSE-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8669 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-CLTN-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8635 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-ELIS-ER7 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8987 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-HLTP-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8768 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-HMPA-ER8 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8931 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-HRLM-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8866 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-INDM-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8297 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-KLKP-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8659 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-LKPL-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8926 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-LTCH-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8903 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-MRRD-ER7 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8981 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-NMAR-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8617 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-PARK-ER8 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8946 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-PLAT-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8857 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-PLNO-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.883 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-RVR1-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8878 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-RVR2-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8878 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-SALM-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8669 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | MOS-SPNC-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8625 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | MTVERNON-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8968 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | None | 27L, 27WP | None | [7 empty] | None
01ALL | DISIS-2023-001 | ERIS | Voltage | ORLAND-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8509 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | PARKERCI-ER8 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8912 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | PARKER-ER8 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8937 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | PLANO-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8811 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | PUKWANA-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8725 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | SALEM-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8669 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | SANDCRK-ER8 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8951 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SHINDLER-ER7 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8884 | 0.9 | 1.05 | Multi - Sioux Falls 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SPENCER-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8625 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SUNDOWN-ER7 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8993 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SW1142-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8744 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | SW124-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8666 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | SW130-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8669 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SW144-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8427 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SW145-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8539 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | SW156-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8394 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SW159-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8685 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | SW162-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8519 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | SW170-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8724 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | SW412-ER8 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8981 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SW425-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8768 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV
01ALL | DISIS-2023-001 | ERIS | Voltage | SW640-ER8 | 24SP, 27SP | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 |  |  |  |  | 0.8854 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SW-EMERY-ER8 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8775 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SW-EMERY-ER8 | 24SP, 27SP | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 |  |  |  |  | 0.8777 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SW-SANDC-ER8 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8958 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SW-SPENC-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8625 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SXFALLS2-ER7 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8982 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | SYCAMORE-ER7 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8904 | 0.9 | 1.05 | Multi - Sioux Falls 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | TRKYRDGE-ER8 | 24SP, 27SP | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 |  |  |  |  | 0.885 | 0.9 | 1.05 | Multi - Marion Area 115 kV Voltage Conversion Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | WILBUR-ER8 | 24SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8976 | 0.9 | 1.05 | Multi - Hanson County 115 kV System Reconfig
01ALL | DISIS-2023-001 | ERIS | Voltage | XLSW4X1-ER8 | 24SP, 27SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: |  |  |  |  | 0.8669 | 0.9 | 1.05 | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV
01NR | DISIS-2023-001 | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
01NR | DISIS-2023-001 | NRIS | Thermal | None | 27L | None | [7 empty] | None
01NR | DISIS-2023-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
02ALL | DISIS-2023-001 | ERIS | Non-Converged | Non-Converged | 24SP, 27L, 27SP, 27WP | POI 640252_0 | [7 empty] | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Stability | Unstable power response with failed voltage recovery was observed at GENTLM1G (640010), GENTLM2G (640011), SIDNEY___TS4 (659134), and other nearby units. | 25SP, 25WP | GROUP2_P4_LOCAL_FAULT_416 | [7 empty] | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 27WP | POI 640065_1 | 956 | 966 | <90% | 104.14 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 533303 MARSHAL3 115 533332 KNOB HL3 115 1 | 27L | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 92 | 92 | <90% | 105.87 |  |  |  | Rebuild the MARSHAL3 to KNOB HL3 115kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 27L | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 956 | 1135 | <90% | 105.55 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 27L | POI 763982_4 | 956 | 1135 | <90% | 105.55 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 27WP | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | 956 | 956 | <90% | 106.95 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 27WP | POI 767280_2 | 956 | 956 | <90% | 106.95 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 24SP, 27L, 27SP, 27WP | P12:115:WERE:KNOB-NPPD-115:::HV: | 99 | 99 | <90% | 187.41 |  |  |  | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 27L, 27WP | System Intact | 99 | 99 | <90% | 122.61 |  |  |  | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640080 BELDEN 7 115 640228 HOSKINS7 115 1 | 27L | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | 115 | 115 | <90% | 119.97 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640080 BELDEN 7 115 640228 HOSKINS7 115 1 | 27L | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | 115 | 115 | <90% | 119.97 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640082 BEVERLY7 115 640167 ENDERS 7 115 1 | 27WP | P42:345:NPPD:BKR-GGS-3322:::: | 160 | 160 | <90% | 122.4 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640082 BEVERLY7 115 640326 REDWILO7 115 1 | 27WP | P42:345:NPPD:BKR-GGS-3322:::: | 160 | 160 | <90% | 107.8 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640136 COLMBUS7 115 640151 CRESTON7 115 1 | 27L | POI 763982_4 | 120 | 120 | <90% | 108.87 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640136 COLMBUS7 115 640151 CRESTON7 115 1 | 27L | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 120 | 120 | <90% | 108.87 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640151 CRESTON7 115 640263 MADISON7 115 1 | 27L, 27WP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 120 | 120 | 96.23 | 118.41 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640151 CRESTON7 115 640263 MADISON7 115 1 | 27L, 27WP | POI 763982_4 | 120 | 120 | 96.23 | 118.41 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640163 EMERSON7 115 640387 TWIN CH7 115 1 | 27SP, 27WP | P12:230:WAPA:TWINCH-SIOUXCY:1 | 120 | 120 | <90% | 101.68 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 24SP, 27L, 27SP, 27WP | System Intact | 1195 | 1195 | <90% | 126.95 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 24SP, 27L, 27SP, 27WP | POI 640226_1 | 1195 | 1195 | <90% | 137.12 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 24SP, 27L, 27SP, 27WP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 120 | 120 | 105.17 | 127.42 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 24SP, 27L, 27SP, 27WP | POI 763982_4 | 120 | 120 | 105.17 | 127.42 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 27L | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001:: | 956 | 956 | <90% | 107.82 |  |  |  | Line - Elm Creek 345 kV - Tobias 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640277 MOORE 3 345 996822 MOORE T1 115 1 | 27WP | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | 336 | 400 | <90% | 103.36 |  |  |  | Line - Elm Creek 345 kV - Tobias 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640278 SHELDON7 115 996822 MOORE T1 115 1 | 27WP | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | 336 | 400 | <90% | 100.47 |  |  |  | Line - Elm Creek 345 kV - Tobias 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 24SP, 27SP, 27WP | P42:345:NPPD:BKR-GGS-3322:::: | 137 | 165 | 106.4 | 140.27 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640326 REDWILO7 115 640365 STOCKVL7 115 1 | 27WP | P42:345:NPPD:BKR-GGS-3322:::: | 137 | 190 | <90% | 117.4 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 27L | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | 1195 | 1195 | <90% | 108.46 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 27L | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | 1195 | 1195 | <90% | 108.46 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 27L, 27SP, 27WP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | 336 | 360 | <90% | 104.19 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 27L, 27SP, 27WP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | 336 | 360 | <90% | 107.13 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640342 SHELCRK3 345 996785 SHELLCREEKT1 230 1 | 24SP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | 336 | 360 | <90% | 106 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640342 SHELCRK3 345 996785 SHELLCREEKT1 230 1 | 24SP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | 336 | 360 | <90% | 103.79 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 27L, 27SP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | 336 | 360 | <90% | 105.94 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 27L, 27SP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | 336 | 360 | <90% | 103.5 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640343 SHELCRK4 230 996785 SHELLCREEKT1 230 1 | 24SP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | 336 | 360 | <90% | 105.18 |  |  |  | Line - Holt County 345 kV - Antelope 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Thermal | 640343 SHELCRK4 230 996785 SHELLCREEKT1 230 1 | 24SP | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | 336 | 360 | <90% | 102.99 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 27WP | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 717 | 717 | <90% | 107.78 |  |  |  | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 24SP, 27L, 27SP, 27WP | POI 640226_1 | 320 | 425 | 91.04 | 133.48 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 24SP, 27L, 27SP, 27WP | System Intact | 320 | 425 | <90% | 112.98 |  |  |  | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 24SP, 27SP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 1160 | 1160 | <90% | 101.87 |  |  |  | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 24SP, 27SP | System Intact | 1000 | 1000 | <90% | 101.57 |  |  |  | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Thermal | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 24SP, 27L, 27SP, 27WP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 1000 | 1000 | 91.47 | 118.17 |  |  |  | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
02ALL | DISIS-2023-001 | ERIS | Voltage | GRANT 3 | 27WP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8984 | 0.9 | 1.05 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
02ALL | DISIS-2023-001 | ERIS | Voltage | GRANT 3 | 27WP | POI 531449_1 |  |  |  |  | 0.8984 | 0.9 | 1.05 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
02ALL | DISIS-2023-001 | ERIS | Voltage | GRANTTP3 | 27WP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8986 | 0.9 | 1.05 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
02ALL | DISIS-2023-001 | ERIS | Voltage | GRANTTP3 | 27WP | POI 531449_1 |  |  |  |  | 0.8986 | 0.9 | 1.05 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
02ALL | DISIS-2023-001 | ERIS | Voltage | HASKELL3 | 27WP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8972 | 0.9 | 1.05 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
02ALL | DISIS-2023-001 | ERIS | Voltage | HASKELL3 | 27WP | POI 531449_1 |  |  |  |  | 0.8972 | 0.9 | 1.05 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
02ALL | DISIS-2023-001 | ERIS | Voltage | None | 24SP, 27L, 27SP | None | [7 empty] | None
02ALL | DISIS-2023-001 | ERIS | Voltage | SATMKEC3 | 27WP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.897 | 0.9 | 1.05 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
02ALL | DISIS-2023-001 | ERIS | Voltage | SATMKEC3 | 27WP | POI 531449_1 |  |  |  |  | 0.897 | 0.9 | 1.05 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
02ALL | DISIS-2023-001 | ERIS | Voltage | SAT-TAP3 | 27WP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.897 | 0.9 | 1.05 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
02ALL | DISIS-2023-001 | ERIS | Voltage | SAT-TAP3 | 27WP | POI 531449_1 |  |  |  |  | 0.897 | 0.9 | 1.05 | Build a new 30MVAR Switched Shunt at RUBART 3 115kV
02NR | DISIS-2023-001 | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
02NR | DISIS-2023-001 | NRIS | Thermal | None | 27L | None | [7 empty] | None
02NR | DISIS-2023-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
03ALL | DISIS-2023-001 | ERIS | Non-Converged | Non-Converged | 24SP, 27SP | 533304 LANG 3 115 767120 G22-007-TAP 115 1 | [7 empty] | Build 2nd LANG 3 to G22-007-TAP 115 kV Line
03ALL | DISIS-2023-001 | ERIS | Stability | Unstable behavior, machine tripping, voltage violations | 25SP, 25WP | G3_FLT2043-3PH | [7 empty] | Build 2nd LANG 3 to G22-007-TAP 115 kV Line
03ALL | DISIS-2023-001 | ERIS | Thermal | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 27L | 300042 7HUBEN 345 300045 7MORGAN 345 1 | 167 | 167 | 64.72 | 131.96 |  |  |  | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
03ALL | DISIS-2023-001 | ERIS | Thermal | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 24SP, 27SP, 27WP | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 266 | 266 | 9.85 | 100.45 |  |  |  | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
03ALL | DISIS-2023-001 | ERIS | Thermal | 300117 5SEDALA 161 541209 SEDALIA5 161 1 | 24SP, 27SP | System Intact | 111 | 111 | 123.27 | 125.02 |  |  |  | SEDALA to SEDALIA5 161 kV Line 1 Rating Update
03ALL | DISIS-2023-001 | ERIS | Thermal | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 24SP, 27SP | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | 870 | 870 | 90.97 | 128.8 |  |  |  | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
03ALL | DISIS-2023-001 | ERIS | Thermal | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 27WP | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | 294 | 294 | 85.18 | 107.32 |  |  |  | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
03ALL | DISIS-2023-001 | ERIS | Thermal | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | 1015 | 1015 | 97.81 | 116.72 |  |  |  | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
03ALL | DISIS-2023-001 | ERIS | Thermal | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 27WP | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | 500 | 550 | 88.63 | 112.07 |  |  |  | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
03ALL | DISIS-2023-001 | ERIS | Thermal | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 27WP | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | 400 | 440 | 94.14 | 120.47 |  |  |  | Reconfigure the Neosho Transformers
03ALL | DISIS-2023-001 | ERIS | Thermal | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 27WP | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | 500 | 550 | 84.85 | 110.29 |  |  |  | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
03ALL | DISIS-2023-001 | ERIS | Thermal | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 27WP | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | 400 | 440 | 89.94 | 114.96 |  |  |  | Reconfigure the Neosho Transformers
03ALL | DISIS-2023-001 | ERIS | Thermal | 533745 NEWTON 2 69.0 533746 ADAMS 2 69.0 1 | 27WP | 533011 HALSTD 4 138 3WXFMR HALS TX-4 1 | 55 | 65 | 1.77 | 109.64 |  |  |  | Rebuild the NEWTON 2 to ADAMS 2 69 kV Line 1
03ALL | DISIS-2023-001 | ERIS | Thermal | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 24SP, 27SP | System Intact | 717 | 875 | 90.21 | 101.91 |  |  |  | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
03ALL | DISIS-2023-001 | ERIS | Thermal | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 24SP, 27SP, 27WP | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 233 | 254 | 17.39 | 104.1 |  |  |  | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
03ALL | DISIS-2023-001 | ERIS | Thermal | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 27SP | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | 1248 | 1248 | 78.54 | 100.56 |  |  |  | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
03ALL | DISIS-2023-001 | ERIS | Thermal | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | 24SP, 27SP | POI 542965_9 | 1792 | 1792 | 98.56 | 105.6 |  |  |  | Build STILWEL7 to G21-029-TAP 345 kV Line 1
03ALL | DISIS-2023-001 | ERIS | Thermal | 547467 ORO110 5 161 547469 RIV4525 161 1 | 24SP, 27WP | 547469 RIV4525 161 547498 STL439 5 161 1 | 404 | 420 | 94.13 | 115.19 |  |  |  | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
03ALL | DISIS-2023-001 | ERIS | Thermal | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 24SP, 27SP, 27WP | 532937 NEOSHO 5 161 547469 RIV4525 161 2 | 558 | 558 | 80.84 | 128.83 |  |  |  | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
03ALL | DISIS-2023-001 | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
03NR | DISIS-2023-001 | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
03NR | DISIS-2023-001 | NRIS | Thermal | None | 27L | None | [7 empty] | None
03NR | DISIS-2023-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
04ALL | DISIS-2023-001 | ERIS | Non-Converged | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
04ALL | DISIS-2023-001 | ERIS | Stability | High power export from Group 04 after case dispatch causes case solving and low voltage issues. This causes non-convergence in 25SP under system intact conditions. | 25SP | System-Intact | [7 empty] | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line; Line - Elm Creek 345 kV - Tobias 345 kV New Line; Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
04ALL | DISIS-2023-001 | ERIS | Stability | System intact Low Voltage, Flatline Issues | 25SP | System-Intact | [7 empty] | Build new Benton 345 kV STATCOM; Build new Reno 345 kV Capbank; Build new ELMCREEK7 345kV Capbank
04ALL | DISIS-2023-001 | ERIS | Thermal | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 24SP,27SP | 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | 205 | 205 | <90% | 111.47 |  |  |  | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 504000 AVOCA 5 161 506931 EROGERS5 161 1 | 27WP | System-Intact | 266 | 273 | <90% | 103.55 |  |  |  | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
04ALL | DISIS-2023-001 | ERIS | Thermal | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 27WP | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | 335 | 335 | <90% | 113.4 |  |  |  | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 505590 WELEETK5 161 998044 WLK X1 138 1 | 27L | 301551 4CHECOTA 138 505592 WELEETK4 138 1 | 120 | 120 | <90% | 106.09 |  |  |  | Upgrade the existing WLK X1 161/138 kV Transformer
04ALL | DISIS-2023-001 | ERIS | Thermal | 505592 WELEETK4 138 998044 WLK X1 138 1 | 27L | 301551 4CHECOTA 138 505592 WELEETK4 138 1 | 120 | 120 | <90% | 105.85 |  |  |  | Upgrade the existing WLK X1 161/138 kV Transformer
04ALL | DISIS-2023-001 | ERIS | Thermal | 507189 NHUNTNT5 161 775580 G23-180-TAP 161 1 | 24SP,27SP | 515261 BONANZT5 161 515299 BEVYTAP5 161 1 | 158 | 178 | <90% | 101.74 |  |  |  | Rebuild the existing NHUNTNT5 to G23-180-TAP 161 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: | 1323 | 1393 | <90% | 100.46 |  |  |  | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
04ALL | DISIS-2023-001 | ERIS | Thermal | 508809 LONGWD 7 345 508841 WILKES 7 345 1 | 24SP,27SP,27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: | 1256 | 1256 | <90% | 113.05 |  |  |  | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 509083 ROKHILL4 138 773160 G23-059-TAP 138 1 | 27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: | 219 | 219 | <90% | 113.43 |  |  |  | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update
04ALL | DISIS-2023-001 | ERIS | Thermal | 510398 BIRDHOL4 138 510421 JAY 4 138 1 | 24SP,27SP | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 131 | 151 | <90% | 122.63 |  |  |  | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 510402 GROVE 4 138 510421 JAY 4 138 1 | 24SP,27SP | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 131 | 151 | <90% | 117.57 |  |  |  | Rebuild the existing GROVE 4 to JAY 4 138 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 510402 GROVE 4 138 997939 GROVE 138 1 | 27SP,27WP | P12:161:AEPW-EMDE:FLINTCR5:739952::: | 112 | 112 | <90% | 120.84 |  |  |  | Upgrade the existing GROVE 161/138 kV Transformer
04ALL | DISIS-2023-001 | ERIS | Thermal | 510402 GROVE 4 138 997940 GROVE 138 1 | 24SP | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 112 | 112 | <90% | 117.08 |  |  |  | Upgrade the existing GROVE 161/138 kV Transformer
04ALL | DISIS-2023-001 | ERIS | Thermal | 510411 GROVE 5 161 997939 GROVE 138 1 | 27SP,27WP | P12:161:AEPW-EMDE:FLINTCR5:739952::: | 112 | 112 | <90% | 121.81 |  |  |  | Upgrade the existing GROVE 161/138 kV Transformer
04ALL | DISIS-2023-001 | ERIS | Thermal | 510411 GROVE 5 161 997940 GROVE 138 1 | 24SP | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 112 | 112 | <90% | 118.27 |  |  |  | Upgrade the existing GROVE 161/138 kV Transformer
04ALL | DISIS-2023-001 | ERIS | Thermal | 510898 OKMULGE4 138 510923 EC.HEN-4 138 1 | 24SP | P12:138:AEPW:HENRYET4:WELETK4::: | 152 | 152 | <90% | 101.94 |  |  |  | OKMULGE to ECHEN4 Ckt 1 Rating Update
04ALL | DISIS-2023-001 | ERIS | Thermal | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 24SP,27SP | P12:138:AEPW:HENRYET4:WELETK4::: | 151 | 152 | <90% | 104.71 |  |  |  | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 510918 VALIANT4 138 520948 HUGO PP4 138 1 | 24SP,27SP,27WP,27L | 520560 HUGOITC4 138 520948 HUGO PP4 138 1 | 287 | 287 | <90% | 110.16 |  |  |  | VALIANT to HUGO 138 kV Ckt 1 Rating Update
04ALL | DISIS-2023-001 | ERIS | Thermal | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 24SP,27SP,27WP | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 435 | 435 | <90% | 108.88 |  |  |  | Sweetwater to Chisholm 230 kV Line Rebuild
04ALL | DISIS-2023-001 | ERIS | Thermal | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 24SP,27SP,27WP | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | <90% | 111.98 |  |  |  | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
04ALL | DISIS-2023-001 | ERIS | Thermal | 512631 MIAMI 5 161 512632 AFTON 5 161 1 | 24SP,27SP,27WP | Potential P4 Event - POI 532793_18 | 194 | 194 | <90% | 171.81 |  |  |  | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 24SP,27SP,27WP | Potential P4 Event - POI 532793_18 | 167 | 210 | <90% | 136.36 |  |  |  | MIAMI to HOC404 5 161kV Line Rebuild
04ALL | DISIS-2023-001 | ERIS | Thermal | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 24SP,27SP,27WP | Potential P4 Event - POI 532793_18 | 194 | 194 | <90% | 183.92 |  |  |  | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 512633 AFTON 2 69.0 512708 FAIRTAP2 69.0 1 | 24SP,27SP,27WP | P21:161:GRDA:MIAMI5-AFTON5:::HV: | 72 | 72 | <90% | 199 |  |  |  | AFTON2 to FAIRTAP2 69 kV Ckt 1 Terminal Upgrade
04ALL | DISIS-2023-001 | ERIS | Thermal | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 24SP,27SP,27WP | Potential P4 Event - POI 532793_18 | 194 | 194 | <90% | 188.67 |  |  |  | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 24SP,27SP,27WP | P12:161:GRDA:DRYGULCH5-MAID 5:::HV: | 335 | 335 | <90% | 134.05 |  |  |  | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 512750 TONECE7 345 774740 G23-138-TAP 345 1 | 24SP,27SP,27WP | P23:345:AEPW:CHAMBERS SPRING CB 13850 NBTB:::: | 1182 | 1182 | <90% | 111.12 |  |  |  | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 514803 SOONER 7 345 515576 RANCHRD7 345 1 | 24SP,27SP,27WP | Potential P4 Event - POI 532794_7 | 1716 | 1793 | <90% | 101.73 |  |  |  | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
04ALL | DISIS-2023-001 | ERIS | Thermal | 515077 FIXICO 2 69.0 997804 FIXICO4 69.0 4 | 24SP,27SP,27L | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | 62 | 67 | <90% | 110.5 |  |  |  | Upgrade the existing FIXICO4 138/69 kV Transformer
04ALL | DISIS-2023-001 | ERIS | Thermal | 515078 FIXICO 4 138 997804 FIXICO4 69.0 4 | 24SP,27SP,27L | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | 62 | 67 | <90% | 109.05 |  |  |  | Upgrade the existing FIXICO4 138/69 kV Transformer
04ALL | DISIS-2023-001 | ERIS | Thermal | 515336 VBI 2 69.0 997769 VBI2 69.0 2 | 27SP | System-Intact | 76 | 95 | <90% | 103.63 |  |  |  | Upgrade the existing VBI2 161/69 kV Transformer
04ALL | DISIS-2023-001 | ERIS | Thermal | 515339 VBI 5 161 997769 VBI2 69.0 2 | 27SP | System-Intact | 76 | 95 | <90% | 103.84 |  |  |  | Upgrade the existing VBI2 161/69 kV Transformer
04ALL | DISIS-2023-001 | ERIS | Thermal | 520430 NOELSW 4 138 774060 G23-104-TAP 138 1 | 24SP,27SP,27L | P42:345:OKGE:SB_DGSE7385:::: | 160 | 187 | <90% | 142.32 |  |  |  | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 24SP,27SP,27WP | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | 353 | 353 | <90% | 135.11 |  |  |  | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line
04ALL | DISIS-2023-001 | ERIS | Thermal | 532774 SWISVAL7 345 776380 G23-220-TAP 345 1 | 24SP,27SP | System-Intact | 1076 | 1076 | <90% | 106.07 |  |  |  | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line; Line - Elm Creek 345 kV - Tobias 345 kV New Line
04ALL | DISIS-2023-001 | ERIS | Thermal | 532791 BENTON 7 345 532794 ROSEHIL7 345 1 | 24SP,27SP | P23:345:WERE:WOLF-345-50:::EHV: | 878 | 956 | <90% | 118.12 |  |  |  | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
04ALL | DISIS-2023-001 | ERIS | Thermal | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 24SP,27SP | Potential P4 Event - POI 532794_2 | 1294 | 1294 | <90% | 103.8 |  |  |  | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
04ALL | DISIS-2023-001 | ERIS | Thermal | 532794 ROSEHIL7 345 560053 G15052_T 345 1 | 24SP,27SP,27WP | P42:345:OKGE:SB_DGSE7313:::: | 1532 | 1793 | <90% | 124.84 |  |  |  | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2; Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2; Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1; Line - Buffalo Flats 345 kV - Delaware 345 kV New Line
04ALL | DISIS-2023-001 | ERIS | Thermal | 542981 LACYGNE7 345 767240 G22-013-TAP 345 1 | 24SP | Potential P4 Event - POI 532794_7 | 1015 | 1015 | <90% | 101.92 |  |  |  | Line - Wolf Creek - Blackberry 345 kV
04ALL | DISIS-2023-001 | ERIS | Thermal | 767240 G22-013-TAP 345 776600 G23-231-TAP 345 1 | 24SP | Potential P4 Event - POI 532794_7 | 1015 | 1015 | <90% | 102.19 |  |  |  | Line - Wolf Creek - Blackberry 345 kV
04ALL | DISIS-2023-001 | ERIS | Voltage | ARNOLD3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8658 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | BEELER 3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8692 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | BIRDCTY3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.8701 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | BREWSTR3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.8984 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | BVERVLLY | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.8848 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | CHASE 3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8256 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | CNTRLPL3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.854 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | CSTFRAN3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.8578 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | DIGHTON3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8526 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | ELLIS 2 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8564 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | GANO 3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8426 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | GODLNDT3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.8681 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | GOODCTY3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.8638 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | GOODLND3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.8699 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | GOVE 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8772 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | JAGGER 3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8533 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | KANARAD3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8272 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | LAWNRID3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.8497 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | LEOTI 3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8422 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | LIBERTY3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8553 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | LIBERTYT | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.86 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | MANNGT 3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8471 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | MANNING3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8459 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | MCDONLD3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.881 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | NESCTY 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8721 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | NESSCTY3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.872 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | None | 27L, 27WP | None | [7 empty] | None
04ALL | DISIS-2023-001 | ERIS | Voltage | NSI | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8343 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | NSI TAP3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8352 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | ONEOK 3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.8838 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | PALMER3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8311 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | PILE 3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8268 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | RANSOM 2 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8633 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | RANSOM 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8658 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | RULETON3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8463 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | RUSHMORE-RM8 | 24SP,27SP | P42:345:NPPD:BKR-MOR-3312:::: |  |  |  |  | 0.8954 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | SCOTCTY3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8447 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | SELKIRK3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8395 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | SETAB 3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8577 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | SHARNSP3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8257 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | STFRAN 3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.8599 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | STFRANT3 | 24SP,27SP | Potential P4 Event - POI 531465_2 |  |  |  |  | 0.858 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | SYRACUS3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8668 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | TRIB SW3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8351 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | TRIBUNE3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8348 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | WILLIAM3 | 24SP,27SP | Potential P4 Event - POI 531449_3 |  |  |  |  | 0.8921 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | WTCLF 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8191 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04ALL | DISIS-2023-001 | ERIS | Voltage | WTCLFTP3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8203 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line
04NR | DISIS-2023-001 | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
04NR | DISIS-2023-001 | NRIS | Thermal | None | 27L | None |  |  | <90% |  |  |  |  | None
04NR | DISIS-2023-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
05ALL | DISIS-2023-001 | ERIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | [7 empty] | Build new Tolk to Needmore 230 kV Line
05ALL | DISIS-2023-001 | ERIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | System-Intact | [7 empty] | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
05ALL | DISIS-2023-001 | ERIS | Stability | High power export from Group 05 after case dispatch causes case solving and low voltage issues. This causes non-convergence in 25SP, 25WP under system intact conditions. | 25SP, 25WP | System-Intact | [7 empty] | Build New Phantom to Crossroads to Potter 765 kV Line; Build New Beckham to Potter 345 kV Line; Build new Double Circuit Crawfish to Seminole 765 kV Line; Build new Potter to Chisholm 765 kV Line
05ALL | DISIS-2023-001 | ERIS | Stability | Fault Crashing Issues due to lack of reactive power support to handle G05 exports | 25SP | P1_525832_TUCO_INT-560022_CRAWFISH_DR_Ckt2 | [7 empty] | Build new Border 345 kV STATCOM
05ALL | DISIS-2023-001 | ERIS | Stability | Fault Crashing Issues due to lack of reactive power support to handle G05 exports | 25SP | P1_516059_BECKHAM7-511553_CHISHOLM7_Ckt1 | [7 empty] | Build new Potter 345 kV STATCOM
05ALL | DISIS-2023-001 | ERIS | Stability | Fault Crashing Issues due to lack of reactive power support to handle G05 exports | 25WP | P1_523961_POTTER_CO-516059_BECKHAM7_Ckt2 | [7 empty] | Build new Potter 345 kV STATCOM
05ALL | DISIS-2023-001 | ERIS | Stability | Fault Crashing Issues due to lack of reactive power support to handle G05 exports | 25WP | P1_560022_CRAWFISH_DR-525832_TUCO_INT_Ckt2 | [7 empty] | Build new Border 345 kV STATCOM
05ALL | DISIS-2023-001 | ERIS | Stability | Fault Crashing Issues due to lack of reactive power support to handle G05 exports | 25WP | P1_511456_OKU-7-766291_G20-009-TAP_Ckt2 | [7 empty] | Build new Crawfish 345 kV STATCOM
05ALL | DISIS-2023-001 | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 27WP | Potential P4 Event - POI 511468_7 | 956 | 956 | <90% | 114.36 |  |  |  | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 27SP,27WP | Potential P4 Event - POI 515375_50 | 279 | 330 | <90% | 138.19 |  |  |  | Upgrade the existing ELKCITY6 230/138 kV Transformer
05ALL | DISIS-2023-001 | ERIS | Thermal | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 24SP,27SP | POI 515800_22 | 353 | 353 | <90% | 134.08 |  |  |  | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 27SP,27WP | Potential P4 Event - POI 515375_50 | 279 | 330 | <90% | 137.17 |  |  |  | Upgrade the existing ELKCITY6 230/138 kV Transformer
05ALL | DISIS-2023-001 | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 24SP,27SP | P12:115:SPS:T08_2_SPRMN_PRNGLE:::: | 159 | 159 | <90% | 118.92 |  |  |  | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line
05ALL | DISIS-2023-001 | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2 | 24SP,27SP | P12:115:SPS:T06_1_SPRMN_PRNGLE:::: | 159 | 159 | <90% | 107.09 |  |  |  | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT2 line
05ALL | DISIS-2023-001 | ERIS | Thermal | 523266 PRINGLE 3 115 997652 ENRCO13617-1 115 1 | 27SP,27WP,27L | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | 168 | 193 | <90% | 145.55 |  |  |  | Upgrade the exsting PRINGLE6 230/115 kV Transformer
05ALL | DISIS-2023-001 | ERIS | Thermal | 523267 PRINGLE 6 230 997652 ENRCO13617-1 115 1 | 27SP,27WP,27L | 523267 PRINGLE 6 230 523979 HARRNG_EST 6 230 1 | 168 | 193 | <90% | 144.13 |  |  |  | Upgrade the exsting PRINGLE6 230/115 kV Transformer
05ALL | DISIS-2023-001 | ERIS | Thermal | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 24SP | 523961 POTTER_CO 7 345 3WXFMR WAUK 90343-A 1 | 353 | 353 | <90% | 108.36 |  |  |  | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 523823 CARPENTER 7 345 772280 G23-015-TAP 345 1 | 24SP,27SP | P42:345:OKGE:SB_DGSE7313:::: | 950 | 950 | <90% | 108.27 |  |  |  | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 523853 FINNEY 7 345 531449 HOLCOMB7 345 1 | 24SP,27SP | P42:345:OKGE:SB_DGSE7313:::: | 956.1 | 956.1 | <90% | 136.76 |  |  |  | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 523853 FINNEY 7 345 772280 G23-015-TAP 345 1 | 24SP,27SP | P42:345:OKGE:SB_DGSE7313:::: | 950 | 950 | <90% | 122.4 |  |  |  | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 523959 POTTER_CO 6 230 997634 WAUK 90343-A 230 1 | 24SP | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | 516 | 559 | <90% | 192.31 |  |  |  | XFR-Potter County 345/230 kV Ckt1 & Ckt2
05ALL | DISIS-2023-001 | ERIS | Thermal | 523961 POTTER_CO 7 345 997634 WAUK 90343-A 230 1 | 24SP | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | 516 | 559 | <90% | 191.18 |  |  |  | XFR-Potter County 345/230 kV Ckt1 & Ckt2
05ALL | DISIS-2023-001 | ERIS | Thermal | 523977 HARRNG_WST 6 230 523978 HARRNG_MID 6 230 @1 | 27WP | System-Intact | 478 | 610 | <90% | 100.99 |  |  |  | HARRING_WST6 to HARRNG_MID6 230 kV Ckt 1 Terminal Upgrade
05ALL | DISIS-2023-001 | ERIS | Thermal | 524623 DEAFSMITH 6 230 760498 G17-146-TAP 230 1 | 24SP,27SP,27WP | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | 430 | 430 | <90% | 117.12 |  |  |  | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 525454 HALE_CNTY 3 115 525828 TUCO_INT 3 115 1 | 24SP,27SP,27WP | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 96 | 106 | <90% | 109.26 |  |  |  | Rebuild the existing HALE_CNTY3 to TUCO3 115 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 24SP,27SP,27WP | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | 456 | 456 | <90% | 118.45 |  |  |  | Rebuild the existing NEWHART to PLANTX 230 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 525480 PLANT_X 3 115 997586 WH ALM20171 115 1 | 24SP,27SP,27WP | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 251 | 251 | <90% | 127.17 |  |  |  | Upgrade the existing PLANTX 230/115 kV Transformer
05ALL | DISIS-2023-001 | ERIS | Thermal | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 27WP | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | 430 | 430 | <90% | 102.36 |  |  |  | Rebuild the existing PLANTX to G17-146-TAP 230 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 525481 PLANT_X 6 230 997586 WH ALM20171 115 1 | 24SP,27SP,27WP | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 251 | 251 | <90% | 126.28 |  |  |  | Upgrade the existing PLANTX 230/115 kV Transformer
05ALL | DISIS-2023-001 | ERIS | Thermal | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 24SP,27SP,27WP | Potential P4 Event - POI 527656_0 | 478 | 478 | <90% | 172.87 |  |  |  | Build a new TOLK6 to TUCO6 230 kV line 2; Rebuild the existing TOLK6 to TUCO6 230 kV line 1
05ALL | DISIS-2023-001 | ERIS | Thermal | 525531 TOLK 6 230 997584 SAME AS YOAK 230 2 | 27WP | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | 560 | 644 | <90% | 103.43 |  |  |  | Build a new TOLK7 345/230 kV Transformer 3
05ALL | DISIS-2023-001 | ERIS | Thermal | 525531 TOLK 6 230 997585 ABBXNL844501 230 1 | 24SP,27SP,27WP | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | 478 | 553 | <90% | 121.96 |  |  |  | Build a new TOLK7 345/230 kV Transformer 3
05ALL | DISIS-2023-001 | ERIS | Thermal | 525549 TOLK 7 345 997584 SAME AS YOAK 230 2 | 27WP | 525549 TOLK 7 345 3WXFMR ABBXNL844501 1 | 560 | 644 | <90% | 104.2 |  |  |  | Build a new TOLK7 345/230 kV Transformer 3
05ALL | DISIS-2023-001 | ERIS | Thermal | 525549 TOLK 7 345 997585 ABBXNL844501 230 1 | 24SP,27SP,27WP | 525549 TOLK 7 345 3WXFMR SAME AS YOAKUM UPD 2 | 478 | 553 | <90% | 122.84 |  |  |  | Build a new TOLK7 345/230 kV Transformer 3
05ALL | DISIS-2023-001 | ERIS | Thermal | 525830 TUCO_INT 6 230 997571 UPDATE LATER 230 1 | 24SP,27SP,27WP,27L | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 675 | 675 | <90% | 209.63 |  |  |  | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
05ALL | DISIS-2023-001 | ERIS | Thermal | 525830 TUCO_INT 6 230 997572 SIEM 8743066 230 2 | 24SP,27SP,27WP,27L | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 675 | 675 | <90% | 202.95 |  |  |  | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
05ALL | DISIS-2023-001 | ERIS | Thermal | 525830 TUCO_INT 6 230 997572 UPDATE LATER 230 1 | 24SP,27SP,27WP,27L | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 675 | 675 | <90% | 209.63 |  |  |  | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
05ALL | DISIS-2023-001 | ERIS | Thermal | 525830 TUCO_INT 6 230 997573 SIEM 8743066 230 2 | 24SP,27SP,27WP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 675 | 675 | <90% | 202.95 |  |  |  | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
05ALL | DISIS-2023-001 | ERIS | Thermal | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 24SP,27SP,27WP | Potential P4 Event - POI 560022_8 | 1250 | 1250 | <90% | 196.2 |  |  |  | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1
05ALL | DISIS-2023-001 | ERIS | Thermal | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 24SP,27SP,27WP | Potential P4 Event - POI 560022_4 | 1250 | 1250 | <90% | 196.88 |  |  |  | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2; Build a new TUCO7 to CRAWFISH 345 kV line 3
05ALL | DISIS-2023-001 | ERIS | Thermal | 525832 TUCO_INT 7 345 997571 UPDATE LATER 230 1 | 24SP,27SP,27WP,27L | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 675 | 675 | <90% | 209.63 |  |  |  | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
05ALL | DISIS-2023-001 | ERIS | Thermal | 525832 TUCO_INT 7 345 997572 SIEM 8743066 230 2 | 24SP,27SP,27WP,27L | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 675 | 675 | <90% | 202.95 |  |  |  | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
05ALL | DISIS-2023-001 | ERIS | Thermal | 525832 TUCO_INT 7 345 997572 UPDATE LATER 230 1 | 24SP,27SP,27WP,27L | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 675 | 675 | <90% | 210.55 |  |  |  | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
05ALL | DISIS-2023-001 | ERIS | Thermal | 525832 TUCO_INT 7 345 997573 SIEM 8743066 230 2 | 24SP,27SP,27WP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 675 | 675 | <90% | 203.74 |  |  |  | Upgrade the existing TUCO7 345/230 kV Transformer 1; Build a new TUCO7 345/230 kV Transformer 3; Build a new TUCO7 345/230 kV Transformer 4
05ALL | DISIS-2023-001 | ERIS | Thermal | 526435 SUNDOWN 6 230 526525 WOLFFORTH 6 230 1 | 24SP,27SP | P43:345:SPS:TUCO:NR50_SLG::EHV: | 426 | 426 | <90% | 121.3 |  |  |  | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line
05ALL | DISIS-2023-001 | ERIS | Thermal | 528413 TAYLOR 3 115 528449 W_BENDER 3 115 1 | 24SP,27SP,27WP | 528355 MADDOX 3 115 762442 G18-004-TAP 115 1 | 143 | 157 | <90% | 136.32 |  |  |  | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line
05ALL | DISIS-2023-001 | ERIS | Voltage | ABBK 3 | 24SP,27SP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8912 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | ARNOLD3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8699 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | ASGI_12_06 | 24SP,27SP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8912 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | BEELER 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.868 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | BIRDCTY3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8786 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | BVERVLLY | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8962 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | CHASE 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8259 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | CNTRLPL3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8884 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | CSTFRAN3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8638 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | DIGHTON3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8814 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | ELLIS 2 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.859 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | GANO 3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8772 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | GODLNDT3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8728 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | GOODCTY3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8686 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | GOODLND3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8749 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | GOVE 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8875 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | GRANT 3 | 24SP,27SP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8767 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | GRANTTP3 | 24SP,27SP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.877 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | HUGOTON3 | 24SP,27SP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8896 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | JAGGER 3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8821 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | KANARAD3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8253 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | LAWNRID3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.853 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | LEOTI 3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8773 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | LIBERTY3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.871 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | LIBERTYT | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8756 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | MANNGT 3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8794 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | MANNING3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8783 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | MCDONLD3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8918 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | NESCTY 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.869 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | NESSCTY3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8689 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | None | 27L, 27WP | None | [7 empty] | None
05ALL | DISIS-2023-001 | ERIS | Voltage | NSI | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.834 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | NSI TAP3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8349 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | ONEOK 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8952 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | PALMER3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8667 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | PILE 3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.866 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | RANSOM 2 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8659 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | RANSOM 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8684 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | ROLLA 3 | 24SP,27SP | P23:345:SUNC:HLC_BRK188:::EHV: |  |  |  |  | 0.8894 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | RULETON3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8478 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | SCOTCTY3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8794 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | SELKIRK3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8748 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | SETAB 3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8899 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | SHARNSP3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.826 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | STFRAN 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8665 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | STFRANT3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.864 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | SYRACUS3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8921 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | TRIB SW3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8702 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | TRIBUNE3 | 24SP,27SP | Potential P4 Event - POI 531465_1 |  |  |  |  | 0.8699 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | WTCLF 3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8142 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05ALL | DISIS-2023-001 | ERIS | Voltage | WTCLFTP3 | 24SP,27SP | 531451 MINGO 7 345 531465 SETAB 7 345 1 |  |  |  |  | 0.8154 | 0.9 | 1.05 | Build a new 36 MVAR cap bank at SHARNSP3 115 kV; Line - Holcomb - Sidney 345 kV Ckt 1 New Line; Build a new FINNEY7 to HOLCOMB7 345 kV line 2
05NR | DISIS-2023-001 | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
05NR | DISIS-2023-001 | NRIS | Thermal | None | 27L | None |  |  | <90% |  |  |  |  | None
05NR | DISIS-2023-001 | NRIS | Voltage | None | 27L | None | [7 empty] | None
00NR | DISIS-2023-001 | NRIS | Non-Converged | None | 24SP, 27SP, 27WP | None | [7 empty] | None
00NR | DISIS-2023-001 | NRIS | Thermal | 508284 ADORA 2 69.0 508285 ADORA T2 69.0 1 |  | P12:138:AEPW:CAMPCOR4:PITTSB_4::: | 76 | 76 | <90% | 107.46 |  |  |  | ADORA2 to ADORAT2 Ckt 1 Rating Update
00NR | DISIS-2023-001 | NRIS | Thermal | 512635 KERR GR5 161 512648 MAID 5 161 1 | 24SP | P12:161:GRDA:KERR GR5-MAID-2 5:::HV: | 198 | 198 | <90% | 122.61 |  |  |  | Kerr - Maid 161 kV Ckt 1 Rebuild #2
00NR | DISIS-2023-001 | NRIS | Thermal | 512635 KERR GR5 161 512648 MAID 5 161 2 | 24SP | P12:161:GRDA:KERR GR5-MAID 5-1:::HV: | 198 | 198 | <90% | 122.58 |  |  |  | Kerr - Maid 161 kV Ckt 2 Rebuild
00NR | DISIS-2023-001 | NRIS | Thermal | 515073 ERLSBOR2 69.0 515074 FRSTHIL2 69.0 1 | 24SP,27SP | P12:138:OKGE:BKRBKR224:::: | 39 | 48 | <90% | 119.24 |  |  |  | Rebuild the existing ERLSBOR2 to FRSTHIL2 69 kV line
00NR | DISIS-2023-001 | NRIS | Thermal | 515152 BROWNTP4 138 515944 STRRDTP4 138 1 | 24SP,27SP | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | 133 | 153 | <90% | 106.22 |  |  |  | Brown Substation Expansion
00NR | DISIS-2023-001 | NRIS | Thermal | 515157 BROWN 4 138 515944 STRRDTP4 138 1 | 24SP,27SP | 505602 S BROWN4 138 515159 COLBRTP4 138 1 | 133 | 153 | <90% | 110.81 |  |  |  | Brown Substation Expansion
00NR | DISIS-2023-001 | NRIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | Potential P4 Event - POI 514801_4 | 200 | 234 | <90% | 117.58 |  |  |  | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3
00NR | DISIS-2023-001 | NRIS | Thermal | 541264 LEX69 2 69.0 541232 LEX161 5 161 1 | 27SP,27WP | 541229 ODESSA 5 161 772620 G23-032-TAP 161 1 | 50 | 55 | <90% | 105.29 |  |  |  | Upgrade the existing LEX161 5 161/69 kV Transformer
00NR | DISIS-2023-001 | NRIS | Thermal | 547469 RIV4525 161 547498 STL439 5 161 1 | 24SP,27SP,27WP | 547467 ORO110 5 161 547469 RIV4525 161 1 | 463 | 481 | <90% | 108.68 |  |  |  | Rebuild the existing RIV4525 to STL439_5 161 kV line
00NR | DISIS-2023-001 | NRIS | Thermal | 547525 JOP 59 2 69.0 547541 RIV167 2 69.0 1 | 27SP,27WP | 547469 RIV4525 161 547498 STL439 5 161 1 | 72 | 72 | <90% | 113.03 |  |  |  | Rebuild the existing JOP 59 2 to RIV167 2 69 kV line
00NR | DISIS-2023-001 | NRIS | Thermal | 640227 HOSKINS4 230 996833 HOSKINS T1 115 1 | 27SP,27WP | P13:115-345:NPPD:NUCOR-2 | 187 | 187 | 97.53 | 113.5 |  |  |  | Upgrade existing HOSKINS T1 230/115 kV Transformer
00NR | DISIS-2023-001 | NRIS | Thermal | 640227 HOSKINS4 230 996836 HOSKINS T1 115 1 | 24SP | P13:115-345:NPPD:NUCOR-2 | 187 | 187 | 97.55 | 112.21 |  |  |  | Upgrade existing HOSKINS T1 230/115 kV Transformer
00NR | DISIS-2023-001 | NRIS | Thermal | 640228 HOSKINS7 115 996833 HOSKINS T1 115 1 | 27SP,27WP | P13:115-345:NPPD:NUCOR-2 | 187 | 187 | 97.53 | 112.83 |  |  |  | Upgrade existing HOSKINS T1 230/115 kV Transformer
00NR | DISIS-2023-001 | NRIS | Thermal | 640228 HOSKINS7 115 996836 HOSKINS T1 115 1 | 24SP | P13:115-345:NPPD:NUCOR-2 | 187 | 187 | 97.55 | 111.12 |  |  |  | Upgrade existing HOSKINS T1 230/115 kV Transformer
00NR | DISIS-2023-001 | NRIS | Thermal | 652296 WARD 4 230 652426 BISMARK4 230 1 | 27WP | Potential P4 Event - POI 620358_1 | 320 | 352 | 105.9 | 107.06 |  |  |  | WARD4 to BISMARK4 230 kV Ckt 1 Terminal Upgrade
00NR | DISIS-2023-001 | NRIS | Voltage | None | 24SP, 27SP, 27WP | None | [7 empty] | None
01ALL | DISIS-2023-001 | ERIS | Stability | None | 25SP, 25WP | None | [7 empty] | None
02ALL | DISIS-2023-001 | ERIS | Stability | High power export from Group 02 to Group 03 after case dispatch is causing a low voltage profile at the receiving terminals of Group 03. This issue causes non-convergence of the case in 25WP under system intact conditions. | 25SP, 25WP | GROUP2_P0 | [7 empty] | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
02ALL | DISIS-2023-001 | ERIS | Stability | High power export from Group 02 to Group 03 after case dispatch is causing a low voltage profile at the receiving terminals of Group 03. This issue causes non-convergence of the case in 25WP under system intact conditions. | 25SP, 25WP | GROUP2_P0 | [7 empty] | Line - Elm Creek 345 kV - Tobias 345 kV New Line
02ALL | DISIS-2023-001 | ERIS | Stability | Low voltage profile observed at the ELMCREEK7 (539805), ELMCREK6 (539639), and other nearby buses. | 25SP, 25WP | GROUP2_P0 | [7 empty] | Build new ELMCREEK7 345kV Capbank
02ALL | DISIS-2023-001 | ERIS | Stability | Low voltage profile observed at the MARSHAL3 (533303), SENECA 3 (533337), and other nearby buses. | 25SP, 25WP | GROUP2_P0 | [7 empty] | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1
02ALL | DISIS-2023-001 | ERIS | Stability | Unstable power response with failed voltage recovery was observed at GEN-2023-222, GEN-2023-223, BPS, and other nearby units. | 25SP, 25WP | GROUP2_P1_LOCAL_FAULT_603 | [7 empty] | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00ALL | DISIS-2023-001 CF | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 24SP,27SP,27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: | 905 | 1059 | <90% | 109.12 |  |  |  | WELSH 7 to WILKES 7 345kV Line Rebuild
00ALL | DISIS-2023-001 CF | ERIS | Thermal | 508359 WELSH 7 345 776060 G23-204-TAP 345 1 | 24SP,27SP | Potential P4 Event - POI 508298_0 | 905 | 1059 | <90% | 101.45 |  |  |  | LYDIA7 to WELSH Line Rebuild
00ALL | DISIS-2023-001 CF | ERIS | Thermal | 640088 BPS SUB7 115 996910 BPS_345_115 115 1 | 27SP,27WP | Potential P4 Event - POI 640590_0 | 417 | 417 | <90% | 119.4 |  |  |  | Multi - Sheldon - Monolith 115 kV
00ALL | DISIS-2023-001 CF | ERIS | Thermal | 640088 BPS SUB7 115 996912 BPS_345_115 115 1 | 24SP | Potential P4 Event - POI 640590_0 | 417 | 417 | <90% | 115.65 |  |  |  | Multi - Sheldon - Monolith 115 kV
00ALL | DISIS-2023-001 CF | ERIS | Thermal | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 24SP,27SP,27WP | Potential P4 Event - POI 640525_3 | 956 | 956 | <90% | 111.08 |  |  |  | Multi - Sheldon - Monolith 115 kV
00ALL | DISIS-2023-001 CF | ERIS | Thermal | 771999 G23-222-POI 345 996910 BPS_345_115 115 1 | 27SP,27WP | Potential P4 Event - POI 640590_0 | 417 | 417 | <90% | 118.77 |  |  |  | Multi - Sheldon - Monolith 115 kV
00ALL | DISIS-2023-001 CF | ERIS | Thermal | 771999 G23-222-POI 345 996912 BPS_345_115 115 1 | 24SP | Potential P4 Event - POI 640590_0 | 417 | 417 | <90% | 113.68 |  |  |  | Multi - Sheldon - Monolith 115 kV
01ALL | DISIS-2023-001 CF | ERIS | Non-Converged | Non-Converged | 24SP, 27L, 27SP, 27WP | 652806 FTTHOM1-LNX3 345 659130 CHAPELLE-BE3 345 1 | [7 empty] | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
01ALL | DISIS-2023-001 CF | ERIS | Non-Converged | Non-Converged | 24SP, 27L, 27SP, 27WP | P21:345:UMZW:# 2409 #:: FT2 IN SD. FT2-FT21LNX3 OPENED:EHV: | [7 empty] | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
01ALL | DISIS-2023-001 CF | ERIS | Non-Converged | Non-Converged | 24SP, 27L, 27SP, 27WP | P21:345:UMZW:# 323 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | [7 empty] | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 24SP, 27L, 27SP, 27WP | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | 720 | 720 | 125.51 | 118.65 |  |  |  | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 652506 FTTHOMP3 345 996589 FT2 KU1B 230 1 | 27L, 27SP | POI 652532_1 | 250 | 313 | 97.94 | 126.55 |  |  |  | Build Third Ft Thompson 345-230 kV Transformer
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 652506 FTTHOMP3 345 996590 FT2 KU1A 230 1 | 27L, 27SP | POI 652532_1 | 250 | 313 | 100.06 | 129.29 |  |  |  | Build Third Ft Thompson 345-230 kV Transformer
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 652506 FTTHOMP3 345 996592 FT2 KU1B 230 1 | 24SP | POI 652532_1 | 250 | 313 | <90% | 115.19 |  |  |  | Build Third Ft Thompson 345-230 kV Transformer
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 652506 FTTHOMP3 345 996593 FT2 KU1A 230 1 | 24SP | POI 652532_1 | 250 | 313 | <90% | 117.68 |  |  |  | Build Third Ft Thompson 345-230 kV Transformer
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 652507 FTTHOMP4 230 996589 FT2 KU1B 230 1 | 27L, 27SP | POI 652532_1 | 250 | 313 | 96.92 | 124.96 |  |  |  | Build Third Ft Thompson 345-230 kV Transformer
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 652507 FTTHOMP4 230 996590 FT2 KU1A 230 1 | 27L, 27SP | POI 652532_1 | 250 | 313 | 99.02 | 127.67 |  |  |  | Build Third Ft Thompson 345-230 kV Transformer
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 652507 FTTHOMP4 230 996592 FT2 KU1B 230 1 | 24SP | POI 652532_1 | 250 | 313 | <90% | 113.63 |  |  |  | Build Third Ft Thompson 345-230 kV Transformer
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 652507 FTTHOMP4 230 996593 FT2 KU1A 230 1 | 24SP | POI 652532_1 | 250 | 313 | <90% | 116.09 |  |  |  | Build Third Ft Thompson 345-230 kV Transformer
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 24SP, 27L, 27SP, 27WP | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | 717 | 717 | 124.06 | 117.49 |  |  |  | Cherry Co. - Gentleman 345 kV Ckt 1
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 24SP, 27L, 27SP, 27WP | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | 717 | 717 | 124.06 | 117.49 |  |  |  | Cherry Co. - Holt Co. 345 kV Ckt 1
01ALL | DISIS-2023-001 CF | ERIS | Thermal | 653571 GR ISLD3 345 653871 GR ISLD-LNX3 345 Z | 24SP, 27L, 27SP, 27WP | 640520 ANTELOPE 3 345 652532 GR PRAIRIE 3 345 1 | 717 | 717 | 124.06 | 117.49 |  |  |  | Holt Co. Substation 345 kV
01ALL | DISIS-2023-001 CF | ERIS | Voltage | None | 24SP, 27L, 27SP, 27WP | None | [7 empty] | None
01NR | DISIS-2023-001 CF | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
01NR | DISIS-2023-001 CF | NRIS | Thermal | None | 27L | None | [7 empty] | None
01NR | DISIS-2023-001 CF | NRIS | Voltage | None | 27L | None | [7 empty] | None
01ALL | DISIS-2023-001 CF | ERIS | Stability | The loss of the path from FTTHOMP3 (652506) to CHAPELLE-BE3 (659130) causes TRPLHH1W (659437) and TRPLHH2W (659441) to trip. When protection is disabled, instability is evident. | 25SP, 25WP | GROUP1_P1_LOCAL_FAULT_118 | [7 empty] | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1
02ALL | DISIS-2023-001 CF | ERIS | Stability | Unstable power response with failed voltage recovery was observed at COOPER1G (640009), WSEC3G (635023), WSEC4G (635024), and other nearby units. | 25SP, 25WP | GROUP2_P1_LOCAL_FAULT_128 | [7 empty] | Multi - Sheldon - Monolith 115 kV
02ALL | DISIS-2023-001 CF | ERIS | Thermal | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 27WP | 635200 RAUN 3 345 640999 E.HOSKINS3 345 1 | 460 | 320 | <90% | 106.03 |  |  |  | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1
02ALL | DISIS-2023-001 CF | ERIS | Thermal | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 24SP, 27SP | System Intact | 956 | 956 | <90% | 106.81 |  |  |  | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
02ALL | DISIS-2023-001 CF | ERIS | Thermal | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 24SP, 27L, 27SP, 27WP | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 956 | 956 | 98.12 | 124.65 |  |  |  | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
02NR | DISIS-2023-001 CF | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
02NR | DISIS-2023-001 CF | NRIS | Thermal | None | 27L | None | [7 empty] | None
02NR | DISIS-2023-001 CF | NRIS | Voltage | None | 27L | None | [7 empty] | None
03ALL | DISIS-2023-001 CF | ERIS | Non-Converged | Non-Converged | 24SP, 27L, 27SP, 27WP | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | [7 empty] | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
03ALL | DISIS-2023-001 CF | ERIS | Stability | Unstable behavior, machine tripping, voltage violations | 25SP, 25WP | G3_FLT2558-3PH | [7 empty] | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1
03ALL | DISIS-2023-001 CF | ERIS | Stability | Unstable behavior, machine tripping, voltage violations | 25SP, 25WP | G3_FLT1854-3PH | [7 empty] | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
03ALL | DISIS-2023-001 CF | ERIS | Thermal | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 27WP | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | 956 | 956 | 83 | 113.76 |  |  |  | Neosho 345 kV Terminal Upgrade
03ALL | DISIS-2023-001 CF | ERIS | Thermal | 505486 NEO SPA5 161 547472 TIP292 5 161 1 | 24SP, 27SP | System Intact | 222 | 222 | 95.29 | 103.99 |  |  |  | Rebuild the NEO SPA5 to TIP292 5 161kV Line 1 (EMDE)
03ALL | DISIS-2023-001 CF | ERIS | Thermal | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 24SP, 27SP, 27WP | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | 717 | 717 | 125.32 | 138.21 |  |  |  | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
03ALL | DISIS-2023-001 CF | ERIS | Thermal | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 24SP, 27SP | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | 717 | 717 | 102.94 | 121.21 |  |  |  | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
03ALL | DISIS-2023-001 CF | ERIS | Thermal | 541207 ARCHIE 5 161 541239 HSNVL 5 161 1 | 27SP | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 223 | 223 | 57.24 | 101.63 |  |  |  | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade
03ALL | DISIS-2023-001 CF | ERIS | Thermal | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 24SP, 27SP, 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 2 | 583 | 607 | 74.18 | 118.69 |  |  |  | Build new NEOSHO 5 to RIV4525 161kV Line 2
03ALL | DISIS-2023-001 CF | ERIS | Thermal | 547469 RIV4525 161 764310 G20-079-TAP 161 2 | 24SP, 27SP, 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 583 | 607 | 74.24 | 118.78 |  |  |  | Build new NEOSHO 5 to RIV4525 161kV Line 2
03ALL | DISIS-2023-001 CF | ERIS | Voltage | 523823 CARPENTER 7 345 | 27SP, 27WP | POI 531449_3 |  |  |  |  | 0.9 | 1.05 | 0.8676 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
03ALL | DISIS-2023-001 CF | ERIS | Voltage | 531405 WALKMYR3 115 | 27WP | POI 531449_3 |  |  |  |  | 0.9 | 1.05 | 0.8905 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
03ALL | DISIS-2023-001 CF | ERIS | Voltage | 531481 HUGOTON3 115 | 27WP | POI 531449_3 |  |  |  |  | 0.9 | 1.05 | 0.8999 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
03ALL | DISIS-2023-001 CF | ERIS | Voltage | 531510 HARBNGR3 115 | 27WP | POI 531449_3 |  |  |  |  | 0.9 | 1.05 | 0.8866 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
03ALL | DISIS-2023-001 CF | ERIS | Voltage | 531512 HARBNGR7 345 | 27SP, 27WP | POI 531449_3 |  |  |  |  | 0.9 | 1.05 | 0.8677 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
03ALL | DISIS-2023-001 CF | ERIS | Voltage | 764980 GEN-2020-008 345 | 27SP, 27WP | POI 531449_3 |  |  |  |  | 0.9 | 1.05 | 0.8676 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
03ALL | DISIS-2023-001 CF | ERIS | Voltage | 765490 GEN-2021-021 345 | 27SP, 27WP | POI 531449_3 |  |  |  |  | 0.9 | 1.05 | 0.8677 | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV
03NR | DISIS-2023-001 CF | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
03NR | DISIS-2023-001 CF | NRIS | Thermal | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 27L | 300042 7HUBEN 345 300045 7MORGAN 345 1 | 167 | 167 | 57.86 | 115.33 |  |  |  | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1
03NR | DISIS-2023-001 CF | NRIS | Voltage | None | 27L | None | [7 empty] | None
04ALL | DISIS-2023-001 CF | ERIS | Non-Converged | None | 27L | None | [7 empty] | None
04ALL | DISIS-2023-001 CF | ERIS | Stability | System Intact non-convergence, Flatline Issues | 25SP, 25WP | System Intact | [7 empty] | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1; Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Stability | Fault Crashing Issues | 25SP, 25WP | P1_511468_LES-7-766291_G20-009-TAP_Ckt1 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 338875 3PATMOS.W# 115 503912 FULTON 3 115 1 | 24SP,27SP,27WP | Potential P4 Event - POI 508809_1 | 157 | 157 | <90% | 112.51 |  |  |  | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 24SP,27SP,27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: | 905 | 1059 | <90% | 108.31 |  |  |  | WELSH 7 to WILKES 7 345kV Line Rebuild
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 509790 CATOOSA4 138 512636 CATSAGR4 138 Z1 | 27WP,27L | 509852 T.NO.--7 345 765721 G21-047-TAP 345 1 | 150 | 188 | 174.33 | 150.9 |  |  |  | Catoosa Terminal Upgrade
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 510948 EARLSBORO 4 138 515055 MAUD 4 138 1 | 27WP,27L | 510902 WELETK4 138 774660 G23-134-TAP 138 1 | 143 | 143 | 112.63 | 113.16 |  |  |  | Maud Tap 138 kV Terminal Upgrade
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 27SP | P42:345:OKGE:SB_CION7384:::: | 191 | 191 | <90% | 107.13 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 136 | 136 | <90% | 114.93 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 212 | 212 | <90% | 116.24 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 136 | 136 | 96.28 | 133.71 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 27SP | P42:345:OKGE:SB_CION7384:::: | 209 | 212 | <90% | 105.06 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 24SP,27SP,27WP | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 353 | 353 | 92.74 | 134.17 |  |  |  | Sweetwater to Chisholm 230 kV Line Rebuild
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 512631 MIAMI 5 161 547487 HOC404 5 161 1 | 24SP,27SP,27WP | 510417 VINTAJC4 138 547486 HOC404 4 138 1 | 360 | 167 | <90% | 167.18 |  |  |  | MIAMI to HOC404 5 161kV Line Rebuild
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 27SP | Potential P4 Event - POI 511468_23 | 1195 | 1195 | <90% | 100.81 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 514868 DOUGLTP4 138 514922 CLASSEN4 138 1 | 24SP,27SP,27WP | 514861 MUSTANG4 138 514865 COUNCIL4 138 1 | 268 | 287 | 103.69 | 116.06 |  |  |  | Multi - West Oaks - Council - Classen 138 kV Reconductor
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 515073 ERLSBOR2 69.0 515074 FRSTHIL2 69.0 1 | 27SP | P12:138:OKGE:BKRBKR224:::: | 39 | 48 | <90% | 106.64 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | P42:345:OKGE:SB_GRNT7313:::: | 200 | 234 | <90% | 108.77 |  |  |  | Gracemont to Minco 345 kV New Line
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 27SP | P42:345:OKGE:SB_GRNT7313:::: | 145 | 169 | <90% | 116.6 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 24SP,27SP | P42:345:OKGE:SB_GRNT7313:::: | 145 | 169 | <90% | 120.3 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 24SP | P42:345:OKGE:SB_CION7384:::: | 145 | 169 | <90% | 102.47 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 29 | 35 | <90% | 137.05 |  |  |  | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 29 | 35 | <90% | 136.75 |  |  |  | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 27SP | P42:345:OKGE:SB_GRNT7313:::: | 145 | 169 | <90% | 113.14 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 27SP | P42:345:OKGE:SB_CION7384:::: | 200 | 234 | <90% | 104.06 |  |  |  | Multi - Park Community - Sunshine 138 kV
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 200 | 234 | <90% | 111.71 |  |  |  | Multi - Park Community - Sunshine 138 kV
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 24SP,27SP,27WP | System Intact | 58 | 68 | <90% | 327.54 |  |  |  | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520810 ANADARK2 69.0 520838 CADDO 2 69.0 1 | 24SP,27SP | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | 58 | 68 | <90% | 111.38 |  |  |  | Multi - Park Community - Sunshine 138 kV
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 520838 CADDO 2 69.0 521088 WASHITA2 69.0 1 | 24SP,27SP,27WP | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | 58 | 68 | <90% | 107.01 |  |  |  | Multi - Park Community - Sunshine 138 kV
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 521022 PAOLI 2 69.0 997686 PAOLI 69.0 1 | 27WP | P12:138:WFEC:LOCO_PAOLI:::: | 70 | 70 | <90% | 101.49 |  |  |  | Canadian Switch138 kV Terminal Upgrades Lexington - Lil Axe 138 kV Paoli - Lexington kV 138 kV Paoli 138 kV Terminal Upgrades
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 521023 PAOLI 4 138 997686 PAOLI 69.0 1 | 27WP | P12:138:WFEC:LOCO_PAOLI:::: | 70 | 70 | <90% | 101.03 |  |  |  | Canadian Switch138 kV Terminal Upgrades Lexington - Lil Axe 138 kV Paoli - Lexington kV 138 kV Paoli 138 kV Terminal Upgrades
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 200 | 234 | <90% | 117.68 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 523701 MCCULLOUGH 2 69.0 523747 BOWERS 2 69.0 1 |  | 523771 GRAPEVINE 6 230 524044 NICHOLS 6 230 1 | 88 | 88 | 98.12 | 101.8 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 24SP,27SP,27WP | Potential P4 Event - POI 515554_14 | 487 | 487 | 108.74 | 122.36 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); G17-151-Tap to G18-015-Tap 345 kV New Line; Build New Beckham to Potter 345 kV Line Ckt 2
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 24SP,27SP,27WP,27L | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | 353 | 353 | 135.74 | 110.25 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | 24SP,27SP | 300739 7BLACKBERRY 345 300740 7SPORTSMAN 345 1 | 956 | 956 | <90% | 107.95 |  |  |  | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 547469 RIV4525 161 547729 BAX488 5 161 1 | 24SP,27SP,27WP | Potential P4 Event - POI 532793_18 | 279 | 279 | <90% | 119.57 |  |  |  | RIV4525 to BAX488 5 161kV Line Rebuild
04ALL | DISIS-2023-001 CF | ERIS | Thermal | 547487 HOC404 5 161 547729 BAX488 5 161 1 | 24SP,27SP,27WP | Potential P4 Event - POI 532793_18 | 290 | 290 | <90% | 119.49 |  |  |  | HOC404 5 to BAX488 5 161kV Line Rebuild
04NR | DISIS-2023-001 CF | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
04NR | DISIS-2023-001 CF | NRIS | Thermal | None | 27L | None | [7 empty] | None
04NR | DISIS-2023-001 CF | NRIS | Voltage | None | 27L | None | [7 empty] | None
05ALL | DISIS-2023-001 CF | ERIS | Non-Converged | Non-Converged | 24SP, 27SP, 27WP | 523966 POTTER_CO 9 765 527669 CROSSROADS 9 765 1 | [7 empty] | Build New Crossroads to Potter County 345 kV Line
05ALL | DISIS-2023-001 CF | ERIS | Non-Converged | Non-Converged | 24SP, 27SP, 27WP | System Intact | [7 empty] | Build the Crawfish Draw 345 kV Substation; Woodward EHV to Beckham 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Stability | System Intact non-convergence, Flatline Issues | 25SP, 25WP | System Intact | [7 empty] | Build the Crawfish Draw 345 kV Substation; G17-151-Tap to G18-015-Tap 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line; Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2; Build New Hitchland to Potter 345 kV Line Ckt 2; Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line; Lawton Eastside to G20-009-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2; Woodward EHV to Beckham 345 kV New Line; Hobbs to Andrews Voltage Conversion;
05ALL | DISIS-2023-001 CF | ERIS | Stability | Fault Crashing Issues | 25SP, 25WP | P1_516059_BECKHAM7-515458_BORDER_Ckt1 | [7 empty] | Border to Beckham 345 kV New Line; Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2; Build New G17-151-Tap to Border 345 kV Line; Build New Beckham to Potter 345 kV Line Ckt 2; Build New Crossroads to Potter County 345 kV Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 510907 PITTSB-7 345 515045 SEMINOL7 345 1 | 27WP | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | 1135 | 1135 | <90% | 104.83 |  |  |  | Lawton Eastside to Draper 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 511458 ELKCTY-4 138 997923 ELKCTY-6 138 1 | 27SP,27WP | Potential P4 Event - POI 560078_0 | 510 | 510 | <90% | 132.23 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 511458 ELKCTY-4 138 997924 ELKCTY-6 138 1 | 24SP | Potential P4 Event - POI 515800_3 | 510 | 510 | <90% | 136.26 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 511490 ELKCITY6 230 511557 CHISHOLM6 230 1 | 24SP,27SP,27WP | Potential P4 Event - POI 515800_3 | 501 | 501 | <90% | 144.75 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 511490 ELKCITY6 230 997923 ELKCTY-6 138 1 | 27SP,27WP | Potential P4 Event - POI 560078_0 | 510 | 510 | <90% | 132.65 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 511490 ELKCITY6 230 997924 ELKCTY-6 138 1 | 24SP | Potential P4 Event - POI 515800_3 | 510 | 510 | <90% | 136.91 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP); Gracemont to Treasure Island 345 kV New Line; Gracemont to G16-037-Tap 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 24SP,27SP,27WP | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | 353 | 353 | <90% | 154.62 |  |  |  | Sweetwater to Chisholm 230 kV Line Rebuild
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 24SP,27SP,27WP | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | 349 | 395 | <90% | 126.95 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 514934 DRAPER 7 345 515045 SEMINOL7 345 2 | 24SP,27SP | P42:345:OKGE:SB_SEOL7385:::: | 717 | 717 | <90% | 112.25 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Gracemont to Minco 345 kV New Line; Lawton Eastside to G20-009-TAP 345kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 515045 SEMINOL7 345 560101 SEMINOLE765 765 1 | 24SP,27SP,27WP | 515045 SEMINOL7 345 560101 SEMINOLE765 765 2 | 2768 | 2768 | <90% | 101.94 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 515045 SEMINOL7 345 560101 SEMINOLE765 765 2 | 24SP,27SP,27WP | 515045 SEMINOL7 345 560101 SEMINOLE765 765 1 | 2768 | 2768 | <90% | 101.94 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 515800 GRACMNT7 345 997727 GRACMNT3 138 3 | 24SP | P42:345:OKGE:SB_GRNT7313:::: | 478 | 478 | <90% | 125.33 |  |  |  | Gracemont to Minco 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 27SP,27WP | P42:345:OKGE:SB_GRNT7313:::: | 478 | 478 | <90% | 127.36 |  |  |  | Gracemont to Minco 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | P42:345:OKGE:SB_GRNT7313:::: | 200 | 234 | <90% | 175.85 |  |  |  | Gracemont to Minco 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 515802 GRACMNT4 138 997727 GRACMNT3 138 3 | 24SP | P42:345:OKGE:SB_GRNT7313:::: | 478 | 478 | <90% | 128.84 |  |  |  | Gracemont to Minco 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 27SP,27WP | P42:345:OKGE:SB_GRNT7313:::: | 478 | 478 | <90% | 130.92 |  |  |  | Gracemont to Minco 345 kV New Line
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 523097 HITCHLAND 7 345 523823 CARPENTER 7 345 1 | 24SP,27SP,27WP | P42:345:OKGE:SB_BAER7314:::: | 1098 | 1098 | <90% | 112.52 |  |  |  | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 523177 RB-SPURLCK+3 115 523308 MOORE_E 3 115 1 |  | 523095 HITCHLAND 6 230 523309 MOORE_CNTY 6 230 1 | 80 | 80 | <90% | 113 |  |  |  | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 1 | 24SP,27SP | P12:115:SPS:T08_2_SPRMN_PRNGLE:::: | 196 | 196 | <90% | 113.76 |  |  |  | Build New Hitchland to Potter 345 kV Line Ckt 2
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 523186 SPEARMAN 3 115 523266 PRINGLE 3 115 2 | 24SP,27SP | P12:115:SPS:T06_1_SPRMN_PRNGLE:::: | 184 | 184 | <90% | 116.78 |  |  |  | Build New Hitchland to Potter 345 kV Line Ckt 2
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 523777 WHEELER 6 230 774000 G23-101-TAP 230 1 | 24SP,27SP,27WP | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | 353 | 353 | <90% | 124.26 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 523779 STLN-DEMARC6 230 774000 G23-101-TAP 230 1 | 24SP,27SP,27WP,27L | 106 CHISHOLM_9 765 523966 POTTER_CO 9 765 1 | 385 | 385 | <90% | 129.28 |  |  |  | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP)
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 24SP,27SP,27WP | 525531 TOLK 6 230 525830 TUCO_INT 6 230 2 | 840 | 840 | <90% | 104.14 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525531 TOLK 6 230 525830 TUCO_INT 6 230 2 | 27WP | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 840 | 840 | <90% | 104.14 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525830 TUCO_INT 6 230 997569 UPDATE LATER 230 1 | 27SP,27WP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 559 | 559 | <90% | 134.76 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525830 TUCO_INT 6 230 997570 SIEM 8743066 230 4 | 27WP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 675 | 675 | <90% | 101.53 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525830 TUCO_INT 6 230 997570 UPDATE LATER 230 1 | 24SP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 559 | 559 | <90% | 118.23 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525830 TUCO_INT 6 230 997571 SIEM 8743066 230 3 | 27WP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 675 | 675 | <90% | 101.53 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525830 TUCO_INT 6 230 997572 SIEM 8743066 230 2 | 27WP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 559 | 643 | <90% | 106.59 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 1 | 24SP,27SP,27WP | Potential P4 Event - POI 560022_8 | 1385 | 1385 | <90% | 102.96 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525832 TUCO_INT 7 345 560022 CRAWFISH_DR 345 2 | 24SP,27SP,27WP | Potential P4 Event - POI 560022_4 | 1385 | 1385 | <90% | 102.85 |  |  |  | Build New Beckham to Potter 345 kV Line Ckt 2
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525832 TUCO_INT 7 345 997569 UPDATE LATER 230 1 | 27SP,27WP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 559 | 559 | <90% | 133.51 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525832 TUCO_INT 7 345 997570 SIEM 8743066 230 4 | 27WP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 675 | 675 | <90% | 100.57 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525832 TUCO_INT 7 345 997570 UPDATE LATER 230 1 | 24SP | 525832 TUCO_INT 7 345 3WXFMR SIEM 8743066 2 | 559 | 559 | <90% | 116.7 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525832 TUCO_INT 7 345 997571 SIEM 8743066 230 3 | 27WP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 675 | 675 | <90% | 100.57 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 525832 TUCO_INT 7 345 997572 SIEM 8743066 230 2 | 27WP | 525832 TUCO_INT 7 345 3WXFMR UPDATE LATER _11 1 | 559 | 643 | <90% | 105.57 |  |  |  | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | 24SP,27SP,27WP | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | 2768 | 2768 | <90% | 101.98 |  |  |  | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
05ALL | DISIS-2023-001 CF | ERIS | Thermal | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 2 | 24SP,27SP,27WP | 560022 CRAWFISH_DR 345 560100 CRAWFISH765 765 1 | 2768 | 2768 | <90% | 101.98 |  |  |  | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2
05NR | DISIS-2023-001 CF | NRIS | Non-Converged | None | 27L | None | [7 empty] | None
05NR | DISIS-2023-001 CF | NRIS | Thermal | None | 27L | None | [7 empty] | None
05NR | DISIS-2023-001 CF | NRIS | Voltage | None | 27L | None | [7 empty] | None
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | 511456 O.K.U.-7 345 767200 G22-011-TAP 345 1 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | 511468 L.E.S.-7 345 766291 G20-009-TAP 345 1 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | 525531 TOLK 6 230 525586 NEEDMORE 6 230 1 | [7 empty] | Build new Tolk to Needmore 230 kV Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | [7 empty] | G17-151-Tap to G18-015-Tap 345 kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | 533304 LANG 3 115 767120 G22-007-TAP 115 1 | [7 empty] | Build 2nd LANG 3 to G22-007-TAP 115 kV Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 27WP | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | [7 empty] | Multi - Sheldon - Monolith 115 kV
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | 762216 G17-151TAP 345 762467 G18-015-TAP 345 1 | [7 empty] | G17-151-Tap to G18-015-Tap 345 kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | 766291 G20-009-TAP 345 769260 G22-114-TAP 345 1 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | 767200 G22-011-TAP 345 769260 G22-114-TAP 345 1 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 27WP | P12:115:NPPD:1178B:BPS SUB7-SHELDON7:BTB:: | [7 empty] | Multi - Sheldon - Monolith 115 kV
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | [7 empty] | Multi - Sheldon - Monolith 115 kV
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 27WP | P12:115:NPPD:LN008::SHELDON.CLATONIA.CKT1:: | [7 empty] | Multi - Sheldon - Monolith 115 kV
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 27WP | P13:115-345:NPPD:MOORE 3:T1::: | [7 empty] | Multi - Sheldon - Monolith 115 kV
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 27WP | P13:115-345:NPPD:T960::MOORE.CKT1:: | [7 empty] | Multi - Sheldon - Monolith 115 kV
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | P23:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB:::: | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | P42:345:AEPW:LAWTON EASTSIDE CB 3433A NBTB+FAULT:::: | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511456_12 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511456_15 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511456_18 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511456_19 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511456_3 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511456_8 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511468_11 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511468_16 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511468_20 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511468_23 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511468_25 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511468_27 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511468_27 | [7 empty] | Gracemont to G22-114-Tap 345 kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 511468_5 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP | Potential P4 Event - POI 762216_10 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP | Potential P4 Event - POI 762216_12 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP | Potential P4 Event - POI 762216_14 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP | Potential P4 Event - POI 762216_3 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP | Potential P4 Event - POI 762216_7 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP | Potential P4 Event - POI 762467_1 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP | Potential P4 Event - POI 762467_4 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP | Potential P4 Event - POI 762467_7 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP | Potential P4 Event - POI 762467_8 | [7 empty] | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2; Oklaunion to G22-011-TAP 345kV New Line; Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 766291_0 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 766291_0 | [7 empty] | Gracemont to G22-114-Tap 345 kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 766291_1 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 766291_2 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 766291_3 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 766291_5 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 766291_7 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line
00NR | DISIS-2023-001 CF | NRIS | Non-Converged | Non-Converged | 24SP,27SP,27WP | Potential P4 Event - POI 766291_9 | [7 empty] | Lawton Eastside to G20-009-TAP 345kV New Line; Gracemont to G22-114-Tap 345 kV New Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 24SP,27SP | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 187 | 211 | <90% | 118.87 |  |  |  | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 300101 5MORGAN 161 547478 DAD368 5 161 1 | 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 223 | 223 | 91.96 | 100.48 |  |  |  | Build RIV4525 to G20-079-TAP 161 kV Line 2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 338758 5HEBER.N# 161 505422 GREERSF5 161 1 | 24SP,27SP | 505418 JONESBO5 161 774620 G23-132-TAP 161 1 | 205 | 205 | <90% | 109.93 |  |  |  | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 27WP | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | 223 | 223 | <90% | 101.36 |  |  |  | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 505522 VAN BUR5 161 515339 VBI 5 161 Z1 | 27WP | 505582 RS KERR5 161 515254 SUNSTCN5 161 1 | 335 | 335 | <90% | 100.79 |  |  |  | Rebuild the existing VAN BUR5 to VBI 5 161 kV line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 508359 WELSH 7 345 508841 WILKES 7 345 1 | 24SP,27SP,27WP | P23:345:AEPW:WELSH CB 11990 NBTB:::: | 905 | 1059 | <90% | 116.97 |  |  |  | WELSH 7 to WILKES 7 345kV Line Rebuild; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 508808 LONGWD 4 138 997975 LONGWOOD 138 1 | 24SP,27SP | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | 451.7 | 478.4 | 111.42 | 107.81 |  |  |  | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 508809 LONGWD 7 345 997975 LONGWOOD 138 1 | 24SP,27SP | P23:345:AEPW:SW SHREVEPORT CB 10500 NBTB:::: | 451.7 | 478.4 | 112.97 | 109.46 |  |  |  | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 510902 WELETK4 138 510923 EC.HEN-4 138 1 | 24SP,27SP | P12:138:AEPW:HENRYET4:WELETK4::: | 151 | 152 | <90% | 111.62 |  |  |  | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511421 VERDEN 4 138 511477 S.W.S.-4 138 1 | 27SP | P42:345:OKGE:SB_MICO7312:::: | 212 | 212 | <90% | 101.62 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511425 TUTCONT4 138 511501 TUTTLE4 138 1 | 24SP,27SP | P42:345:OKGE:SB_MICO7312:::: | 209 | 212 | <90% | 109.45 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511425 TUTCONT4 138 514898 CIMARON4 138 1 | 24SP,27SP | P42:345:OKGE:SB_MICO7312:::: | 191 | 191 | <90% | 117.97 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511449 CORNVIL4 138 511483 NORGE--4 138 1 | 24SP,27SP | P42:345:OKGE:SB_MICO7312:::: | 136 | 136 | <90% | 139.62 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511449 CORNVIL4 138 511575 LEONARD4 138 1 | 24SP,27SP | P42:345:OKGE:SB_MICO7312:::: | 212 | 212 | <90% | 127.4 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511453 DUNCAN-4 138 511552 DUNCHERTP4 138 1 | 24SP,27SP | Potential P4 Event - POI 515800_5 | 106 | 106 | <90% | 145.87 |  |  |  | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511453 DUNCAN-4 138 529304 OMDUNCN4 138 1 | 24SP,27SP | Potential P4 Event - POI 515800_5 | 121 | 158 | <90% | 135.01 |  |  |  | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511455 D.E.S.-4 138 511552 DUNCHERTP4 138 1 | 24SP,27SP | Potential P4 Event - POI 515800_5 | 106 | 106 | <90% | 142.14 |  |  |  | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511455 D.E.S.-4 138 529344 OMDUNE-4 138 1 | 24SP,27SP | Potential P4 Event - POI 515800_5 | 106 | 106 | <90% | 137.49 |  |  |  | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511467 L.E.S.-4 138 997918 LES 5 138 2 | 24SP,27SP | Potential P4 Event - POI 515800_5 | 484 | 515 | <90% | 105.43 |  |  |  | Gracemont to Treasure Island 345 kV New Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511468 L.E.S.-7 345 997918 LES 5 138 2 | 24SP,27SP | Potential P4 Event - POI 515800_5 | 484 | 515 | <90% | 104.92 |  |  |  | Gracemont to Treasure Island 345 kV New Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511477 S.W.S.-4 138 511483 NORGE--4 138 1 | 24SP,27SP,27WP | P42:345:OKGE:SB_MICO7312:::: | 136 | 136 | <90% | 159.25 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Lawton Eastside to Draper 345 kV New Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511494 COMMTAP4 138 529304 OMDUNCN4 138 1 | 24SP,27SP | Potential P4 Event - POI 515800_5 | 121 | 171 | <90% | 124.89 |  |  |  | Gracemont to Treasure Island 345 kV New Line; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511501 TUTTLE4 138 511575 LEONARD4 138 1 | 24SP,27SP | P42:345:OKGE:SB_MICO7312:::: | 209 | 212 | <90% | 114.6 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511541 SWEETWT6 230 511557 CHISHOLM6 230 1 | 24SP,27SP,27WP | Potential P4 Event - POI 762216_14 | 353 | 353 | <90% | 145.09 |  |  |  | Sweetwater to Chisholm 230 kV Line Rebuild
00NR | DISIS-2023-001 CF | NRIS | Thermal | 511541 SWEETWT6 230 523779 STLN-DEMARC6 230 1 | 24SP,27SP,27WP | Potential P4 Event - POI 762216_14 | 349 | 395 | <90% | 105.25 |  |  |  | Sweetwater to Demarcation 230 kV Line Rebuild
00NR | DISIS-2023-001 CF | NRIS | Thermal | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 24SP,27SP,27WP | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 335 | 335 | <90% | 111.47 |  |  |  | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade
00NR | DISIS-2023-001 CF | NRIS | Thermal | 512632 AFTON 5 161 512669 KETCHUM5 161 1 | 24SP,27SP,27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 194 | 194 | <90% | 104.47 |  |  |  | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 512654 PENSA 5 161 512669 KETCHUM5 161 1 | 24SP,27SP,27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 194 | 194 | <90% | 108.1 |  |  |  | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 512654 PENSA 5 161 772960 G23-049-TAP 161 1 | 24SP,27SP,27WP | 512629 DRYGULCH5 161 772540 G23-028-TAP 161 1 | 335 | 335 | <90% | 111.84 |  |  |  | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 514801 MINCO 7 345 514901 CIMARON7 345 1 | 24SP,27SP,27WP | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1195 | 1195 | <90% | 149.51 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 514801 MINCO 7 345 515800 GRACMNT7 345 1 | 24SP,27SP | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 1342 | 1541 | <90% | 109.26 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 514853 DVISION4 138 514863 HAYMAKR4 138 1 | 27SP | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 268 | 308 | <90% | 105.49 |  |  |  | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 24SP,27SP | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 268 | 308 | <90% | 115.66 |  |  |  | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 514868 DOUGLTP4 138 514922 CLASSEN4 138 1 | 24SP,27SP,27WP | 514861 MUSTANG4 138 514865 COUNCIL4 138 1 | 268 | 287 | 103.69 | 115.8 |  |  |  | Multi - West Oaks - Council - Classen 138 kV Reconductor
00NR | DISIS-2023-001 CF | NRIS | Thermal | 514893 XEROX 4 138 514894 CZECHAL4 138 1 | 24SP,27SP | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 382 | 382 | <90% | 109.36 |  |  |  | Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 514894 CZECHAL4 138 514898 CIMARON4 138 1 | 24SP,27SP | 514863 HAYMAKR4 138 514898 CIMARON4 138 1 | 382 | 382 | 90.54 | 120.13 |  |  |  | Czech Hall 138 kV Terminal Upgrade
00NR | DISIS-2023-001 CF | NRIS | Thermal | 514898 CIMARON4 138 997829 CIMARON1 138 1 | 24SP,27SP | P13:138-345:OKGE:BKRBKR_3W021:::: | 478 | 478 | 91.05 | 105.83 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 514901 CIMARON7 345 997829 CIMARON1 138 1 | 24SP,27SP | P13:138-345:OKGE:BKRBKR_3W021:::: | 478 | 478 | 95.06 | 109.83 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 515135 SUNNYSD4 138 997799 SUNNYSD3 138 3 | 24SP | P13:138-345:OKGE:BKRBKR_3W045:::: | 330 | 330 | <90% | 103.63 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 515135 SUNNYSD4 138 997801 SUNNYSD3 138 3 | 27SP | P13:138-345:OKGE:BKRBKR_3W045:::: | 330 | 330 | <90% | 104.14 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 515136 SUNNYSD7 345 764115 G20-074-TAP 345 1 | 24SP,27SP | P42:345:OKGE:SB_MICO7312:::: | 1058 | 1195 | <90% | 111.17 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 515136 SUNNYSD7 345 997799 SUNNYSD3 138 3 | 24SP | P13:138-345:OKGE:BKRBKR_3W045:::: | 330 | 330 | <90% | 102.54 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 515136 SUNNYSD7 345 997801 SUNNYSD3 138 3 | 27SP | P13:138-345:OKGE:BKRBKR_3W045:::: | 330 | 330 | <90% | 103.47 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 515800 GRACMNT7 345 997726 GRACMNT3 138 3 | 24SP | P42:345:OKGE:SB_GRNT7381:::: | 478 | 478 | <90% | 117.5 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 515800 GRACMNT7 345 997728 GRACMNT3 138 3 | 27SP,27WP | P42:345:OKGE:SB_GRNT7381:::: | 478 | 478 | <90% | 112.3 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 515802 GRACMNT4 138 520814 ANADARK4 138 1 | 24SP | P42:345:OKGE:SB_CION7384:::: | 200 | 234 | <90% | 112.08 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 515802 GRACMNT4 138 997726 GRACMNT3 138 3 | 24SP | P42:345:OKGE:SB_GRNT7381:::: | 478 | 478 | <90% | 117.6 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 515802 GRACMNT4 138 997728 GRACMNT3 138 3 | 27SP,27WP | P42:345:OKGE:SB_GRNT7381:::: | 478 | 478 | <90% | 112.61 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520422 SEQUOYAHJ4 138 520473 CKSHATP4 138 1 | 27SP,27WP | P42:345:OKGE:SB_CION7384:::: | 145 | 169 | <90% | 143.77 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520422 SEQUOYAHJ4 138 520814 ANADARK4 138 1 | 24SP,27SP,27WP | P42:345:OKGE:SB_CION7384:::: | 145 | 169 | <90% | 147.54 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520422 SEQUOYAHJ4 138 520867 CORN TP4 138 1 | 24SP | P42:345:OKGE:SB_CION7384:::: | 145 | 169 | <90% | 136.68 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520429 AMBJCT 2 69.0 520509 CLVJCTS2 69.0 1 | 24SP,27SP,27WP | P42:345:OKGE:SB_MICO7312:::: | 29 | 35 | <90% | 161.91 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520429 AMBJCT 2 69.0 520828 BLANCHD2 69.0 1 | 24SP,27SP,27WP | P42:345:OKGE:SB_MICO7312:::: | 29 | 35 | <90% | 161.63 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520473 CKSHATP4 138 520867 CORN TP4 138 1 | 27SP | P42:345:OKGE:SB_CION7384:::: | 145 | 169 | <90% | 140.23 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520501 BRIDGCR4 138 521059 SUNSHIN4 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 200 | 234 | <90% | 106.45 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520501 BRIDGCR4 138 521072 TUTLETP4 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 200 | 234 | <90% | 114.05 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520508 CLVJCTN2 69.0 520810 ANADARK2 69.0 1 | 24SP,27SP,27WP | System Intact | 58 | 68 | <90% | 327.65 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520510 NAPLSTP4 138 520867 CORN TP4 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 145 | 169 | <90% | 123.24 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520510 NAPLSTP4 138 520888 PAYNESW4 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 145 | 169 | <90% | 120.69 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520810 ANADARK2 69.0 520838 CADDO 2 69.0 1 | 24SP,27SP | 520814 ANADARK4 138 3WXFMR ANADARKO 1 | 58 | 68 | <90% | 102.3 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520814 ANADARK4 138 521031 POCASET4 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 200 | 234 | <90% | 122.01 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 520882 DOVERSW4 138 521016 OKEENE 4 138 1 | 24SP | Potential P4 Event - POI 515375_0 | 74 | 83 | <90% | 135.17 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 521031 POCASET4 138 768080 G22-055-TAP 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 200 | 234 | <90% | 120.12 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 521072 TUTLETP4 138 768080 G22-055-TAP 138 1 | 24SP,27SP | P42:345:OKGE:SB_CION7384:::: | 200 | 234 | <90% | 120.12 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV; Build the Crawfish Draw 345 kV Substation; Build new Double Circuit Crawfish to Seminole 765 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 523323 MCDWL_CREEK6 230 523959 POTTER_CO 6 230 1 | 24SP,27SP | 523961 POTTER_CO 7 345 3WXFMR POTTER_CO 7 1 | 318.7 | 318.7 | <90% | 104.57 |  |  |  | XFR-Potter County 345/230 kV Ckt1 & Ckt2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 523959 POTTER_CO 6 230 773700 G23-086-TAP 230 1 | 24SP,27SP | 525832 TUCO_INT 7 345 762216 G17-151TAP 345 1 | 490 | 540 | <90% | 141.71 |  |  |  | XFR-Potter County 345/230 kV Ckt1 & Ckt2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 523959 POTTER_CO 6 230 997630 POTTER_CO 7 230 1 | 27WP | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | 516 | 559 | <90% | 128 |  |  |  | XFR-Potter County 345/230 kV Ckt1 & Ckt2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 523961 POTTER_CO 7 345 997630 POTTER_CO 7 230 1 | 27WP | P12:230:AEPW:SWEETWT6:CHISHOLM6::: | 516 | 559 | <90% | 127.53 |  |  |  | XFR-Potter County 345/230 kV Ckt1 & Ckt2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 524648 CARGILL 3 115 524655 FRIONA 3 115 1 | 24SP,27SP | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 95.6 | 105 | <90% | 123.27 |  |  |  | Curry - Deafsmith 115 kV Ckt 1 Rebuild
00NR | DISIS-2023-001 CF | NRIS | Thermal | 524669 DS-#20 3 115 524822 CURRY 3 115 1 | 24SP,27SP | 525481 PLANT_X 6 230 760498 G17-146-TAP 230 1 | 93.2 | 102.6 | <90% | 162.53 |  |  |  | Curry - Deafsmith 115 kV Ckt 1 Rebuild
00NR | DISIS-2023-001 CF | NRIS | Thermal | 524822 CURRY 3 115 524908 ROOSEVELT 3 115 2 | 24SP,27SP | 524770 PLSNT_HILL 6 230 3WXFMR EFAE1100068A 1 | 158 | 174 | <90% | 109.48 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 524875 OASIS 6 230 524909 ROOSEVELT 6 230 1 | 24SP,27SP | 524770 PLSNT_HILL 6 230 524909 ROOSEVELT 6 230 1 | 319 | 319 | <90% | 108.58 |  |  |  | Multi - Minco - Pleasant Valley - Draper 345 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 24SP,27SP,27WP | 525531 TOLK 6 230 525830 TUCO_INT 6 230 1 | 321.1 | 321.1 | <90% | 268.3 |  |  |  | Newhart - Plant X 230 kV Ckt 1 Rebuild
00NR | DISIS-2023-001 CF | NRIS | Thermal | 525480 PLANT_X 3 115 997582 WH ALM20171 115 1 | 24SP,27SP,27WP | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 251 | 251 | <90% | 170.84 |  |  |  | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 525481 PLANT_X 6 230 997582 WH ALM20171 115 1 | 24SP,27SP,27WP | 525461 NEWHART 6 230 525481 PLANT_X 6 230 1 | 251 | 251 | <90% | 175.67 |  |  |  | Upgrade the existing PLANTX 230/115 kV Transformer; Build New Crossroads to Potter County 345 kV Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 527867 CUNNIGHM_S 6 230 527894 HOBBS_INT 6 230 1 | 27SP | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | 478 | 478 | <90% | 103.69 |  |  |  | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
00NR | DISIS-2023-001 CF | NRIS | Thermal | 527894 HOBBS_INT 6 230 997499 HICO 68759-1 230 1 | 27SP | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | 528 | 607 | <90% | 102.31 |  |  |  | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
00NR | DISIS-2023-001 CF | NRIS | Thermal | 527896 HOBBS_INT 7 345 997499 HICO 68759-1 230 1 | 27SP | 527896 HOBBS_INT 7 345 527965 KIOWA 7 345 1 | 528 | 607 | <90% | 103.84 |  |  |  | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt
00NR | DISIS-2023-001 CF | NRIS | Thermal | 529307 OMMARLO4 138 529344 OMDUNE-4 138 1 | 24SP | Potential P4 Event - POI 515800_5 | 106 | 106 | <90% | 101.18 |  |  |  | Gracemont to Treasure Island 345 kV New Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 531379 JONES3 115 531426 JAMESON3 115 1 | 24SP,27SP | Potential P4 Event - POI 531449_3 | 119.5 | 148.2 | <90% | 100.85 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 531379 JONES3 115 531448 HOLCOMB3 115 1 | 24SP,27SP | Potential P4 Event - POI 531449_3 | 119.5 | 148.2 | <90% | 106.84 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 531405 WALKMYR3 115 531510 HARBNGR3 115 1 | 24SP,27SP | Potential P4 Event - POI 531449_2 | 355 | 355 | <90% | 104.63 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 531405 WALKMYR3 115 539654 CIM-PLT3 115 1 | 24SP,27SP | Potential P4 Event - POI 531449_2 | 153.4 | 165.1 | <90% | 115.93 |  |  |  | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
00NR | DISIS-2023-001 CF | NRIS | Thermal | 531419 DOBSON 3 115 531493 GANO 3 115 1 | 24SP,27SP | Potential P4 Event - POI 531449_3 | 211.7 | 228.5 | <90% | 115.14 |  |  |  | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
00NR | DISIS-2023-001 CF | NRIS | Thermal | 531420 FLETCHR3 115 531440 WILLIAM3 115 1 | 24SP,27SP | Potential P4 Event - POI 531449_3 | 99.6 | 99.6 | <90% | 103.1 |  |  |  | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
00NR | DISIS-2023-001 CF | NRIS | Thermal | 531432 PILE 3 115 531433 SCOTCTY3 115 1 | 24SP,27SP,27WP | Potential P4 Event - POI 531449_3 | 195.4 | 195.4 | <90% | 131.7 |  |  |  | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
00NR | DISIS-2023-001 CF | NRIS | Thermal | 531432 PILE 3 115 531493 GANO 3 115 1 | 24SP,27SP | Potential P4 Event - POI 531449_3 | 211.7 | 228.5 | <90% | 114.1 |  |  |  | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion
00NR | DISIS-2023-001 CF | NRIS | Thermal | 531445 GRDNCTY3 115 531448 HOLCOMB3 115 1 | 24SP,27SP,27WP | Potential P4 Event - POI 531449_3 | 195.4 | 195.4 | <90% | 113.71 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 531449 HOLCOMB7 345 997448 HOLCOMB 115 1 | 24SP,27SP | Potential P4 Event - POI 531449_3 | 336 | 358.5 | <90% | 100.35 |  |  |  | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
00NR | DISIS-2023-001 CF | NRIS | Thermal | 532935 MARMTNW5 161 532937 NEOSHO 5 161 1 | 24SP,27SP,27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 148 | 148 | <90% | 132.53 |  |  |  | Build RIV4525 to G20-079-TAP 161 kV Line 2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 532937 NEOSHO 5 161 997363 NEOSHO TX-5 138 1 | 24SP,27SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 150 | 165 | <90% | 110.57 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2023-001 CF | NRIS | Thermal | 532937 NEOSHO 5 161 997364 NEOSHO TX-4 138 1 | 24SP,27SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 112 | 123.2 | <90% | 107.95 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2023-001 CF | NRIS | Thermal | 533020 NEOSHOS4 138 997363 NEOSHO TX-5 138 1 | 24SP,27SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 150 | 165 | <90% | 110.35 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2023-001 CF | NRIS | Thermal | 533021 NEOSHO 4 138 997364 NEOSHO TX-4 138 1 | 24SP,27SP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 112 | 123.2 | <90% | 107.73 |  |  |  | Reconfigure the Neosho Transformers
00NR | DISIS-2023-001 CF | NRIS | Thermal | 533301 EAST ST3 115 533309 WEMPORI3 115 1 | 27SP | 533304 LANG 3 115 533307 PRAIRIE3 115 1 | 92 | 92 | <90% | 110.31 |  |  |  | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 533758 CRAWFOR2 69.0 533772 SE1GREE2 69.0 1 | 24SP,27SP,27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 48 | 57 | 91.2 | 119.21 |  |  |  | Build RIV4525 to G20-079-TAP 161 kV Line 2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 533762 GIR JCT2 69.0 533772 SE1GREE2 69.0 1 | 24SP,27SP,27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 55 | 57 | <90% | 112.47 |  |  |  | Build RIV4525 to G20-079-TAP 161 kV Line 2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 533762 GIR JCT2 69.0 533876 FRANKLIN2 69.0 1 | 27WP | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 55 | 57 | <90% | 101.42 |  |  |  | Build RIV4525 to G20-079-TAP 161 kV Line 2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 27SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | 717 | 717 | 95.73 | 102.17 |  |  |  | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
00NR | DISIS-2023-001 CF | NRIS | Thermal | 541210 MARTCTY5 161 543002 MARTCIT5 161 1 | 24SP,27SP,27WP | 541198 PECULR 7 345 542968 STILWEL7 345 1 | 311 | 334 | <90% | 111.68 |  |  |  | Martin City (East) - Martin City (West) 161 kV Terminal Equipment
00NR | DISIS-2023-001 CF | NRIS | Thermal | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 24SP,27SP,27WP | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 199 | 223 | <90% | 116.8 |  |  |  | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 542965 W.GRDNR7 345 997212 WEST GARDN11 161 11 | 27SP,27WP | Potential P4 Event - POI 542965_4 | 535 | 535 | <90% | 116.76 |  |  |  | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 542965 W.GRDNR7 345 997213 WEST GARDN11 161 11 | 24SP | Potential P4 Event - POI 542965_4 | 535 | 535 | 96.27 | 106.73 |  |  |  | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 542966 WGARDNR5 161 543049 CEDRCRK5 161 1 | 24SP,27SP | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | 334 | 334 | 110.42 | 112.07 |  |  |  | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 542966 WGARDNR5 161 543132 BNSF 5 161 1 | 24SP,27SP | Potential P4 Event - POI 542965_4 | 311 | 334 | 100.69 | 105.73 |  |  |  | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 542966 WGARDNR5 161 997212 WEST GARDN11 161 11 | 27SP,27WP | Potential P4 Event - POI 542965_4 | 535 | 535 | <90% | 116.48 |  |  |  | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 542966 WGARDNR5 161 997213 WEST GARDN11 161 11 | 24SP | Potential P4 Event - POI 542965_4 | 535 | 535 | 95.07 | 105.67 |  |  |  | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 542969 STILWEL5 161 543053 REDEL 5 161 1 | 24SP,27SP,27WP | 541198 PECULR 7 345 542968 STILWEL7 345 1 | 311 | 334 | 112.52 | 113.16 |  |  |  | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 542978 CRAIG 5 161 542979 PFLUMM 5 161 1 | 24SP,27SP | 543036 OLATHE 5 161 543045 SWITZER5 161 1 | 311 | 334 | 110.09 | 102.28 |  |  |  | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 543002 MARTCIT5 161 543053 REDEL 5 161 1 | 27SP | 541198 PECULR 7 345 542968 STILWEL7 345 1 | 311 | 334 | 103.65 | 104.46 |  |  |  | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 543044 MOONLT 5 161 543132 BNSF 5 161 1 | 27SP | Potential P4 Event - POI 542965_4 | 311 | 334 | 96.34 | 101.37 |  |  |  | Multi - Atlantic- Craig - West Gardener 345/115 kV; Build STILWEL7 to G21-029-TAP 345 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 547467 ORO110 5 161 547469 RIV4525 161 1 | 24SP,27SP,27WP | 547469 RIV4525 161 547498 STL439 5 161 1 | 404 | 420 | <90% | 105.44 |  |  |  | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 24SP,27SP,27WP | Potential P4 Event - POI 532793_1 | 558 | 558 | <90% | 133.79 |  |  |  | Build RIV4525 to G20-079-TAP 161 kV Line 2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 24SP,27SP | P42:345:NPPD:BKR-AXT-3308:::: | 229 | 229 | 109.39 | 111.04 |  |  |  | Build new AXTELL 7 to KEARNEY7 115kV Line 2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 24SP,27SP,27WP | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 193 | 193 | <90% | 121.49 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640076 BEATRCE7 115 640088 BPS SUB7 115 2 | 24SP,27SP,27WP | 640076 BEATRCE7 115 640088 BPS SUB7 115 1 | 193 | 193 | <90% | 122 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 99 | 99 | <90% | 187.53 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 140 | 140 | <90% | 273.17 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640088 BPS SUB7 115 640278 SHELDON7 115 1 | 24SP,27SP,27WP | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 193 | 193 | <90% | 218.14 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640088 BPS SUB7 115 996896 BPS_345_115 115 1 | 27SP,27WP | System Intact | 417 | 417 | <90% | 174.4 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640088 BPS SUB7 115 996897 BPS_345_115 115 1 | 24SP | System Intact | 417 | 417 | <90% | 174.4 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640111 CLATONA7 115 640278 SHELDON7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 137 | 137 | <90% | 272.34 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | 24SP,27SP,27WP | P12:115:NPPD:LN007::SHELDON.BPS SUB.CKT1:: | 99 | 99 | <90% | 119.44 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 640261 LOWELL 7 115 640275 MINDEN 7 115 1 | 27SP | 640066 AXTELL 7 115 640250 KEARNEY7 115 1 | 120 | 120 | 99.26 | 103.25 |  |  |  | Build new AXTELL 7 to KEARNEY7 115kV Line 2
00NR | DISIS-2023-001 CF | NRIS | Thermal | 652519 OAHE 4 230 655487 SULLYBT-ER4 230 1 | 27WP | Potential P4 Event - POI 659105_15 | 239 | 239 | <90% | 107.96 |  |  |  | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 655487 SULLYBT-ER4 230 655510 SB.LS-WK-ER4 230 Z | 27WP | Potential P4 Event - POI 659105_15 | 239 | 239 | <90% | 100.31 |  |  |  | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV
00NR | DISIS-2023-001 CF | NRIS | Thermal | 771999 G23-222-POI 345 996896 BPS_345_115 115 1 | 27SP,27WP | 640088 BPS SUB7 115 640111 CLATONA7 115 1 | 417 | 417 | <90% | 171.62 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1
00NR | DISIS-2023-001 CF | NRIS | Thermal | 771999 G23-222-POI 345 996897 BPS_345_115 115 1 | 24SP | System Intact | 417 | 417 | <90% | 170.93 |  |  |  | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1; Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1

## Assigned Upgrade Costs
Gen Number | Study Name | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2023-166 | DISIS-2023-001 | 04 SOUTHEAST | 158931 | ERIS | 84th Street - Tennessee Tap 138 kV Line GEN-2023-166 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-166 (150MW/Battery/Storage), into 84th Street - Tennessee Tap 138 kV Line | 7079843 | 100% | 7079843 | 1
GEN-2023-166 | DISIS-2023-001 | 04 SOUTHEAST | 158930 | ERIS | 84th Street - Tennessee Tap 138 kV Line GEN-2023-166 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-166 (150MW/Battery/Storage), into 84th Street - Tennessee Tap 138 kV Line | 3759390 | 100% | 3759390 | 1
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | 159002 | ERIS | Amarillo South 115 kV GEN-2023-209 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-209 (125MW/Battery/Storage), into Amarillo South 115 kV | 15402434 | 100% | 15402434 | 1
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | 159001 | ERIS | Amarillo South 115 kV GEN-2023-209 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-209 (125MW/Battery/Storage), into Amarillo South 115 kV | 2948304 | 100% | 2948304 | 1
GEN-2023-087 | DISIS-2023-001 | 03 CENTRAL | 158821 | ERIS | Archie 161 kV Substation GEN-2023-087 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-087 (200MW/Solar), into Archie 161 kV Substation | 26353701 | 100% | 26353701 | 1
GEN-2023-087 | DISIS-2023-001 | 03 CENTRAL | 158820 | ERIS | Archie 161 kV Substation GEN-2023-087 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-087 (200MW/Solar), into Archie 161 kV Substation | 1085685 | 100% | 1085685 | 1
GEN-2023-206 | DISIS-2023-001 | 04 SOUTHEAST | 158996 | ERIS | Battlefield BESS 161 kV Substation GEN-2023-206 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-206 (50MW/Battery/Storage), into Battlefield BESS 161 kV Substation | 30000 | 100% | 30000 | 1
GEN-2023-206 | DISIS-2023-001 | 04 SOUTHEAST | 158995 | ERIS | Battlefield BESS 161 kV Substation GEN-2023-206 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-206 (50MW/Battery/Storage), into Battlefield BESS 161 kV Substation | 100000 | 100% | 100000 | 1
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | 158723 | ERIS | Bird Hollow (Langley) - Pryor Junction 138 kV Line GEN-2023-027 Intercon (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-027 (150MW/Hybrid), into Bird Hollow (Langley) - Pryor Junction 138 kV Line | 11850000 | 100% | 11850000 | 1
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | 158722 | ERIS | Bird Hollow (Langley) - Pryor Junction 138 kV Line GEN-2023-027 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-027 (150MW/Hybrid), into Bird Hollow (Langley) - Pryor Junction 138 kV Line | 2125000 | 100% | 2125000 | 1
GEN-2023-022 | DISIS-2023-001 | 04 SOUTHEAST | 158713 | ERIS | Candian River 345 kV Substation GEN-2023-022 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-022 (250MW/Wind), into Candian River 345 kV Substation | 1790488 | 100% | 1790488 | 1
GEN-2023-022 | DISIS-2023-001 | 04 SOUTHEAST | 158712 | ERIS | Candian River 345 kV Substation GEN-2023-022 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-022 (250MW/Wind), into CaN/Adian River 345 kV Substation | 1591654 | 100% | 1591654 | 1
GEN-2023-061 | DISIS-2023-001 | 03 CENTRAL | 158778 | ERIS | Carthage 161 kV Substation GEN-2023-061 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-061 (100MW/Battery/Storage), into Carthage 161 kV Substation | 4200000 | 100% | 4200000 | 1
GEN-2023-061 | DISIS-2023-001 | 03 CENTRAL | 158777 | ERIS | Carthage 161 kV Substation GEN-2023-061 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-061 (100MW/Battery/Storage), into Carthage 161 kV Substation | 700000 | 100% | 700000 | 1
GEN-2023-063 | DISIS-2023-001 | 04 SOUTHEAST | 158782 | ERIS | Catoosa - Owasso 88th 138 kV line GEN-2023-063 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-063 (135MW/Hybrid), into Catoosa - Owasso 88th 138 kV line | 11850000 | 100% | 11850000 | 1
GEN-2023-063 | DISIS-2023-001 | 04 SOUTHEAST | 158781 | ERIS | Catoosa - Owasso 88th 138 kV line GEN-2023-063 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-063 (135MW/Hybrid), into Catoosa - Owasso 88th 138 kV line | 2125000 | 100% | 2125000 | 1
GEN-2023-023 | DISIS-2023-001 | 03 CENTRAL | 158715 | ERIS | Center City 161 kV Substation GEN-2023-023 Interconnection (Non-Shared NU) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-023 (200MW/Battery/Storage), into Center City 161 kV Substation | 4998381 | 100% | 4998381 | 1
GEN-2023-023 | DISIS-2023-001 | 03 CENTRAL | 158714 | ERIS | Center City 161 kV Substation GEN-2023-023 Interconnection (TOIF) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-023 (200MW/Battery/Storage), into Center City 161 kV Substation | $- | 100% | $- | 1
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | 159010 | ERIS | Chamber Springs 161 kV Substation GEN-2023-213 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-213 (100MW/Battery/Storage), into Chamber Springs 161 kV Substation | 3160652 | 100% | 3160652 | 1
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | 159009 | ERIS | Chamber Springs 161 kV Substation GEN-2023-213 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-213 (100MW/Battery/Storage), into Chamber Springs 161 kV Substation | 6911274 | 100% | 6911274 | 1
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | 158847 | ERIS | Chappelle Creek 345 kV Substation GEN-2023-105 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-105 (249MW/Wind), into Chappelle Creek 345 Kv Substation | 2041297 | 100% | 2041297 | 1
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | 158661 | ERIS | Chappelle Creek 345 kV Substation Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-105(249 MW/Wind), into Chappelle Creek 345 kV Substation | 11207272 | 100% | 11207272 | 1
GEN-2023-168 | DISIS-2023-001 | 04 SOUTHEAST | 158935 | ERIS | Classen 138 kV Substation GEN-2023-168 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-168 (175MW/Battery/Storage), into Classen 138 kV Substation | 10000000 | 100% | 10000000 | 1
GEN-2023-168 | DISIS-2023-001 | 04 SOUTHEAST | 158934 | ERIS | Classen 138 kV Substation GEN-2023-168 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-168 (175MW/Battery/Storage), into Classen 138 kV Substation | 2000000 | 100% | 2000000 | 1
GEN-2023-034 | DISIS-2023-001 | 03 CENTRAL | 158737 | ERIS | Clear Water - Waco 138 kV line GEN-2023-034 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-034 (130MW/Solar), into Clear Water - Waco 138 kV line | 15091408 | 100% | 15091408 | 1
GEN-2023-034 | DISIS-2023-001 | 03 CENTRAL | 158736 | ERIS | Clear Water - Waco 138 kV line GEN-2023-034 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-034 (130MW/Solar), into Clear Water - Waco 138 kV line | 928794 | 100% | 928794 | 1
GEN-2023-035 | DISIS-2023-001 | 04 SOUTHEAST | 158739 | ERIS | Cleveland - Amber Tap 138 kV Line GEN-2023-035 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-035 (200MW/Solar), into Cleveland - Amber Tap 138 kV Line | 6050000 | 100% | 6050000 | 1
GEN-2023-035 | DISIS-2023-001 | 04 SOUTHEAST | 158738 | ERIS | Cleveland - Amber Tap 138 kV Line GEN-2023-035 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-035 (200MW/Solar), into Cleveland - Amber Tap 138 kV Line | 517000 | 100% | 517000 | 1
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | 159043 | ERIS | Crawfish Draw 345 kV Substation GEN-2023-237 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-237 (500MW/Wind), into Crawfish Draw 345 kV Substation | 56159206 | 100% | 56159206 | 1
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | 159042 | ERIS | Crawfish Draw 345 kV Substation GEN-2023-237 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-237 (500MW/Wind), into Crawfish Draw 345 kV Substation | 3433613 | 100% | 3433613 | 1
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | 158809 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-081 Interconnection (Non-Shared NU) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-081 (625MW/Hybrid), into Crossroads - Hobbs 345 kV Line | 41756429 | 100% | 41756429 | 1
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | 158808 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-081 Interconnection (TOIF) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-081 (625MW/Hybrid), into Crossroads - Hobbs 345 kV Line | 578564 | 100% | 578564 | 1
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | 158986 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-201 Interconnection (Non-Shared NU) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-201 (300MW/Hybrid), into Crossroads - Hobbs 345 kV Line | 27334989 | 100% | 27334989 | 1
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | 158985 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-201 Interconnection (TOIF) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-201 (300MW/Hybrid), into Crossroads - Hobbs 345 kV Line | 589025 | 100% | 589025 | 1
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | 158839 | ERIS | Degrasse 345 kV Substation GEN-2023-100 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100 (300MW/Hybrid), into Degrasse 345 kV Substation | 2986797 | 100% | 2986797 | 1
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | 158842 | ERIS | Degrasse 345 kV Substation GEN-2023-102 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-102 (475MW/Hybrid), into Degrasse 345 kV Substation | 2986797 | 100% | 2986797 | 1
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | 158662 | ERIS | Degrasse 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100/102 (300/475MW/Hybrid), into Degrasse 345 kV Substation | 2887952.9 | 38.71% | 7460545 | 1
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | 158662 | ERIS | Degrasse 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100/102 (300/475MW/Hybrid), into Degrasse 345 kV Substation | 4572592.1 | 61.29% | 7460545 | 1
GEN-2023-075 | DISIS-2023-001 | 04 SOUTHEAST | 158801 | ERIS | Delaware - Neosho 345 kV GEN-2023-075 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-075 (200MW/Wind), into Delaware - Neosho 345 kV | 1958090 | 100% | 1958090 | 1
GEN-2023-076 | DISIS-2023-001 | 04 SOUTHEAST | 158802 | ERIS | Delaware - Neosho 345 kV GEN-2023-076 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-076 (100MW/Wind), into Delaware - Neosho 345 kV | 112909 | 100% | 112909 | 1
GEN-2023-075 | DISIS-2023-001 | 04 SOUTHEAST | 158663 | ERIS | Delaware - Neosho 345 kV Interconnection (DISIS-2023-001) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-075/076 (200/100MW/Wind), into Delaware - Neosho 345 kV | 20936266.67 | 66.67% | 31404400 | 1
GEN-2023-076 | DISIS-2023-001 | 04 SOUTHEAST | 158663 | ERIS | Delaware - Neosho 345 kV Interconnection (DISIS-2023-001) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-075/076 (200/100MW/Wind), into Delaware - Neosho 345 kV | 10468133.33 | 33.33% | 31404400 | 1
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | 158725 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-028 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-028 (230MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | 6545735 | 100% | 6545735 | 1
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | 158724 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-028 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-028 (230MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | 1057500 | 100% | 1057500 | 1
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | 158758 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-049 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-049 (150MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | 5801735 | 100% | 5801735 | 1
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | 158757 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-049 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-049 (150MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | 852499 | 100% | 852499 | 1
GEN-2023-036 | DISIS-2023-001 | 03 CENTRAL | 158741 | ERIS | Eckles Road 161 kV Substation GEN-2023-036 Interconnection (Non-Shared NU) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-036 (165MW/Battery/Storage), into Eckles Road 161 kV Substation | 2800000 | 100% | 2800000 | 1
GEN-2023-036 | DISIS-2023-001 | 03 CENTRAL | 158740 | ERIS | Eckles Road 161 kV Substation GEN-2023-036 Interconnection (TOIF) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-036 (165MW/Battery/Storage), into Eckles Road 161 kV Substation. | 500000 | 100% | 500000 | 1
GEN-2023-220 | DISIS-2023-001 | 03 CENTRAL | 159019 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-220 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-220 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | 32882571 | 100% | 32882571 | 1
GEN-2023-220 | DISIS-2023-001 | 03 CENTRAL | 159018 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-220 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-220 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | 1958092 | 100% | 1958092 | 1
GEN-2023-221 | DISIS-2023-001 | 03 CENTRAL | 159021 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-221 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-221 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | 33237331 | 100% | 33237331 | 1
GEN-2023-221 | DISIS-2023-001 | 03 CENTRAL | 159020 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-221 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-221 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | 1958092 | 100% | 1958092 | 1
GEN-2023-015 | DISIS-2023-001 | 03 CENTRAL | 158701 | ERIS | Finney-Carpenter 345 KV line GEN-2023-015 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-015 (330MW/Solar), into Finney-Carpenter 345 KV line | 42358867 | 100% | 42358867 | 1
GEN-2023-015 | DISIS-2023-001 | 03 CENTRAL | 158700 | ERIS | Finney-Carpenter 345 KV line GEN-2023-015 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-015 (330MW/Solar), into Finney-Carpenter 345 KV line | 3480128 | 100% | 3480128 | 1
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | 158879 | ERIS | Fixico Tap to Weleetka 138 kV Line GEN-2023-134 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-134 (252MW/Wind), into Fixico Tap to Weleetka 138 kV Line | 11850000 | 100% | 11850000 | 1
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | 158878 | ERIS | Fixico Tap to Weleetka 138 kV Line GEN-2023-134 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-134 (252MW/Wind), into Fixico Tap to Weleetka 138 kV Line | 1925000 | 100% | 1925000 | 1
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | 158911 | ERIS | Fort Thompson - Huron 230 kV Tap GEN-2023-154 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-154 (175MW/Solar), into Fort Thompson - Huron 230 kV Tap | 9974000 | 100% | 9974000 | 1
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | 158910 | ERIS | Fort Thompson - Huron 230 kV Tap GEN-2023-154 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-154 (175MW/Solar), into Fort Thompson - Huron 230 kV Tap | 641000 | 100% | 641000 | 1
GEN-2023-150 | DISIS-2023-001 | 04 SOUTHEAST | 158903 | ERIS | Gracemont 138 kV Substation GEN-2023-150 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-150 (150MW/Solar), into Gracemont 138 kV Substation | 2762110 | 100% | 2762110 | 1
GEN-2023-150 | DISIS-2023-001 | 04 SOUTHEAST | 158902 | ERIS | Gracemont 138 kV Substation GEN-2023-150 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-150 (150MW/Solar), into Gracemont 138 kV Substation | 3163387 | 100% | 3163387 | 1
GEN-2023-164 | DISIS-2023-001 | 04 SOUTHEAST | 158928 | ERIS | Gracemont 345 kV Substation GEN-2023-164 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-164 (210MW/Battery/Storage), into Gracemont 345 kV Substation | 1960313 | 100% | 1960313 | 1
GEN-2023-165 | DISIS-2023-001 | 04 SOUTHEAST | 158929 | ERIS | Gracemont 345 kV Substation GEN-2023-165 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-165 (210MW/Battery/Storage), into Gracemont 345 kV Substation | 1960313 | 100% | 1960313 | 1
GEN-2023-164 | DISIS-2023-001 | 04 SOUTHEAST | 158664 | ERIS | Gracemont 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-164/165 (210MW/Battery/Storage), into Gracemont 345 kV Substation | 2292428 | 50% | 4584856 | 1
GEN-2023-165 | DISIS-2023-001 | 04 SOUTHEAST | 158664 | ERIS | Gracemont 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-164/165 (210MW/Battery/Storage), into Gracemont 345 kV Substation | 2292428 | 50% | 4584856 | 1
GEN-2023-153 | DISIS-2023-001 | 02 NEBRASKA | 158909 | ERIS | Grant 115 kV Substation GEN-2023-153 Interconnection (Non-Shared NU) (Tri-State) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-153 (120MW/Hybrid), into Grant 115 kV Substation | 5250000 | 100% | 5250000 | 1
GEN-2023-153 | DISIS-2023-001 | 02 NEBRASKA | 158908 | ERIS | Grant 115 kV Substation GEN-2023-153 Interconnection (TOIF) (Tri-State) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-153 (120MW/Hybrid), into Grant 115 kV Substation | 1250000 | 100% | 1250000 | 1
GEN-2023-138 | DISIS-2023-001 | 04 SOUTHEAST | 158887 | ERIS | GRDA1 - Tonece7 345 kV Line GEN-2023-138 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-138 (250MW/Wind), into GRDA1 - Tonece7 345 kV Line | 12220783.75 | 100% | 12220783.75 | 1
GEN-2023-138 | DISIS-2023-001 | 04 SOUTHEAST | 158886 | ERIS | GRDA1 - Tonece7 345 kV Line GEN-2023-138 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-138 (250MW/Wind), into GRDA1 - Tonece7 345 kV Line | 1809871 | 100% | 1809871 | 1
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | 158956 | ERIS | Groton - Leland Olds 345 kV Line GEN-2023-182 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-182 (300MW/Wind), into Groton - Leland Olds 345 kV Line | 4110843 | 100% | 4110843 | 1
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | 158665 | ERIS | Groton - Leland Olds 345 kV Line Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-182 (300MW/Wind), into Groton - Leland Olds 345 kV Line | 22697499 | 100% | 22697499 | 1
GEN-2023-180 | DISIS-2023-001 | 04 SOUTHEAST | 158954 | ERIS | Hackett - N Huntington 161 kV Line Tap GEN-2023-180 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-180 (150MW/Solar), into Hackett - N Huntington 161 kV Line Tap | 11850000 | 100% | 11850000 | 1
GEN-2023-180 | DISIS-2023-001 | 04 SOUTHEAST | 158953 | ERIS | Hackett - N Huntington 161 kV Line Tap GEN-2023-180 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-180 (150MW/Solar), into Hackett - N Huntington 161 kV Line Tap | 1925000 | 100% | 1925000 | 1
GEN-2023-065 | DISIS-2023-001 | 03 CENTRAL | 158786 | ERIS | Halstead 69 kV Substation GEN-2023-065 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-065 (140MW/Battery/Storage), into Halstead 69 kV Substation | 949941 | 100% | 949941 | 1
GEN-2023-065 | DISIS-2023-001 | 03 CENTRAL | 158785 | ERIS | Halstead 69 kV Substation GEN-2023-065 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-065 (140MW/Battery/Storage), into Halstead 69 kV Substation | 897140 | 100% | 897140 | 1
GEN-2023-011 | DISIS-2023-001 | 02 NEBRASKA | 158695 | ERIS | Harbine 115 kV Substation GEN-2023-011 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-011 (190MW/Wind), into Harbine 115 kV Substation | 2300000 | 100% | 2300000 | 1
GEN-2023-011 | DISIS-2023-001 | 02 NEBRASKA | 158694 | ERIS | Harbine 115 kV Substation GEN-2023-011 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-011 (190MW/Wind), into Harbine 115 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | 158990 | ERIS | Hobbs - Ink Basin 230 kV Transmission Line GEN-2023-203 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-203 (300MW/Hybrid), into Hobbs - Ink Basin 230 kV Transmission Line | 25538381 | 100% | 25538381 | 1
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | 158989 | ERIS | Hobbs - Ink Basin 230 kV Transmission Line GEN-2023-203 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-203 (300MW/Hybrid), into Hobbs - Ink Basin 230 kV Transmission Line | 2989552 | 100% | 2989552 | 1
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | 159041 | ERIS | Hobbs - Yoakum 345 kV GEN-2023-236 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-236 (400MW/Solar), into Hobbs - Yoakum 345 kV | 42358867 | 100% | 42358867 | 1
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | 159040 | ERIS | Hobbs - Yoakum 345 kV GEN-2023-236 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-236 (400MW/Solar), into Hobbs - Yoakum 345 Kv | 3480128 | 100% | 3480128 | 1
GEN-2023-172 | DISIS-2023-001 | 03 CENTRAL | 158942 | ERIS | Holcomb 345 kV GEN-2023-172 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172 (200MW/Wind), into Holcomb 345 kV | 2718247 | 100% | 2718247 | 1
GEN-2023-173 | DISIS-2023-001 | 03 CENTRAL | 158943 | ERIS | Holcomb 345 kV GEN-2023-173 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-173 (100MW/Wind), into Holcomb 345 kV | 2718247 | 100% | 2718247 | 1
GEN-2023-172 | DISIS-2023-001 | 03 CENTRAL | 158666 | ERIS | Holcomb 345 kV Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172/173 (200/100MW/Wind), into Holcomb 345 kV | 6005658.67 | 66.67% | 9008488 | 1
GEN-2023-173 | DISIS-2023-001 | 03 CENTRAL | 158666 | ERIS | Holcomb 345 kV Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172/173 (200/100MW/Wind), into Holcomb 345 kV | 3002829.33 | 33.33% | 9008488 | 1
GEN-2023-009 | DISIS-2023-001 | 04 SOUTHEAST | 158691 | ERIS | Hugo 138 kV Substation GEN-2023-009 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-009 (250MW/Battery/Storage), into Hugo 138 kV Substation | 1200000 | 100% | 1200000 | 1
GEN-2023-009 | DISIS-2023-001 | 04 SOUTHEAST | 158690 | ERIS | Hugo 138 kV Substation GEN-2023-009 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-009 (250MW/Battery/Storage), into Hugo 138 kV Substation | 517000 | 100% | 517000 | 1
GEN-2023-099 | DISIS-2023-001 | 03 CENTRAL | 158838 | ERIS | Jeffery Energy Center 345 kV Substation GEN-2023-099 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-099 (300MW/Solar), into Jeffery Energy Center 345 kV Substation | $- | 100% | $- | 1
GEN-2023-099 | DISIS-2023-001 | 03 CENTRAL | 158837 | ERIS | Jeffery Energy Center 345 kV Substation GEN-2023-099 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-099 (300MW/Solar), into Jeffery Energy Center 345 kV Substation | 112910 | 100% | 112910 | 1
GEN-2023-132 | DISIS-2023-001 | 04 SOUTHEAST | 158875 | ERIS | Jonesboro - Independence 161 kV GEN-2023-132 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-132 (150MW/Solar), into Jonesboro - Independence 161 kV | 8600000 | 100% | 8600000 | 1
GEN-2023-132 | DISIS-2023-001 | 04 SOUTHEAST | 158874 | ERIS | Jonesboro - Independence 161 kV GEN-2023-132 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-132 (150MW/Solar), into Jonesboro - Independence 161 kV | 800000 | 100% | 800000 | 1
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | 158834 | ERIS | Judson 345 kV Substation GEN-2023-097 Interconnection (Non-Shared NU) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-097 (250MW/Battery/Storage), into Judson 345 kV Substation | 3197203 | 100% | 3197203 | 1
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | 158833 | ERIS | Judson 345 kV Substation GEN-2023-097 Interconnection (TOIF) (BEPC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-097 (250MW/Battery/Storage), into Judson 345 kV Substation | 3010423 | 100% | 3010423 | 1
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | 158769 | ERIS | Kerr Grove 161 kV GEN-2023-055 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-055 (100MW/Battery/Storage), into Kerr Grove 161 kV | 1750000 | 100% | 1750000 | 1
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | 158768 | ERIS | Kerr Grove 161 kV GEN-2023-055 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-055 (100MW/Battery/Storage), into Kerr Grove 161 kV | 2619247 | 100% | 2619247 | 1
GEN-2023-116 | DISIS-2023-001 | 02 NEBRASKA | 158859 | ERIS | Keystone 345 kV Substation GEN-2023-116 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-116 (500MW/Wind), into Keystone 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-117 | DISIS-2023-001 | 02 NEBRASKA | 158860 | ERIS | Keystone 345 kV Substation GEN-2023-117 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-117 (300MW/Wind), into Keystone 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-116 | DISIS-2023-001 | 02 NEBRASKA | 158667 | ERIS | Keystone 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-116/117 (500/300MW/Wind), into Keystone 345 kV Substation | 4687500 | 62.5% | 7500000 | 1
GEN-2023-117 | DISIS-2023-001 | 02 NEBRASKA | 158667 | ERIS | Keystone 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-116/117 (500/300MW/Wind), into Keystone 345 kV Substation | 2812500 | 37.5% | 7500000 | 1
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | 158697 | ERIS | Kingsbury County 115kV Substation GEN-2023-012 Interconnection (Non-Shared NU) (EREP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-012 (98.6MW/Wind), into Kingsbury County 115kV Substation | $- | 100% | $- | 1
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | 158696 | ERIS | Kingsbury County 115kV Substation GEN-2023-012 Interconnection (TOIF) (EREP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-012 (98.6MW/Wind), into Kingsbury County 115kV Substation | 5135000 | 100% | 5135000 | 1
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | 158863 | ERIS | Kress 115 kV Substation GEN-2023-120 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-120 (130MW/Solar), into Kress 115 kV Substation | 4967846 | 100% | 4967846 | 1
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | 158862 | ERIS | Kress 115 kV Substation GEN-2023-120 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-120 (130MW/Solar), into Kress 115 kV Substation | 2840814 | 100% | 2840814 | 1
GEN-2023-149 | DISIS-2023-001 | 03 CENTRAL | 158901 | ERIS | LaCygne - Stilwell 345 kV Line GEN-2023-149 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-149 (300MW/Battery/Storage), into LaCygne - Stilwell 345 kV Line | 33114559 | 100% | 33114559 | 1
GEN-2023-149 | DISIS-2023-001 | 03 CENTRAL | 158900 | ERIS | LaCygne - Stilwell 345 kV Line GEN-2023-149 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-149 (300MW/Battery/Storage), into LaCygne - Stilwell 345 kV Line | 1958092 | 100% | 1958092 | 1
GEN-2023-033 | DISIS-2023-001 | 03 CENTRAL | 158735 | ERIS | Liberty South 161 kV Substation GEN-2023-033 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-033 (200MW/Battery/Storage), into Liberty South 161 kV Substation | 1265759 | 100% | 1265759 | 1
GEN-2023-033 | DISIS-2023-001 | 03 CENTRAL | 158734 | ERIS | Liberty South 161 kV Substation GEN-2023-033 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-033 (200MW/Battery/Storage), into Liberty South 161 kV Substation | 940803 | 100% | 940803 | 1
GEN-2023-038 | DISIS-2023-001 | 04 SOUTHEAST | 158745 | ERIS | Lula 138 kV Substation GEN-2023-038 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-038 (200MW/Solar), into Lula 138 kV Substation | 2513699 | 100% | 2513699 | 1
GEN-2023-038 | DISIS-2023-001 | 04 SOUTHEAST | 158744 | ERIS | Lula 138 kV Substation GEN-2023-038 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-038 (200MW/Solar), into Lula 138 kV Substation | 3711456 | 100% | 3711456 | 1
GEN-2023-135 | DISIS-2023-001 | 04 SOUTHEAST | 158881 | ERIS | Lydia 345kV substation GEN-2023-135 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-135 (52MW/Solar), into Lydia 345kV substation | 171180 | 100% | 171180 | 1
GEN-2023-135 | DISIS-2023-001 | 04 SOUTHEAST | 158880 | ERIS | Lydia 345kV substation GEN-2023-135 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-135 (52MW/Solar), into Lydia 345kV substation | 206941 | 100% | 206941 | 1
GEN-2023-085 | DISIS-2023-001 | 03 CENTRAL | 158817 | ERIS | Mansfield - Logan 161 kV Line GEN-2023-085 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-085 (150MW/Wind), into Mansfield - Logan 161 kV Line | 8600000 | 100% | 8600000 | 1
GEN-2023-085 | DISIS-2023-001 | 03 CENTRAL | 158816 | ERIS | Mansfield - Logan 161 kV Line GEN-2023-085 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-085 (150MW/Wind), into Mansfield - Logan 161 kV Line | 800000 | 100% | 800000 | 1
GEN-2023-205 | DISIS-2023-001 | 04 SOUTHEAST | 158994 | ERIS | McAlester City - Weleetka 138 kV line GEN-2023-205 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-205 (180MW/Solar), into McAlester City - Weleetka 138 kV line | 11850000 | 100% | 11850000 | 1
GEN-2023-205 | DISIS-2023-001 | 04 SOUTHEAST | 158993 | ERIS | McAlester City - Weleetka 138 kV line GEN-2023-205 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-205 (180MW/Solar), into McAlester City - Weleetka 138 kV line | 1925000 | 100% | 1925000 | 1
GEN-2023-169 | DISIS-2023-001 | 03 CENTRAL | 158937 | ERIS | Missouri City - Liberty South 161 kV Line GEN-2023-169 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-169 (125MW/Battery/Storage), into Missouri City - Liberty South 161 kV Line | 17089522 | 100% | 17089522 | 1
GEN-2023-169 | DISIS-2023-001 | 03 CENTRAL | 158936 | ERIS | Missouri City - Liberty South 161 kV Line GEN-2023-169 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-169 (125MW/Battery/Storage), into Missouri City - Liberty South 161 kV Line | 1085688 | 100% | 1085688 | 1
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | 158693 | ERIS | Moore Co 230 kV Substation GEN-2023-010 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-010 (280MW/Wind), into Moore Co 230 kV Substation | 4930512 | 100% | 4930512 | 1
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | 158692 | ERIS | Moore Co 230 kV Substation GEN-2023-010 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-010 (280MW/Wind), into Moore Co 230 kV Substation | 2429360 | 100% | 2429360 | 1
GEN-2023-104 | DISIS-2023-001 | 04 SOUTHEAST | 158846 | ERIS | Mooreland - Noel 138 kV Line GEN-2023-104 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-104 (100MW/Hybrid), into Mooreland - Noel 138 kV Line | 6050000 | 100% | 6050000 | 1
GEN-2023-104 | DISIS-2023-001 | 04 SOUTHEAST | 158845 | ERIS | Mooreland - Noel 138 kV Line GEN-2023-104 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-104 (100MW/Hybrid), into Mooreland - Noel 138 kV Line | 517000 | 100% | 517000 | 1
GEN-2023-037 | DISIS-2023-001 | 03 CENTRAL | 158743 | ERIS | Nearman 161 kV Substation GEN-2023-037 Interconnection (Non-Shared NU) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-037 (200MW/Battery/Storage), into Nearman 161 kV Substation | 3357305 | 100% | 3357305 | 1
GEN-2023-037 | DISIS-2023-001 | 03 CENTRAL | 158742 | ERIS | Nearman 161 kV Substation GEN-2023-037 Interconnection (TOIF) (KACY) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-037 (200MW/Battery/Storage), into Nearman161 kV Substation | $- | 100% | $- | 1
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | 158918 | ERIS | Needmore - Yoakum 230 kV Line GEN-2023-158 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-158 (335MW/Solar), into Needmore - Yoakum 230 kV Line | 2989552 | 100% | 2989552 | 1
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | 158919 | ERIS | Needmore - Yoakum 230 kV Line GEN-2023-159 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-159 (170MW/Battery/Storage), into Needmore - Yoakum 230 kV Line | 2989552 | 100% | 2989552 | 1
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | 158669 | ERIS | Needmore - Yoakum 230 kV Line Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-158/159 (335/170MW/Solar/Battery/Storage), into Needmore - Yoakum 230 kV Line | 15991322.68 | 62.62% | 25538381 | 1
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | 158669 | ERIS | Needmore - Yoakum 230 kV Line Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-158/159 (335/170MW/Solar/Battery/Storage), into Needmore - Yoakum 230 kV Line | 9547058.32 | 37.38% | 25538381 | 1
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | 159037 | ERIS | Neosho - LaCynge 345 kV Line GEN-2023-231 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-231 (310MW/Hybrid), into Neosho - LaCynge 345 kV Line | 80302305 | 100% | 80302305 | 1
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | 159036 | ERIS | Neosho - LaCynge 345 kV Line GEN-2023-231 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-231 (310MW/Hybrid), into Neosho - LaCynge 345 kV Line | 1958090 | 100% | 1958090 | 1
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | 158760 | ERIS | Neosho 345 kV Substation GEN-2023-050 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-050 (400MW/Hybrid), into Neosho 345 kV Substation | 14476634 | 100% | 14476634 | 1
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | 158759 | ERIS | Neosho 345 kV Substation GEN-2023-050 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-050 (400MW/Hybrid), into Neosho 345 kV Substation | 1873996 | 100% | 1873996 | 1
GEN-2023-222 | DISIS-2023-001 | 02 NEBRASKA | 159022 | ERIS | New Beatrice Power Station 345 kV GEN-2023-222 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222 (478MW/Thermal), into New Beatrice Power Station 345 kV | 1000000 | 100% | 1000000 | 1
GEN-2023-223 | DISIS-2023-001 | 02 NEBRASKA | 159023 | ERIS | New Beatrice Power Station 345 kV GEN-2023-223 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-223 (239MW/Thermal), into New Beatrice Power Station 345 kV | 1000000 | 100% | 1000000 | 1
GEN-2023-222 | DISIS-2023-001 | 02 NEBRASKA | 158670 | ERIS | New Beatrice Power Station 345 kV Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222/223 (478/239MW/Thermal), into New Beatrice Power Station 345 kV | 38933333.33 | 66.67% | 58400000 | 1
GEN-2023-223 | DISIS-2023-001 | 02 NEBRASKA | 158670 | ERIS | New Beatrice Power Station 345 kV Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222/223 (478/239MW/Thermal), into New Beatrice Power Station 345 kV | 19466666.67 | 33.33% | 58400000 | 1
GEN-2023-212 | DISIS-2023-001 | 04 SOUTHEAST | 159008 | ERIS | Northwest TexarkaN/A - Valliant 345 kV Line GEN-2023-212 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-212 (400MW/Hybrid), into Northwest TexarkaN/A - Valliant 345 kV Line | 20000000 | 100% | 20000000 | 1
GEN-2023-212 | DISIS-2023-001 | 04 SOUTHEAST | 159007 | ERIS | Northwest TexarkaN/A - Valliant 345 kV Line GEN-2023-212 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-212 (400MW/Hybrid), into Northwest TexarkaN/A - Valliant 345 kV Line | 3475000 | 100% | 3475000 | 1
GEN-2023-032 | DISIS-2023-001 | 03 CENTRAL | 158733 | ERIS | Odessa and Lexington 161 kV Line GEN-2023-032 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-032 (200MW/Solar), into Odessa and Lexington 161 kV Line | 17300479 | 100% | 17300479 | 1
GEN-2023-032 | DISIS-2023-001 | 03 CENTRAL | 158732 | ERIS | Odessa and Lexington 161 kV Line GEN-2023-032 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-032 (200MW/Solar), into Odessa and Lexington 161 kV Line | 940803 | 100% | 940803 | 1
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | 158966 | ERIS | Oklaunion - Lawton 345 kV Line GEN-2023-188 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-188 (160MW/Hybrid), into Oklaunion - Lawton 345 kV Line | 20000000 | 100% | 20000000 | 1
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | 158965 | ERIS | Oklaunion - Lawton 345 kV Line GEN-2023-188 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-188 (160MW/Hybrid), into Oklaunion - Lawton 345 kV Line | 3475000 | 100% | 3475000 | 1
GEN-2023-224 | DISIS-2023-001 | 02 NEBRASKA | 159024 | ERIS | Olive Creek 345 kV Substation GEN-2023-224 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224 (478MW/Thermal), into Olive Creek 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-225 | DISIS-2023-001 | 02 NEBRASKA | 159025 | ERIS | Olive Creek 345 kV Substation GEN-2023-225 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-225 (217MW/Thermal), into Olive Creek 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-224 | DISIS-2023-001 | 02 NEBRASKA | 158671 | ERIS | Olive Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224/225 (478/217MW/Thermal), into Olive Creek 345 kV Substation | 76204892.09 | 68.78% | 110800000 | 1
GEN-2023-225 | DISIS-2023-001 | 02 NEBRASKA | 158671 | ERIS | Olive Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224/225 (478/217MW/Thermal), into Olive Creek 345 kV Substation | 34595107.91 | 31.22% | 110800000 | 1
GEN-2023-177 | DISIS-2023-001 | 04 SOUTHEAST | 158950 | ERIS | Paoli - Seminole 138 kV line tap GEN-2023-177 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-177 (200MW/Solar), into Paoli - Seminole 138 kV line tap | 7079843 | 100% | 7079843 | 1
GEN-2023-177 | DISIS-2023-001 | 04 SOUTHEAST | 158949 | ERIS | Paoli - Seminole 138 kV line tap GEN-2023-177 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-177 (200MW/Solar), into Paoli - Seminole 138 kV line tap | 3759390 | 100% | 3759390 | 1
GEN-2023-174 | DISIS-2023-001 | 04 SOUTHEAST | 158945 | ERIS | Paoli West 138 kV Substation GEN-2023-174 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-174 (150MW/Battery/Storage), into Paoli West 138 kV Substation | 12500000 | 100% | 12500000 | 1
GEN-2023-174 | DISIS-2023-001 | 04 SOUTHEAST | 158944 | ERIS | Paoli West 138 kV Substation GEN-2023-174 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-174 (150MW/Battery/Storage), into Paoli West 138 kV Substation | 517000 | 100% | 517000 | 1
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | 158773 | ERIS | Pawnee Switch 138 kV GEN-2023-057 Interconnection (Non-Shared NU) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-057 (150MW/Battery/Storage), into Pawnee Switch 138 kV | $- | 100% | $- | 1
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | 158772 | ERIS | Pawnee Switch 138 kV GEN-2023-057 Interconnection (TOIF) (GRDA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-057 (150MW/Battery/Storage), into Pawnee Switch 138 kV | 990399 | 100% | 990399 | 1
GEN-2023-227 | DISIS-2023-001 | 04 SOUTHEAST | 159029 | ERIS | Petty to Chapel 138 kV Line GEN-2023-227 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-227 (200MW/Battery/Storage), into Petty to Chapel 138 kV Line | 11850000 | 100% | 11850000 | 1
GEN-2023-227 | DISIS-2023-001 | 04 SOUTHEAST | 159028 | ERIS | Petty to Chapel 138 kV Line GEN-2023-227 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-227 (200MW/Battery/Storage), into Petty to Chapel 138 kV Line | 1925000 | 100% | 1925000 | 1
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | 158960 | ERIS | Phantom 115 kV Substation GEN-2023-184 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-184 (200MW/Solar), into Phantom 115 kV Substation | 1035860 | 100% | 1035860 | 1
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | 158959 | ERIS | Phantom 115 kV Substation GEN-2023-184 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-184 (200MW/Solar), into Phantom 115 kV Substation | 2683685 | 100% | 2683685 | 1
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | 158823 | ERIS | Pharaoh 138 kV Substation GEN-2023-088 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-088 (117MW/Wind), into Pharaoh 138 kV Substation | 1200000 | 100% | 1200000 | 1
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | 158822 | ERIS | Pharaoh 138 kV Substation GEN-2023-088 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-088 (117MW/Wind), into Pharaoh 138 kV Substation | 517000 | 100% | 517000 | 1
GEN-2023-193 | DISIS-2023-001 | 04 SOUTHEAST | 158972 | ERIS | Pirkey - Whitney 138 kV Line GEN-2023-193 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-193 (175MW/Hybrid), into Pirkey - Whitney 138 kV Line | 11850000 | 100% | 11850000 | 1
GEN-2023-193 | DISIS-2023-001 | 04 SOUTHEAST | 158971 | ERIS | Pirkey - Whitney 138 kV Line GEN-2023-193 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-193 (175MW/Hybrid), into Pirkey - Whitney 138 kV Line | 2125000 | 100% | 2125000 | 1
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | 158685 | ERIS | Plant X 230 kV Substation GEN-2023-005 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005 (256MW/Solar), into Plant X 230kV Substation | 4249032 | 100% | 4249032 | 1
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | 158776 | ERIS | Plant X 230 kV Substation GEN-2023-060 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-060 (256MW/Solar), into Plant X 230kV Substation | 4249032 | 100% | 4249032 | 1
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | 158888 | ERIS | Plant X 230 kV Substation GEN-2023-142 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-142 (275MW/Solar), into Plant X 230 kV Substation | 4249032 | 100% | 4249032 | 1
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | 158889 | ERIS | Plant X 230 kV Substation GEN-2023-143 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-143 (200MW/Battery/Storage), into Plant X 230 kV Substation | 4249032 | 100% | 4249032 | 1
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | 158948 | ERIS | Plant X 230 kV Substation GEN-2023-176 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-176 (300MW/Wind), into Plant X 230 kV Substation | 4249032 | 100% | 4249032 | 1
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | 158672 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | 6267932.44 | 19.89% | 31511051 | 1
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | 158672 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | 6267932.44 | 19.89% | 31511051 | 1
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | 158672 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | 6733130.56 | 21.37% | 31511051 | 1
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | 158672 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | 4896822.22 | 15.54% | 31511051 | 1
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | 158672 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | 7345233.33 | 23.31% | 31511051 | 1
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | 158819 | ERIS | Potter - Newhart 230 kV line GEN-2023-086 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-086 (300MW/Hybrid), into Potter - Newhart 230 kV line | 25538381 | 100% | 25538381 | 1
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | 158818 | ERIS | Potter - Newhart 230 kV line GEN-2023-086 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-086 (300MW/Hybrid), into Potter - Newhart 230 kV line | 2989552 | 100% | 2989552 | 1
GEN-2023-210 | DISIS-2023-001 | 04 SOUTHEAST | 159004 | ERIS | Prague - Chernicky 138 kV Line GEN-2023-210 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-210 (191MW/Solar), into Prague - Chernicky 138 kV Line | 6050000 | 100% | 6050000 | 1
GEN-2023-210 | DISIS-2023-001 | 04 SOUTHEAST | 159003 | ERIS | Prague - Chernicky 138 kV Line GEN-2023-210 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-210 (191MW/Solar), into Prague - Chernicky 138 kV Line | 517000 | 100% | 517000 | 1
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | 158869 | ERIS | Pringle Interchange 230 kV Substation GEN-2023-123 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-123 (285MW/Wind), into Pringle Interchange 230 kV Substation | 7205502 | 100% | 7205502 | 1
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | 158868 | ERIS | Pringle Interchange 230 kV Substation GEN-2023-123 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-123 (285MW/Wind), into Pringle Interchange 230 kV Substation | 3656888 | 100% | 3656888 | 1
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | 159006 | ERIS | Ranch Road 345 kV Substation GEN-2023-211 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-211 (250MW/Hybrid), into Ranch Road 345 kV Substation | 30000 | 100% | 30000 | 1
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | 159005 | ERIS | Ranch Road 345 kV Substation GEN-2023-211 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-211 (250MW/Hybrid), into Ranch Road 345 kV Substation | 100000 | 100% | 100000 | 1
GEN-2023-219 | DISIS-2023-001 | 03 CENTRAL | 159017 | ERIS | Reading - Osage Jct 115 kV Line GEN-2023-219 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-219 (125MW/Solar), into Reading - Osage Jct 115 kV Line | 14414502 | 100% | 14414502 | 1
GEN-2023-219 | DISIS-2023-001 | 03 CENTRAL | 159016 | ERIS | Reading - Osage Jct 115 kV Line GEN-2023-219 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-219 (125MW/Solar), into Reading - Osage Jct 115 kV Line | 927366 | 100% | 927366 | 1
GEN-2023-230 | DISIS-2023-001 | 04 SOUTHEAST | 159035 | ERIS | Red Pointe 138 kV Substation GEN-2023-230 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-230 (150MW/Hybrid), into Red Pointe 138 kV Substation | 3338007 | 100% | 3338007 | 1
GEN-2023-230 | DISIS-2023-001 | 04 SOUTHEAST | 159034 | ERIS | Red Pointe 138 kV Substation GEN-2023-230 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-230 (150MW/Hybrid), into Red Pointe 138 kV Substation | 2575383 | 100% | 2575383 | 1
GEN-2023-062 | DISIS-2023-001 | 01 NORTH | 158780 | ERIS | REN 115 kV Substation GEN-2023-062 Interconnection (Non-Shared NU) (LYREC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-062 (98MW/Thermal), into REN 115 kV Substation | 4940802 | 100% | 4940802 | 1
GEN-2023-062 | DISIS-2023-001 | 01 NORTH | 158779 | ERIS | REN 115 kV Substation GEN-2023-062 Interconnection (TOIF) (LYREC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-062 (98MW/Thermal), into REN 115 kV Substation | 407172 | 100% | 407172 | 1
GEN-2023-194 | DISIS-2023-001 | 03 CENTRAL | 158974 | ERIS | Riverton - Neosho 161 kV Line Tap GEN-2023-194 Interconnection (Non-Shared NU) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-194 (225MW/Solar), into Riverton - Neosho 161 kV Line Tap (sharing the gen-tie with GEN-2020-079) | 2368711.8 | 100% | 2368711.8 | 1
GEN-2023-194 | DISIS-2023-001 | 03 CENTRAL | 158973 | ERIS | Riverton - Neosho 161 kV Line Tap GEN-2023-194 Interconnection (TOIF) (EDE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-194 (225MW/Solar), into Riverton - Neosho 161 kV Line Tap (sharing the gen-tie with GEN-2020-079) | $- | 100% | $- | 1
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | 159000 | ERIS | Rolling Hills 115 kV GEN-2023-208 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-208 (200MW/Battery/Storage), into Rolling Hills 115 kV | 1743672 | 100% | 1743672 | 1
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | 158999 | ERIS | Rolling Hills 115 kV GEN-2023-208 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-208 (200MW/Battery/Storage), into Rolling Hills 115 kV | 2165031 | 100% | 2165031 | 1
GEN-2023-161 | DISIS-2023-001 | 04 SOUTHEAST | 158923 | ERIS | Roman Nose 138 kV Substation GEN-2023-161 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-161 (74.9MW/Battery/Storage), into Roman Nose 138 kV Substation | 1502516 | 100% | 1502516 | 1
GEN-2023-161 | DISIS-2023-001 | 04 SOUTHEAST | 158922 | ERIS | Roman Nose 138 kV Substation GEN-2023-161 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-161 (74.9MW/Battery/Storage), into Roman Nose 138 kV Substation | 1764041 | 100% | 1764041 | 1
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | 158975 | ERIS | Roosevelt - Tolk 230 kV line tap GEN-2023-195 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-195 (250MW/Solar), into Roosevelt - Tolk 230 kV line tap | 2989552 | 100% | 2989552 | 1
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | 158673 | ERIS | Roosevelt - Tolk 230 kV line tap Interconnection (DISIS-2023-001) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-195 (250/Solar), into Roosevelt - Tolk 230 kV line tap | 25797424 | 100% | 25797424 | 1
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | 158952 | ERIS | Roosevelt 230kV Substation GEN-2023-178 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-178 (200MW/Solar), into Roosevelt 230kV Substation | $- | 100% | $- | 1
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | 158951 | ERIS | Roosevelt 230kV Substation GEN-2023-178 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-178 (200MW/Solar), into Roosevelt 230kV Substation | $- | 100% | $- | 1
GEN-2023-073 | DISIS-2023-001 | 03 CENTRAL | 158800 | ERIS | Rose Hill 345 kV Substation GEN-2023-073 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-073 250MW/Battery/Storage), into Rose Hill 345 kV Substation | 1958090 | 100% | 1958090 | 1
GEN-2023-073 | DISIS-2023-001 | 03 CENTRAL | 158674 | ERIS | Rose Hill 345 kV Substation Interconnection GEN-2023-073 (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-073 250MW/Battery/Storage), into Rose Hill 345 kV Substation | 16154742 | 100% | 16154742 | 1
GEN-2023-064 | DISIS-2023-001 | 04 SOUTHEAST | 158784 | ERIS | RS Kerr-Stigler 161 kV line GEN-2023-064 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-064 (200MW/Hybrid), into RS Kerr-Stigler 161 kV line | 8600000 | 100% | 8600000 | 1
GEN-2023-064 | DISIS-2023-001 | 04 SOUTHEAST | 158783 | ERIS | RS Kerr-Stigler 161 kV line GEN-2023-064 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-064 (200MW/Hybrid), into RS Kerr-Stigler 161 kV line | 800000 | 100% | 800000 | 1
GEN-2023-170 | DISIS-2023-001 | 03 CENTRAL | 158939 | ERIS | Salisbury 161 kV Substation GEN-2023-170 Interconnection (Non-Shared NU) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-170 (150MW/Battery/Storage), into Salisbury 161 kV Substation | 6267996 | 100% | 6267996 | 1
GEN-2023-170 | DISIS-2023-001 | 03 CENTRAL | 158938 | ERIS | Salisbury 161 kV Substation GEN-2023-170 Interconnection (TOIF) (Evergy) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-170 (150MW/Battery/Storage), into Salisbury 161 kV Substation | 1085688 | 100% | 1085688 | 1
GEN-2023-107 | DISIS-2023-001 | 03 CENTRAL | 158849 | ERIS | Setab 345 kV Substation GEN-2023-107 Interconnection (TOIF) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-107 (300MW/Wind), into Setab 345 kV | 2206495 | 100% | 2206495 | 1
GEN-2023-107 | DISIS-2023-001 | 03 CENTRAL | 158675 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-107 (300MW/Wind), into Setab 345 kV Substation | 5338489 | 100% | 5338489 | 1
GEN-2023-151 | DISIS-2023-001 | 04 SOUTHEAST | 158905 | ERIS | South N/Ashville - South Murfreesboro 138kV GEN-2023-151 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-151 (100MW/Hybrid), into South N/Ashville - South Murfreesboro 138kV | 11850000 | 100% | 11850000 | 1
GEN-2023-151 | DISIS-2023-001 | 04 SOUTHEAST | 158904 | ERIS | South N/Ashville - South Murfreesboro 138kV GEN-2023-151 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-151 (100MW/Hybrid), into South N/Ashville - South Murfreesboro 138kV | 2125000 | 100% | 2125000 | 1
GEN-2023-229 | DISIS-2023-001 | 04 SOUTHEAST | 159033 | ERIS | Southwestern Power Station 138 kV Sub (SWS4) GEN-2023-229 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-229 (230MW/Wind), into Southwestern Power Station 138 kV Substation (SWS4) | 3553691 | 100% | 3553691 | 1
GEN-2023-229 | DISIS-2023-001 | 04 SOUTHEAST | 159032 | ERIS | Southwestern Power Station 138 kV Substation (SWS4) GEN-2023-229 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-229 (230MW/Wind), into Southwestern Power Station 138 kV Substation (SWS4) | 2164113 | 100% | 2164113 | 1
GEN-2023-171 | DISIS-2023-001 | 03 CENTRAL | 158941 | ERIS | Sub M 161 kV Substation GEN-2023-171 Interconnection (Non-Shared NU) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-171 (150MW/Battery/Storage), into Sub M 161 kV Substation | 3280000 | 100% | 3280000 | 1
GEN-2023-171 | DISIS-2023-001 | 03 CENTRAL | 158940 | ERIS | Sub M 161 kV Substation GEN-2023-171 Interconnection (TOIF) (INDN) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-171 (150MW/Battery/Storage), into Sub M 161 kV Substation. | 500000 | 100% | 500000 | 1
GEN-2023-077 | DISIS-2023-001 | 02 NEBRASKA | 158803 | ERIS | Substation 3740 345 kV GEN-2023-077 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077 (255MW/Thermal), into Substation 3740 345 kV | 3348775 | 100% | 3348775 | 1
GEN-2023-078 | DISIS-2023-001 | 02 NEBRASKA | 158804 | ERIS | Substation 3740 345 kV GEN-2023-078 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-078 (255MW/Thermal), into Substation 3740 345 kV | 3004365 | 100% | 3004365 | 1
GEN-2023-079 | DISIS-2023-001 | 02 NEBRASKA | 158805 | ERIS | Substation 3740 345 kV GEN-2023-079 Interconnection (TOIF) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-079 (303MW/Thermal), into Substation 3740 345 kV | 3004365 | 100% | 3004365 | 1
GEN-2023-077 | DISIS-2023-001 | 02 NEBRASKA | 158676 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (255MW/255MW/303MW/Thermal), into Substation 3740 345 kV | 13709162 | 33.33% | 41127486 | 1
GEN-2023-078 | DISIS-2023-001 | 02 NEBRASKA | 158676 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (255MW/255MW/303MW/Thermal), into Substation 3740 345 kV | 13709162 | 33.33% | 41127486 | 1
GEN-2023-079 | DISIS-2023-001 | 02 NEBRASKA | 158676 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (255MW/255MW/303MW/Thermal), into Substation 3740 345 kV | 13709162 | 33.33% | 41127486 | 1
GEN-2023-133 | DISIS-2023-001 | 02 NEBRASKA | 158877 | ERIS | Sweetwater 345 kV Substation GEN-2023-133 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-133 (250MW/Wind), into Sweetwater 345 kV Substation | 100000 | 100% | 100000 | 1
GEN-2023-133 | DISIS-2023-001 | 02 NEBRASKA | 158876 | ERIS | Sweetwater 345 kV Substation GEN-2023-133 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-133 (250MW/Wind), into Sweetwater 345 kV Substation | $- | 100% | $- | 1
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | 158680 | ERIS | T14 Circuit 115 V Line GEN-2023-001 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-001 (230MW/Solar), into T14 Circuit 115 V Line (sharing the gen-tie with GEN-2018-004) | $- | 100% | $- | 1
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | 158679 | ERIS | T14 Circuit 115 V Line GEN-2023-001 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-001 (230MW/Solar), into T14 Circuit 115 V Line (sharing the gen-tie with GEN-2018-004) | $- | 100% | $- | 1
GEN-2023-030 | DISIS-2023-001 | 04 SOUTHEAST | 158728 | ERIS | Tap between 345 kV SW Shreveport-Dolet Hills Subs GEN-2023-030 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-030 (25MW/Solar), into Tap between 345 kV SW Shreveport-Dolet Hills Subs | 206941 | 100% | 206941 | 1
GEN-2023-030 | DISIS-2023-001 | 04 SOUTHEAST | 158729 | ERIS | Tap between 345 kV SW Shreveport-Dolet Hills SubsGEN-2023-030 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-030 (25MW/Solar), into Tap between 345 kV SW Shreveport-Dolet Hills Subs | 171180 | 100% | 171180 | 1
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | 158853 | ERIS | Tap Border to Tuco 345 kV Line GEN-2023-110 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-110 (250MW/Solar), into Tap Border to Tuco 345 kV Line | 47223747 | 100% | 47223747 | 1
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | 158852 | ERIS | Tap Border to Tuco 345 kV Line GEN-2023-110 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-110 (250MW/Solar), into Tap Border to Tuco 345 kV Line | 3480128 | 100% | 3480128 | 1
GEN-2023-059 | DISIS-2023-001 | 04 SOUTHEAST | 158775 | ERIS | Tap Rockhill to South Shreveport 138 kV line GEN-2023-059 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-059 (200MW/Hybrid), into Tap Rockhill to South Shreveport 138 kV line | 11850000 | 100% | 11850000 | 1
GEN-2023-059 | DISIS-2023-001 | 04 SOUTHEAST | 158774 | ERIS | Tap Rockhill to South Shreveport 138 kV line GEN-2023-059 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-059 (200MW/Hybrid), into Tap Rockhill to South Shreveport 138 kV line | 2125000 | 100% | 2125000 | 1
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | 158841 | ERIS | Tap Stateline Demarc - Wheeler 230 kV Line GEN-2023-101 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-101 (150MW/Hybrid), into Tap Stateline Demarc - Wheeler 230 kV Line | 25538381 | 100% | 25538381 | 1
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | 158840 | ERIS | Tap Stateline Demarc - Wheeler 230 kV Line GEN-2023-101 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-101 (150MW/Hybrid), into Tap Stateline Demarc - Wheeler 230 kV Line | 2989552 | 100% | 2989552 | 1
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | 158689 | ERIS | Tuco - Carlisle 230 kV line GEN-2023-008 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-008 (75MW/Solar), into Tuco - Carlisle 230 kV line | 25538381 | 100% | 25538381 | 1
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | 158688 | ERIS | Tuco - Carlisle 230 kV line GEN-2023-008 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-008 (75MW/Solar), into Tuco - Carlisle 230 kV line | 2989552 | 100% | 2989552 | 1
GEN-2023-183 | DISIS-2023-001 | 05 SOUTHWEST | 158958 | ERIS | Tuco 345kV GEN-2023-183 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-183 (217MW/Thermal), into Tuco 345kV | $- | 100% | $- | 1
GEN-2023-183 | DISIS-2023-001 | 05 SOUTHWEST | 158957 | ERIS | Tuco 345kV GEN-2023-183 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-183 (217MW/Thermal), into Tuco 345kV | $- | 100% | $- | 1
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | 159031 | ERIS | Tuco-Okalunion 345 kV line GEN-2023-228 Interconnection (Non-Shared NU) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-228 (250MW/Battery/Storage), into Tuco-Okalunion 345 kV line | $- | 100% | $- | 1
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | 159030 | ERIS | Tuco-Okalunion 345 kV line GEN-2023-228 Interconnection (TOIF) (SPS) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-228 (250MW/Battery/Storage), into Tuco-Okalunion 345 kV line | $- | 100% | $- | 1
GEN-2023-069 | DISIS-2023-001 | 04 SOUTHEAST | 158793 | ERIS | Tupelo - Atoka 138 kV Line GEN-2023-069 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-069 (100MW/Hybrid), into Tupelo - Atoka 138 kV Line | 6050000 | 100% | 6050000 | 1
GEN-2023-069 | DISIS-2023-001 | 04 SOUTHEAST | 158792 | ERIS | Tupelo - Atoka 138 kV Line GEN-2023-069 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-069 (100MW/Hybrid), into Tupelo - Atoka 138 kV Line | 517000 | 100% | 517000 | 1
GEN-2023-216 | DISIS-2023-001 | 02 NEBRASKA | 159013 | ERIS | Turtle Creek 345 kV Substation GEN-2023-216 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216 (200MW/Wind), into Turtle Creek 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-217 | DISIS-2023-001 | 02 NEBRASKA | 159014 | ERIS | Turtle Creek 345 kV Substation GEN-2023-217 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-217 (200MW/Wind), into Turtle Creek 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-218 | DISIS-2023-001 | 02 NEBRASKA | 159015 | ERIS | Turtle Creek 345 kV Substation GEN-2023-218 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-218 (200MW/Wind), into Turtle Creek 345 kV Substation | 1000000 | 100% | 1000000 | 1
GEN-2023-216 | DISIS-2023-001 | 02 NEBRASKA | 158678 | ERIS | Turtle Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216/217/218 (200MW/Wind), into Turtle Creek 345 kV Substation | 3900000 | 33.33% | 11700000 | 1
GEN-2023-217 | DISIS-2023-001 | 02 NEBRASKA | 158678 | ERIS | Turtle Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216/217/218 (200MW/Wind), into Turtle Creek 345 kV Substation | 3900000 | 33.33% | 11700000 | 1
GEN-2023-218 | DISIS-2023-001 | 02 NEBRASKA | 158678 | ERIS | Turtle Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216/217/218 (200MW/Wind), into Turtle Creek 345 kV Substation | 3900000 | 33.33% | 11700000 | 1
GEN-2023-199 | DISIS-2023-001 | 02 NEBRASKA | 158982 | ERIS | Twin Church 230 kV Substation GEN-2023-199 Interconnection (Non-Shared NU) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-199 (250MW/Hybrid), into Twin Church 230 kV Substation | 1200000 | 100% | 1200000 | 1
GEN-2023-199 | DISIS-2023-001 | 02 NEBRASKA | 158981 | ERIS | Twin Church 230 kV Substation GEN-2023-199 Interconnection (TOIF) (NPPD) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-199 (250MW/Hybrid), into Twin Church 230 kV Substation | 500000 | 100% | 500000 | 1
GEN-2023-092 | DISIS-2023-001 | 04 SOUTHEAST | 158828 | ERIS | Unger - Frogville 138 kV line GEN-2023-092 Interconnection (Non-Shared NU) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-092 (125MW/Hybrid), into Unger - Frogville 138 kV line | 6050000 | 100% | 6050000 | 1
GEN-2023-092 | DISIS-2023-001 | 04 SOUTHEAST | 158827 | ERIS | Unger - Frogville 138 kV line GEN-2023-092 Interconnection (TOIF) (WFEC) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-092 (125MW/Hybrid), into Unger - Frogville 138 kV line | 517000 | 100% | 517000 | 1
GEN-2023-056 | DISIS-2023-001 | 04 SOUTHEAST | 158771 | ERIS | Van Buren 161 kV GEN-2023-056 Interconnection (Non-Shared NU) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-056 (150MW/Battery/Storage), into Van Buren 161 kV | 4400000 | 100% | 4400000 | 1
GEN-2023-056 | DISIS-2023-001 | 04 SOUTHEAST | 158770 | ERIS | Van Buren 161 kV GEN-2023-056 Interconnection (TOIF) (SWPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-056 (150MW/Battery/Storage), into Van Buren 161 kV | 775000 | 100% | 775000 | 1
GEN-2023-167 | DISIS-2023-001 | 04 SOUTHEAST | 158933 | ERIS | Washington Park 138 kV Substation GEN-2023-167 Interconnection (Non-Shared NU) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-167 (250MW/Battery/Storage), into Washington Park 138 kV Substation | 1069049 | 100% | 1069049 | 1
GEN-2023-167 | DISIS-2023-001 | 04 SOUTHEAST | 158932 | ERIS | Washington Park 138 kV Substation GEN-2023-167 Interconnection (TOIF) (OGE) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-167 (250MW/Battery/Storage), into Washington Park 138 kV Substation | 1458153 | 100% | 1458153 | 1
GEN-2023-204 | DISIS-2023-001 | 04 SOUTHEAST | 158992 | ERIS | Welsh-Lydia 345kV Line GEN-2023-204 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-204 (953MW/Thermal), into Welsh-Lydia 345kV Line | 20000000 | 100% | 20000000 | 1
GEN-2023-204 | DISIS-2023-001 | 04 SOUTHEAST | 158991 | ERIS | Welsh-Lydia 345kV Line GEN-2023-204 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-204 (953MW/Thermal), into Welsh-Lydia 345kV Line | 3275000 | 100% | 3275000 | 1
GEN-2023-082 | DISIS-2023-001 | 01 NORTH | 158811 | ERIS | White 115 kV Substation GEN-2023-082 Interconnection (Non-Shared NU) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-082 (175MW/Battery/Storage), into White 115 kV Substation | $- | 100% | $- | 1
GEN-2023-082 | DISIS-2023-001 | 01 NORTH | 158810 | ERIS | White 115 kV Substation GEN-2023-082 Interconnection (TOIF) (WAPA) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-082 (175MW/Battery/Storage), into White 115 kV Substation | 4790000 | 100% | 4790000 | 1
GEN-2023-241 | DISIS-2023-001 | 04 SOUTHEAST | 159051 | ERIS | Winnsboro 138 kV Substation GEN-2023-241 Interconnection (Non-Shared NU) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-241 (93MW/Solar), into Winnsboro 138 kV Substation | 4107515 | 100% | 4107515 | 1
GEN-2023-241 | DISIS-2023-001 | 04 SOUTHEAST | 159050 | ERIS | Winnsboro 138 kV Substation GEN-2023-241 Interconnection (TOIF) (AEP) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-241 (93MW/Solar), into Winnsboro 138 kV Substation | 2327363 | 100% | 2327363 | 1
GEN-2023-006 | DISIS-2023-001 | 03 CENTRAL | 158687 | ERIS | Wolf Creek- Blackberry 345 kV Line Break GEN-2023-006 Interconnection (Non-Shared NU) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-006 (202MW/Wind), into Wolf Creek- Blackberry 345 kV Line Break | 26745964 | 100% | 26745964 | 1
GEN-2023-006 | DISIS-2023-001 | 03 CENTRAL | 158686 | ERIS | Wolf Creek- Blackberry 345 kV Line Break GEN-2023-006 Interconnection (TOIF) (NEET) | Interconnection | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-006 (202MW/Wind), into Wolf Creek- Blackberry 345 kV Line Break | $- | 100% | $- | 1
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | AFTON2 to FAIRTAP2 69 kV Ckt 1 Terminal Upgrade | Current Study | Upgrade Terminal Equipment on the AFTON2 to FAIRTAP line Ckt 1 to achieve a rating of 157 MVA | 96540.34 | 56.68% | 170340 | 0.01551
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | AFTON2 to FAIRTAP2 69 kV Ckt 1 Terminal Upgrade | Current Study | Upgrade Terminal Equipment on the AFTON2 to FAIRTAP line Ckt 1 to achieve a rating of 157 MVA | 73799.66 | 43.32% | 170340 | 0.01818
GEN-2023-038 | DISIS-2023-001 | 04 SOUTHEAST | TBD | NRIS | Brown Substation Expansion | Current Study | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation Upgrade BROWN Substation to a breaker-and-a-half configuration. | 8272590.93 | 44.94% | 18406321 | 0.05335
GEN-2023-069 | DISIS-2023-001 | 04 SOUTHEAST | TBD | NRIS | Brown Substation Expansion | Current Study | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation Upgrade BROWN Substation to a breaker-and-a-half configuration. | 3781977.37 | 20.55% | 18406321 | 0.04878
GEN-2023-092 | DISIS-2023-001 | 04 SOUTHEAST | TBD | NRIS | Brown Substation Expansion | Current Study | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation Upgrade BROWN Substation to a breaker-and-a-half configuration. | 6351752.69 | 34.51% | 18406321 | 0.06554
GEN-2023-219 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | Current Study | Build a 2nd LANG 3 to G22-007-TAP 115 kV line (0.41mi approx.) | 22000000 | 100% | 22000000 | 0.35677
GEN-2023-011 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new 30MVAR Switched Shunt at RUBART 3 115kV | Current Study | Install a new 30 MVAR Switched Shunt at RUBART 3 115kV | 302772.32 | 7.569% | 4000000 | 0.00073
GEN-2023-116 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new 30MVAR Switched Shunt at RUBART 3 115kV | Current Study | Install a new 30 MVAR Switched Shunt at RUBART 3 115kV | 1069635.45 | 26.74% | 4000000 | 0.00098
GEN-2023-117 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new 30MVAR Switched Shunt at RUBART 3 115kV | Current Study | Install a new 30 MVAR Switched Shunt at RUBART 3 115kV | 641781.27 | 16.04% | 4000000 | 0.00098
GEN-2023-133 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new 30MVAR Switched Shunt at RUBART 3 115kV | Current Study | Install a new 30 MVAR Switched Shunt at RUBART 3 115kV | 540275.05 | 13.51% | 4000000 | 0.00099
GEN-2023-153 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new 30MVAR Switched Shunt at RUBART 3 115kV | Current Study | Install a new 30 MVAR Switched Shunt at RUBART 3 115kV | 225278.32 | 5.632% | 4000000 | 0.00086
GEN-2023-199 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new 30MVAR Switched Shunt at RUBART 3 115kV | Current Study | Install a new 30 MVAR Switched Shunt at RUBART 3 115kV | 316524.78 | 7.913% | 4000000 | 0.00058
GEN-2023-216 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new 30MVAR Switched Shunt at RUBART 3 115kV | Current Study | Install a new 30 MVAR Switched Shunt at RUBART 3 115kV | 301244.27 | 7.531% | 4000000 | 0.00069
GEN-2023-217 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new 30MVAR Switched Shunt at RUBART 3 115kV | Current Study | Install a new 30 MVAR Switched Shunt at RUBART 3 115kV | 301244.27 | 7.531% | 4000000 | 0.00069
GEN-2023-218 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new 30MVAR Switched Shunt at RUBART 3 115kV | Current Study | Install a new 30 MVAR Switched Shunt at RUBART 3 115kV | 301244.27 | 7.531% | 4000000 | 0.00069
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 18734.7238 | 0.2882% | 6500000 | 0.00226
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 204962.8526 | 3.153% | 6500000 | 0.00215
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 220704.9944 | 3.395% | 6500000 | 0.00208
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 55644.6167 | 0.8561% | 6500000 | 0.00179
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 341204.0854 | 5.249% | 6500000 | 0.00294
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 220704.9944 | 3.395% | 6500000 | 0.00208
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 577688.5253 | 8.888% | 6500000 | 0.00223
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 294698.8639 | 4.534% | 6500000 | 0.00237
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 131806.2429 | 2.028% | 6500000 | 0.00106
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 112532.6885 | 1.731% | 6500000 | 0.00181
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 208693.2179 | 3.211% | 6500000 | 0.00106
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 192735.5439 | 2.965% | 6500000 | 0.00186
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 112615.5855 | 1.733% | 6500000 | 0.00209
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 316583.674 | 4.871% | 6500000 | 0.00268
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 237085.4432 | 3.647% | 6500000 | 0.00208
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 172425.7769 | 2.653% | 6500000 | 0.00208
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 284647.6016 | 4.379% | 6500000 | 0.00205
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 144448.0366 | 2.222% | 6500000 | 0.00205
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 258638.6653 | 3.979% | 6500000 | 0.00208
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 172425.7769 | 2.653% | 6500000 | 0.00208
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 187347.2383 | 2.882% | 6500000 | 0.00226
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 89528.7688 | 1.377% | 6500000 | 0.00135
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 214496.0085 | 3.3% | 6500000 | 0.00207
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 273560.1268 | 4.209% | 6500000 | 0.0022
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 262369.0307 | 4.036% | 6500000 | 0.00211
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 203926.64 | 3.137% | 6500000 | 0.00246
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 125381.7248 | 1.929% | 6500000 | 0.00242
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 156468.1028 | 2.407% | 6500000 | 0.00151
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 359773.0152 | 5.535% | 6500000 | 0.00217
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | Current Study | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | 348167.4341 | 5.356% | 6500000 | 0.00168
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Current Study | Build a new switched shunt at HANLON1-ER8 69 kV with a capacity of 7.5 MVAR; Build a new switched shunt at HANLON2-ER8 69 kV with a capacity of 7.5 MVAR | 45045.99 | 5.507% | 818000 | 0.11944
GEN-2023-082 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Current Study | Build a new switched shunt at HANLON1-ER8 69 kV with a capacity of 7.5 MVAR; Build a new switched shunt at HANLON2-ER8 69 kV with a capacity of 7.5 MVAR | 64781.81 | 7.92% | 818000 | 0.09678
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Current Study | Build a new switched shunt at HANLON1-ER8 69 kV with a capacity of 7.5 MVAR; Build a new switched shunt at HANLON2-ER8 69 kV with a capacity of 7.5 MVAR | 140759.34 | 17.21% | 818000 | 0.1472
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Current Study | Build a new switched shunt at HANLON1-ER8 69 kV with a capacity of 7.5 MVAR; Build a new switched shunt at HANLON2-ER8 69 kV with a capacity of 7.5 MVAR | 278649.67 | 34.06% | 818000 | 0.29257
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Current Study | Build a new switched shunt at HANLON1-ER8 69 kV with a capacity of 7.5 MVAR; Build a new switched shunt at HANLON2-ER8 69 kV with a capacity of 7.5 MVAR | 134838.27 | 16.48% | 818000 | 0.20144
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Current Study | Build a new switched shunt at HANLON1-ER8 69 kV with a capacity of 7.5 MVAR; Build a new switched shunt at HANLON2-ER8 69 kV with a capacity of 7.5 MVAR | 153924.93 | 18.82% | 818000 | 0.13414
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV | Current Study | Build a new switched shunt at PUKWANA-ER8 69 kV with a capacity of 7.5 MVAR | 22522.99 | 5.507% | 409000 | 0.11944
GEN-2023-082 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV | Current Study | Build a new switched shunt at PUKWANA-ER8 69 kV with a capacity of 7.5 MVAR | 32390.9 | 7.92% | 409000 | 0.09678
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV | Current Study | Build a new switched shunt at PUKWANA-ER8 69 kV with a capacity of 7.5 MVAR | 70379.67 | 17.21% | 409000 | 0.1472
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV | Current Study | Build a new switched shunt at PUKWANA-ER8 69 kV with a capacity of 7.5 MVAR | 139324.84 | 34.06% | 409000 | 0.29257
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV | Current Study | Build a new switched shunt at PUKWANA-ER8 69 kV with a capacity of 7.5 MVAR | 67419.13 | 16.48% | 409000 | 0.20144
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV | Current Study | Build a new switched shunt at PUKWANA-ER8 69 kV with a capacity of 7.5 MVAR | 76962.46 | 18.82% | 409000 | 0.13414
GEN-2023-011 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | 5187173.25 | 8.504% | 61000000 | 0.2248
GEN-2023-222 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | 32503843.81 | 53.28% | 61000000 | 0.55992
GEN-2023-223 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | 16251921.91 | 26.64% | 61000000 | 0.55992
GEN-2023-224 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | 4853633.34 | 7.957% | 61000000 | 0.08361
GEN-2023-225 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | 2203427.69 | 3.612% | 61000000 | 0.08361
GEN-2023-011 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | 7372241.72 | 8.882% | 83000000 | 0.14279
GEN-2023-222 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | 42715659.97 | 51.46% | 83000000 | 0.32886
GEN-2023-223 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | 21357829.99 | 25.73% | 83000000 | 0.32886
GEN-2023-224 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | 7946676.63 | 9.574% | 83000000 | 0.06118
GEN-2023-225 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Current Study | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | 3607591.69 | 4.346% | 83000000 | 0.06118
GEN-2023-009 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 9232699.06 | 1.91% | 483363656 | 0.00984
GEN-2023-022 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 12516687.54 | 2.589% | 483363656 | 0.01334
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 7414307.72 | 1.534% | 483363656 | 0.01317
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 11161432.41 | 2.309% | 483363656 | 0.01293
GEN-2023-030 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 161384.58 | 0.03339% | 483363656 | 0.00172
GEN-2023-035 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 11829864.81 | 2.447% | 483363656 | 0.01576
GEN-2023-038 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 10373650.49 | 2.146% | 483363656 | 0.01382
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 7183490.24 | 1.486% | 483363656 | 0.01276
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 4950378.07 | 1.024% | 483363656 | 0.01319
GEN-2023-056 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 3839451.68 | 0.7943% | 483363656 | 0.00682
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 11051090.4 | 2.286% | 483363656 | 0.01963
GEN-2023-059 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 11259389.1 | 2.329% | 483363656 | 0.015
GEN-2023-063 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 8076359.8 | 1.671% | 483363656 | 0.01594
GEN-2023-064 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 6095082.63 | 1.261% | 483363656 | 0.00812
GEN-2023-069 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 4894081.13 | 1.013% | 483363656 | 0.01304
GEN-2023-075 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 11266895.35 | 2.331% | 483363656 | 0.01501
GEN-2023-076 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 5633447.68 | 1.165% | 483363656 | 0.01501
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 6336446.4 | 1.311% | 483363656 | 0.01443
GEN-2023-092 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 4888451.43 | 1.011% | 483363656 | 0.01042
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 15886998.01 | 3.287% | 483363656 | 0.01411
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 7172230.85 | 1.484% | 483363656 | 0.01274
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 25154413.52 | 5.204% | 483363656 | 0.01411
GEN-2023-104 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 6076316.98 | 1.257% | 483363656 | 0.01619
GEN-2023-132 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 2679734.6 | 0.5544% | 483363656 | 0.00476
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 14016588.3 | 2.9% | 483363656 | 0.01482
GEN-2023-135 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 1274412.72 | 0.2637% | 483363656 | 0.00653
GEN-2023-138 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 11578405.12 | 2.395% | 483363656 | 0.01234
GEN-2023-150 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 8635951.44 | 1.787% | 483363656 | 0.01534
GEN-2023-151 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 1535030.05 | 0.3176% | 483363656 | 0.00409
GEN-2023-161 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 4528672.67 | 0.9369% | 483363656 | 0.01611
GEN-2023-164 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 12035161 | 2.49% | 483363656 | 0.01527
GEN-2023-165 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 12035161 | 2.49% | 483363656 | 0.01527
GEN-2023-166 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 9547961.95 | 1.975% | 483363656 | 0.01696
GEN-2023-167 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 15650550.84 | 3.238% | 483363656 | 0.01668
GEN-2023-168 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 10994793.45 | 2.275% | 483363656 | 0.01674
GEN-2023-174 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 8551506.02 | 1.769% | 483363656 | 0.01519
GEN-2023-177 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 11221857.8 | 2.322% | 483363656 | 0.01495
GEN-2023-180 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 3344038.56 | 0.6918% | 483363656 | 0.00594
GEN-2023-193 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 2430151.48 | 0.5028% | 483363656 | 0.0037
GEN-2023-204 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 58264974.1 | 12.05% | 483363656 | 0.01629
GEN-2023-205 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 9626777.68 | 1.992% | 483363656 | 0.01425
GEN-2023-206 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 1133445.17 | 0.2345% | 483363656 | 0.00604
GEN-2023-210 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 11304689.37 | 2.339% | 483363656 | 0.01577
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 36958944.7 | 7.646% | 483363656 | 0.03939
GEN-2023-212 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 9758137.22 | 2.019% | 483363656 | 0.0065
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 4387408.62 | 0.9077% | 483363656 | 0.01169
GEN-2023-227 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 3182653.98 | 0.6584% | 483363656 | 0.00424
GEN-2023-229 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 13207263.41 | 2.732% | 483363656 | 0.0153
GEN-2023-230 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 1576314.47 | 0.3261% | 483363656 | 0.0028
GEN-2023-241 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | 1448520.41 | 0.2997% | 483363656 | 0.00415
GEN-2023-009 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 4024912.59 | 1.627% | 247391685 | 0.00951
GEN-2023-022 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 5650113.89 | 2.284% | 247391685 | 0.01335
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1663291.95 | 0.6723% | 247391685 | 0.00655
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1892343.76 | 0.7649% | 247391685 | 0.00486
GEN-2023-030 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 13966.57 | 0.005646% | 247391685 | 0.00033
GEN-2023-035 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 5444424.35 | 2.201% | 247391685 | 0.01608
GEN-2023-038 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 4845131.37 | 1.958% | 247391685 | 0.01431
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1020829.57 | 0.4126% | 247391685 | 0.00402
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1102089.63 | 0.4455% | 247391685 | 0.00651
GEN-2023-056 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1168113.43 | 0.4722% | 247391685 | 0.0046
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 6635392.18 | 2.682% | 247391685 | 0.02613
GEN-2023-059 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 7557186.04 | 3.055% | 247391685 | 0.02232
GEN-2023-063 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 3391591.96 | 1.371% | 247391685 | 0.01484
GEN-2023-064 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 2126305.03 | 0.8595% | 247391685 | 0.00628
GEN-2023-069 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 2261738.47 | 0.9142% | 247391685 | 0.01336
GEN-2023-075 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 3480639.45 | 1.407% | 247391685 | 0.01028
GEN-2023-076 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1740319.72 | 0.7035% | 247391685 | 0.01028
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 3060203.26 | 1.237% | 247391685 | 0.01545
GEN-2023-092 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 2150005.89 | 0.8691% | 247391685 | 0.01016
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 2722212.18 | 1.1% | 247391685 | 0.00536
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1856284.61 | 0.7503% | 247391685 | 0.00731
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 4310169.28 | 1.742% | 247391685 | 0.00536
GEN-2023-104 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 242087.28 | 0.09786% | 247391685 | 0.00143
GEN-2023-132 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1998489.72 | 0.8078% | 247391685 | 0.00787
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 6774651.61 | 2.738% | 247391685 | 0.01588
GEN-2023-135 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 506182.49 | 0.2046% | 247391685 | 0.00575
GEN-2023-138 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1972249.49 | 0.7972% | 247391685 | 0.00466
GEN-2023-150 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 3791289.91 | 1.533% | 247391685 | 0.01493
GEN-2023-151 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 485867.47 | 0.1964% | 247391685 | 0.00287
GEN-2023-161 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1860149.54 | 0.7519% | 247391685 | 0.01467
GEN-2023-164 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 5236703.31 | 2.117% | 247391685 | 0.01473
GEN-2023-165 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 5236703.31 | 2.117% | 247391685 | 0.01473
GEN-2023-166 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 4923852.06 | 1.99% | 247391685 | 0.01939
GEN-2023-167 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 7948250.1 | 3.213% | 247391685 | 0.01878
GEN-2023-168 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 5566737.68 | 2.25% | 247391685 | 0.01879
GEN-2023-174 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 3984282.56 | 1.611% | 247391685 | 0.01569
GEN-2023-177 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 5339463.43 | 2.158% | 247391685 | 0.01577
GEN-2023-180 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 975120.78 | 0.3942% | 247391685 | 0.00384
GEN-2023-193 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 758427.27 | 0.3066% | 247391685 | 0.00256
GEN-2023-204 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 39865900.07 | 16.11% | 247391685 | 0.02471
GEN-2023-205 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 4601351.18 | 1.86% | 247391685 | 0.0151
GEN-2023-206 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 338583.6 | 0.1369% | 247391685 | 0.004
GEN-2023-210 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 5655345.01 | 2.286% | 247391685 | 0.01749
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 58799275.12 | 23.77% | 247391685 | 0.13893
GEN-2023-212 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 3866624.76 | 1.563% | 247391685 | 0.00571
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 824451.08 | 0.3333% | 247391685 | 0.00487
GEN-2023-227 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 1069924.19 | 0.4325% | 247391685 | 0.00316
GEN-2023-229 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 5782161.5 | 2.337% | 247391685 | 0.01485
GEN-2023-230 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 388524.69 | 0.157% | 247391685 | 0.00153
GEN-2023-241 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Current Study | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | 481770.61 | 0.1947% | 247391685 | 0.00306
GEN-2023-009 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 2605788.48 | 1.332% | 195647827 | 0.00947
GEN-2023-022 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 3571608.71 | 1.826% | 195647827 | 0.01298
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 2732363.21 | 1.397% | 195647827 | 0.01655
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 4030139.43 | 2.06% | 195647827 | 0.01592
GEN-2023-030 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 190687.58 | 0.09746% | 195647827 | 0.00693
GEN-2023-035 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1829280.02 | 0.935% | 195647827 | 0.00831
GEN-2023-038 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 2511682.92 | 1.284% | 195647827 | 0.01141
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 2567265.73 | 1.312% | 195647827 | 0.01555
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1825978.07 | 0.9333% | 195647827 | 0.01659
GEN-2023-056 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1929989.48 | 0.9865% | 195647827 | 0.01169
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 4706929.01 | 2.406% | 195647827 | 0.02851
GEN-2023-059 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 4569898.1 | 2.336% | 195647827 | 0.02076
GEN-2023-063 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 3083195.34 | 1.576% | 195647827 | 0.02075
GEN-2023-064 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 2751624.58 | 1.406% | 195647827 | 0.0125
GEN-2023-069 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1232727.81 | 0.6301% | 195647827 | 0.0112
GEN-2023-075 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 691208.09 | 0.3533% | 195647827 | 0.00314
GEN-2023-076 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 345604.05 | 0.1766% | 195647827 | 0.00314
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 2050114.4 | 1.048% | 195647827 | 0.01592
GEN-2023-092 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1316652.36 | 0.673% | 195647827 | 0.00957
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 14086116.55 | 7.2% | 195647827 | 0.04266
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1598143.56 | 0.8168% | 195647827 | 0.00968
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 22303017.88 | 11.4% | 195647827 | 0.04266
GEN-2023-104 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 2696592.09 | 1.378% | 195647827 | 0.0245
GEN-2023-132 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 736334.74 | 0.3764% | 195647827 | 0.00446
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 4080020.88 | 2.085% | 195647827 | 0.01471
GEN-2023-135 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 486487.23 | 0.2487% | 195647827 | 0.0085
GEN-2023-138 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 4331057.09 | 2.214% | 195647827 | 0.01574
GEN-2023-150 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 974075.1 | 0.4979% | 195647827 | 0.0059
GEN-2023-151 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 866211.42 | 0.4427% | 195647827 | 0.00787
GEN-2023-161 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 280291.49 | 0.1433% | 195647827 | 0.0034
GEN-2023-164 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1206532.35 | 0.6167% | 195647827 | 0.00522
GEN-2023-165 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1206532.35 | 0.6167% | 195647827 | 0.00522
GEN-2023-166 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 2169380.82 | 1.109% | 195647827 | 0.01314
GEN-2023-167 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 3489059.97 | 1.783% | 195647827 | 0.01268
GEN-2023-168 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 2374927.18 | 1.214% | 195647827 | 0.01233
GEN-2023-174 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1546963.34 | 0.7907% | 195647827 | 0.00937
GEN-2023-177 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 2414825.73 | 1.234% | 195647827 | 0.01097
GEN-2023-180 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1824327.1 | 0.9325% | 195647827 | 0.01105
GEN-2023-193 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1460012 | 0.7462% | 195647827 | 0.00758
GEN-2023-204 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 22300024.11 | 11.4% | 195647827 | 0.02126
GEN-2023-205 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 3056944.84 | 1.562% | 195647827 | 0.01543
GEN-2023-206 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 613612.28 | 0.3136% | 195647827 | 0.01115
GEN-2023-210 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 3060863.16 | 1.564% | 195647827 | 0.01456
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 41392688.57 | 21.16% | 195647827 | 0.15043
GEN-2023-212 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 3746612.03 | 1.915% | 195647827 | 0.00851
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1622357.85 | 0.8292% | 195647827 | 0.01474
GEN-2023-227 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1710409.84 | 0.8742% | 195647827 | 0.00777
GEN-2023-229 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1475861.36 | 0.7543% | 195647827 | 0.00583
GEN-2023-230 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 1203560.59 | 0.6152% | 195647827 | 0.00729
GEN-2023-241 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Current Study | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | 791246.16 | 0.4044% | 195647827 | 0.00773
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 71758.58 | 0.3106% | 23105000 | 0.05421
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 783056.78 | 3.389% | 23105000 | 0.05144
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 839552.93 | 3.634% | 23105000 | 0.04955
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 208683.65 | 0.9032% | 23105000 | 0.04204
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 1368774.15 | 5.924% | 23105000 | 0.07386
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 839552.9333 | 3.634% | 23105000 | 0.04955
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 2211844.85 | 9.573% | 23105000 | 0.05347
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 1141704.09 | 4.941% | 23105000 | 0.0575
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 703719.9296 | 3.046% | 23105000 | 0.04253
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 429432.9668 | 1.859% | 23105000 | 0.04991
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 1250046.85 | 5.41% | 23105000 | 0.06627
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 901863.5 | 3.903% | 23105000 | 0.04955
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 655900.73 | 2.839% | 23105000 | 0.04955
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 1085108.66 | 4.696% | 23105000 | 0.04894
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 550652.16 | 2.383% | 23105000 | 0.04894
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 983851.09 | 4.258% | 23105000 | 0.04955
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 656430.22 | 2.841% | 23105000 | 0.04959
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 719703.79 | 3.115% | 23105000 | 0.05437
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 320127.21 | 1.386% | 23105000 | 0.03023
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 815408.37 | 3.529% | 23105000 | 0.04928
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 1047786.52 | 4.535% | 23105000 | 0.05277
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 1001324.13 | 4.334% | 23105000 | 0.05043
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 792772.85 | 3.431% | 23105000 | 0.05989
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 487209.81 | 2.109% | 23105000 | 0.05889
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 571182.98 | 2.472% | 23105000 | 0.03452
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 1378251.95 | 5.965% | 23105000 | 0.05206
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Current Study | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | 1289298.31 | 5.58% | 23105000 | 0.03896
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 324096.8 | 0.2375% | 136450000 | 0.06157
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 3600596 | 2.639% | 136450000 | 0.05948
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 9374919.85 | 6.871% | 136450000 | 0.13914
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 2803329.45 | 2.054% | 136450000 | 0.03804
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 9374919.85 | 6.871% | 136450000 | 0.13914
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 11425899.39 | 8.374% | 136450000 | 0.06946
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 4247157.81 | 3.113% | 136450000 | 0.05379
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 1215323.54 | 0.8907% | 136450000 | 0.03552
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 3052165.99 | 2.237% | 136450000 | 0.04069
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 10070714.69 | 7.381% | 136450000 | 0.13914
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 7324156.14 | 5.368% | 136450000 | 0.13914
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 13884997.71 | 10.18% | 136450000 | 0.15748
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 7046118.24 | 5.164% | 136450000 | 0.15748
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 10986234.2 | 8.051% | 136450000 | 0.13914
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 8090050 | 5.929% | 136450000 | 0.15369
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 3212016.73 | 2.354% | 136450000 | 0.06102
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 10702116.53 | 7.843% | 136450000 | 0.16265
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 5063584.88 | 3.711% | 136450000 | 0.06413
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 4491928.01 | 3.292% | 136450000 | 0.05689
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 2361900.86 | 1.731% | 136450000 | 0.04487
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 1517970.05 | 1.112% | 136450000 | 0.04614
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | Current Study | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | 6279803.27 | 4.602% | 136450000 | 0.05965
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 1756016.33 | 10.71% | 16400000 | 0.06328
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 213734.17 | 1.303% | 16400000 | 0.02629
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 1756016.33 | 10.71% | 16400000 | 0.06328
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 419230.08 | 2.556% | 16400000 | 0.02975
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 1886345.67 | 11.5% | 16400000 | 0.06328
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 1371887.76 | 8.365% | 16400000 | 0.06328
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 2457690.96 | 14.99% | 16400000 | 0.06768
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 1247186.46 | 7.605% | 16400000 | 0.06768
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 2057831.64 | 12.55% | 16400000 | 0.06328
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 1347389.76 | 8.216% | 16400000 | 0.06215
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | Current Study | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | 1886670.86 | 11.5% | 16400000 | 0.06962
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 39127.88 | 0.2386% | 16400000 | 0.05155
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 505049.5 | 3.08% | 16400000 | 0.05786
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 995553 | 6.07% | 16400000 | 0.10247
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 468139.88 | 2.855% | 16400000 | 0.16447
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 437913.49 | 2.67% | 16400000 | 0.04121
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 995553 | 6.07% | 16400000 | 0.10247
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 1318810.79 | 8.042% | 16400000 | 0.0556
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 758838.03 | 4.627% | 16400000 | 0.06665
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 544431.66 | 3.32% | 16400000 | 0.11035
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 521013.75 | 3.177% | 16400000 | 0.04817
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 1069441.69 | 6.521% | 16400000 | 0.10247
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 777775.78 | 4.743% | 16400000 | 0.10247
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 1265141.83 | 7.714% | 16400000 | 0.09951
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 642012.27 | 3.915% | 16400000 | 0.09951
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 1166663.67 | 7.114% | 16400000 | 0.10247
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 751133.9 | 4.58% | 16400000 | 0.09896
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 387711.4 | 2.364% | 16400000 | 0.05108
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 965862.86 | 5.889% | 16400000 | 0.1018
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 616748.03 | 3.761% | 16400000 | 0.05417
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 674472.1 | 4.113% | 16400000 | 0.05924
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 414732.78 | 2.529% | 16400000 | 0.05464
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 283402 | 1.728% | 16400000 | 0.05974
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | Current Study | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | 800470.71 | 4.881% | 16400000 | 0.05273
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 39127.88 | 0.2386% | 16400000 | 0.05155
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 505049.5 | 3.08% | 16400000 | 0.05786
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 995553 | 6.07% | 16400000 | 0.10247
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 468139.88 | 2.855% | 16400000 | 0.16447
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 437913.49 | 2.67% | 16400000 | 0.04121
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 995553 | 6.07% | 16400000 | 0.10247
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 1318810.79 | 8.042% | 16400000 | 0.0556
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 758838.03 | 4.627% | 16400000 | 0.06665
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 544431.66 | 3.32% | 16400000 | 0.11035
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 521013.75 | 3.177% | 16400000 | 0.04817
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 1069441.69 | 6.521% | 16400000 | 0.10247
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 777775.78 | 4.743% | 16400000 | 0.10247
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 1265141.83 | 7.714% | 16400000 | 0.09951
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 642012.27 | 3.915% | 16400000 | 0.09951
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 1166663.67 | 7.114% | 16400000 | 0.10247
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 751133.9 | 4.58% | 16400000 | 0.09896
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 387711.4 | 2.364% | 16400000 | 0.05108
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 965862.86 | 5.889% | 16400000 | 0.1018
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 616748.03 | 3.761% | 16400000 | 0.05417
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 674472.1 | 4.113% | 16400000 | 0.05924
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 414732.78 | 2.529% | 16400000 | 0.05464
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 283402 | 1.728% | 16400000 | 0.05974
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | Current Study | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | 800470.71 | 4.881% | 16400000 | 0.05273
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 14162.72 | 0.2986% | 4743000 | 0.11515
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 197255.94 | 4.159% | 4743000 | 0.13946
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 251969.66 | 5.312% | 4743000 | 0.16005
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 101308.31 | 2.136% | 4743000 | 0.21965
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 119844.99 | 2.527% | 4743000 | 0.0696
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 251969.66 | 5.312% | 4743000 | 0.16005
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 469220.67 | 9.893% | 4743000 | 0.12208
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 195283.12 | 4.117% | 4743000 | 0.10585
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 128161.2 | 2.702% | 4743000 | 0.16031
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 139126.08 | 2.933% | 4743000 | 0.07938
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 270670.53 | 5.707% | 4743000 | 0.16005
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 196851.29 | 4.15% | 4743000 | 0.16005
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 336730.4 | 7.1% | 4743000 | 0.16345
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 170878.11 | 3.603% | 4743000 | 0.16345
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 295276.94 | 6.226% | 4743000 | 0.16005
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 194858.8 | 4.108% | 4743000 | 0.15843
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 139892.95 | 2.949% | 4743000 | 0.11374
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 247524.67 | 5.219% | 4743000 | 0.161
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 236092.41 | 4.978% | 4743000 | 0.12797
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 273543.97 | 5.767% | 4743000 | 0.14827
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 109316.73 | 2.305% | 4743000 | 0.08888
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 73511.75 | 1.55% | 4743000 | 0.09563
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Current Study | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | 329549.11 | 6.948% | 4743000 | 0.13397
GEN-2023-009 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 1629937.87 | 0.8193% | 198936942 | 0.00951
GEN-2023-022 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2288083.13 | 1.15% | 198936942 | 0.01335
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 3509765.27 | 1.764% | 198936942 | 0.03413
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 5780572.09 | 2.906% | 198936942 | 0.03666
GEN-2023-030 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 310905.08 | 0.1563% | 198936942 | 0.01814
GEN-2023-035 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2204786.62 | 1.108% | 198936942 | 0.01608
GEN-2023-038 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 1962095.56 | 0.9863% | 198936942 | 0.01431
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 3890255.5 | 1.956% | 198936942 | 0.03783
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2337101.24 | 1.175% | 198936942 | 0.03409
GEN-2023-056 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2298366.65 | 1.155% | 198936942 | 0.02235
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2687083.7 | 1.351% | 198936942 | 0.02613
GEN-2023-059 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 3060375.46 | 1.538% | 198936942 | 0.02232
GEN-2023-063 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2488714.6 | 1.251% | 198936942 | 0.02689
GEN-2023-064 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2887612.33 | 1.452% | 198936942 | 0.02106
GEN-2023-069 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 915918.82 | 0.4604% | 198936942 | 0.01336
GEN-2023-075 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 9063208.69 | 4.556% | 198936942 | 0.0661
GEN-2023-076 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 4531604.35 | 2.278% | 198936942 | 0.0661
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 1239266.96 | 0.6229% | 198936942 | 0.01545
GEN-2023-092 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 870671.33 | 0.4377% | 198936942 | 0.01016
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 17261916.16 | 8.677% | 198936942 | 0.08393
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 3578664.85 | 1.799% | 198936942 | 0.0348
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 27331367.26 | 13.74% | 198936942 | 0.08393
GEN-2023-104 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 4281372.03 | 2.152% | 198936942 | 0.06245
GEN-2023-132 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2888640.68 | 1.452% | 198936942 | 0.02809
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2743478.52 | 1.379% | 198936942 | 0.01588
GEN-2023-135 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 404622.22 | 0.2034% | 198936942 | 0.01135
GEN-2023-138 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 6024428.62 | 3.028% | 198936942 | 0.03515
GEN-2023-150 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 1535329.49 | 0.7718% | 198936942 | 0.01493
GEN-2023-151 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 1064001.5 | 0.5348% | 198936942 | 0.01552
GEN-2023-161 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 997711.88 | 0.5015% | 198936942 | 0.01943
GEN-2023-164 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2146581.9 | 1.079% | 198936942 | 0.01491
GEN-2023-165 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2146581.9 | 1.079% | 198936942 | 0.01491
GEN-2023-166 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 1993974.47 | 1.002% | 198936942 | 0.01939
GEN-2023-167 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 3218741.67 | 1.618% | 198936942 | 0.01878
GEN-2023-168 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2254318.91 | 1.133% | 198936942 | 0.01879
GEN-2023-174 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 1613484.24 | 0.8111% | 198936942 | 0.01569
GEN-2023-177 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2162281.41 | 1.087% | 198936942 | 0.01577
GEN-2023-180 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2277799.61 | 1.145% | 198936942 | 0.02215
GEN-2023-193 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 1841606.99 | 0.9257% | 198936942 | 0.01535
GEN-2023-204 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 16144186.7 | 8.115% | 198936942 | 0.02471
GEN-2023-205 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 1863373.77 | 0.9367% | 198936942 | 0.0151
GEN-2023-206 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 757552.62 | 0.3808% | 198936942 | 0.0221
GEN-2023-210 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2290201.54 | 1.151% | 198936942 | 0.01749
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 23811489.86 | 11.97% | 198936942 | 0.13893
GEN-2023-212 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 3139901.35 | 1.578% | 198936942 | 0.01145
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2204786.62 | 1.108% | 198936942 | 0.03216
GEN-2023-227 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2005971.91 | 1.008% | 198936942 | 0.01463
GEN-2023-229 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 2341557.44 | 1.177% | 198936942 | 0.01485
GEN-2023-230 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 1714262.73 | 0.8617% | 198936942 | 0.01667
GEN-2023-241 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Benton 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Benton 345 kV | 940427.88 | 0.4727% | 198936942 | 0.01475
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 72088.2 | 0.02403% | 300000000 | 0.00401
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 3386347.52 | 1.129% | 300000000 | 0.01638
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 6429188.49 | 2.143% | 300000000 | 0.02794
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 4423716.44 | 1.475% | 300000000 | 0.06562
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 5408592.21 | 1.803% | 300000000 | 0.02149
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 6429188.49 | 2.143% | 300000000 | 0.02794
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 4247091.37 | 1.416% | 300000000 | 0.00756
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 1426483.39 | 0.4755% | 300000000 | 0.00529
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 138495627.2 | 46.17% | 300000000 | 0.61632
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 3345449.6 | 1.115% | 300000000 | 0.02863
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 4687979.9 | 1.563% | 300000000 | 0.0183
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 6906354.83 | 2.302% | 300000000 | 0.02794
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 5022803.51 | 1.674% | 300000000 | 0.02794
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 9000373.11 | 3% | 300000000 | 0.02989
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 4567353.52 | 1.522% | 300000000 | 0.02989
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 7534205.26 | 2.511% | 300000000 | 0.02794
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 4805280.52 | 1.602% | 300000000 | 0.02673
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 593244.51 | 0.1977% | 300000000 | 0.0033
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 4068578.71 | 1.356% | 300000000 | 0.02829
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 6375131.33 | 2.125% | 300000000 | 0.02837
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 2844877.08 | 0.9483% | 300000000 | 0.01055
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 5622340.01 | 1.874% | 300000000 | 0.02085
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 2689375.11 | 0.8965% | 300000000 | 0.01496
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 1231431.78 | 0.4105% | 300000000 | 0.01096
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 19051238.44 | 6.35% | 300000000 | 0.08478
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 4882582.08 | 1.628% | 300000000 | 0.01358
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Border 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Border 345 kV | 36453077.37 | 12.15% | 300000000 | 0.08111
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 758438.29 | 0.2528% | 300000000 | 0.13194
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 9786348.69 | 3.262% | 300000000 | 0.14804
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 11872703.54 | 3.958% | 300000000 | 0.16136
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 4734850.21 | 1.578% | 300000000 | 0.21965
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 7675896.72 | 2.559% | 300000000 | 0.09538
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 11872703.54 | 3.958% | 300000000 | 0.16136
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 24522133.77 | 8.174% | 300000000 | 0.13651
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 10725572.82 | 3.575% | 300000000 | 0.12439
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 27569122.51 | 9.19% | 300000000 | 0.38368
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 6024249.91 | 2.008% | 300000000 | 0.16123
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 8532172.05 | 2.844% | 300000000 | 0.10416
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 12753880.76 | 4.251% | 300000000 | 0.16136
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 9275549.64 | 3.092% | 300000000 | 0.16136
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 15767629.62 | 5.256% | 300000000 | 0.16376
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 8001483.69 | 2.667% | 300000000 | 0.16376
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 13913324.46 | 4.638% | 300000000 | 0.16136
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 9219215.74 | 3.073% | 300000000 | 0.16038
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 7530923.15 | 2.51% | 300000000 | 0.13101
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 3876232.42 | 1.292% | 300000000 | 0.08429
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 11647609.36 | 3.883% | 300000000 | 0.1621
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 12108627.63 | 4.036% | 300000000 | 0.14043
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 13268358.75 | 4.423% | 300000000 | 0.15388
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 6465177.67 | 2.155% | 300000000 | 0.11247
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 4208516.23 | 1.403% | 300000000 | 0.11714
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 16602406.1 | 5.534% | 300000000 | 0.14441
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Crawfish 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Crawfish 345 kV | 31286872.72 | 10.43% | 300000000 | 0.21771
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 5292192.01 | 0.2515% | 2104646400 | 0.13194
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 68286684.88 | 3.245% | 2104646400 | 0.14804
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 82844745.39 | 3.936% | 2104646400 | 0.16136
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 30276981.84 | 1.439% | 2104646400 | 0.20129
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 53560480.75 | 2.545% | 2104646400 | 0.09538
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 82844745.39 | 3.936% | 2104646400 | 0.16136
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 171109294.66 | 8.13% | 2104646400 | 0.13651
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 74840355.12 | 3.556% | 2104646400 | 0.12439
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 67521174.16 | 3.208% | 2104646400 | 0.13467
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 42035703.82 | 1.997% | 2104646400 | 0.16123
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 59535355.09 | 2.829% | 2104646400 | 0.10416
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 88993378.84 | 4.228% | 2104646400 | 0.16136
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 64722457.34 | 3.075% | 2104646400 | 0.16136
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 110022561.99 | 5.228% | 2104646400 | 0.16376
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 55832344.89 | 2.653% | 2104646400 | 0.16376
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 97083686.01 | 4.613% | 2104646400 | 0.16136
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 64329373.5 | 3.057% | 2104646400 | 0.16038
GEN-2023-183 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 98320375.9 | 4.672% | 2104646400 | 0.22592
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 52548891.52 | 2.497% | 2104646400 | 0.13101
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 10797772.38 | 0.513% | 2104646400 | 0.03365
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 81274094.69 | 3.862% | 2104646400 | 0.1621
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 84490964.47 | 4.014% | 2104646400 | 0.14043
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 92583277.16 | 4.399% | 2104646400 | 0.15388
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 45112387.07 | 2.143% | 2104646400 | 0.11247
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 29365969.93 | 1.395% | 2104646400 | 0.11714
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 56861783.33 | 2.702% | 2104646400 | 0.11341
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 115847422.71 | 5.504% | 2104646400 | 0.14441
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Current Study | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | 218311945.15 | 10.37% | 2104646400 | 0.21771
GEN-2023-116 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Current Study | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | 32850019.9136 | 10.63% | 308987400 | 0.0583
GEN-2023-117 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Current Study | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | 19710011.9481 | 6.379% | 308987400 | 0.0583
GEN-2023-133 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Current Study | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | 16227797.1443 | 5.252% | 308987400 | 0.0576
GEN-2023-199 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Current Study | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | 17946365.9391 | 5.808% | 308987400 | 0.0637
GEN-2023-216 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Current Study | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | 74084401.685 | 23.98% | 308987400 | 0.3287
GEN-2023-217 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Current Study | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | 74084401.685 | 23.98% | 308987400 | 0.3287
GEN-2023-218 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Current Study | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | 74084401.685 | 23.98% | 308987400 | 0.3287
GEN-2023-011 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 472393.08 | 4.294% | 11000000 | 0.11834
GEN-2023-077 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 550532.09 | 5.005% | 11000000 | 0.10276
GEN-2023-078 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 550532.09 | 5.005% | 11000000 | 0.10276
GEN-2023-079 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 654161.66 | 5.947% | 11000000 | 0.10276
GEN-2023-116 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 876836.82 | 7.971% | 11000000 | 0.08347
GEN-2023-117 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 526102.09 | 4.783% | 11000000 | 0.08347
GEN-2023-133 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 562690.36 | 5.115% | 11000000 | 0.10713
GEN-2023-153 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 203154.7 | 1.847% | 11000000 | 0.08058
GEN-2023-199 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 513265.21 | 4.666% | 11000000 | 0.09772
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 305637.56 | 2.779% | 11000000 | 0.05819
GEN-2023-216 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 450698.54 | 4.097% | 11000000 | 0.10726
GEN-2023-217 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 450698.54 | 4.097% | 11000000 | 0.10726
GEN-2023-218 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 450698.54 | 4.097% | 11000000 | 0.10726
GEN-2023-222 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 1480781.69 | 13.46% | 11000000 | 0.14745
GEN-2023-223 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 740390.85 | 6.731% | 11000000 | 0.14745
GEN-2023-224 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 1520952.1 | 13.83% | 11000000 | 0.15145
GEN-2023-225 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new ELMCREEK7 345kV Capbank | Current Study | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | 690474.07 | 6.277% | 11000000 | 0.15145
GEN-2023-116 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | Current Study | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | 113126617.13 | 58.77% | 192504000 | 0.39257
GEN-2023-117 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | Current Study | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | 67875970.28 | 35.26% | 192504000 | 0.39257
GEN-2023-153 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | Current Study | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | 11501412.6 | 5.975% | 192504000 | 0.1663
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | Current Study | Build a new GR PRAIRIE 3 to ANTELOPE 3 345 kV line 1 (50 miles) to a standard rating of 1792 MVA | 2231905.22 | 1.717% | 130000000 | 0.00488
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | Current Study | Build a new GR PRAIRIE 3 to ANTELOPE 3 345 kV line 1 (50 miles) to a standard rating of 1792 MVA | 113142855.43 | 87.03% | 130000000 | 0.09796
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | Current Study | Build a new GR PRAIRIE 3 to ANTELOPE 3 345 kV line 1 (50 miles) to a standard rating of 1792 MVA | 14625239.35 | 11.25% | 130000000 | 0.01051
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 1158373.6 | 0.3861% | 300000000 | 0.09153
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 11932842.68 | 3.978% | 300000000 | 0.08199
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 11015496.34 | 3.672% | 300000000 | 0.068
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 2517687.62 | 0.8392% | 300000000 | 0.05305
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 8515241.91 | 2.838% | 300000000 | 0.04806
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 11015496.34 | 3.672% | 300000000 | 0.068
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 42139430.7 | 14.05% | 300000000 | 0.10655
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 13282759.86 | 4.428% | 300000000 | 0.06997
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 7737361.07 | 2.579% | 300000000 | 0.04891
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 5079670.09 | 1.693% | 300000000 | 0.06175
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 8620410.54 | 2.873% | 300000000 | 0.0478
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 11833052.71 | 3.944% | 300000000 | 0.068
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 8605856.52 | 2.869% | 300000000 | 0.068
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 14728543.76 | 4.91% | 300000000 | 0.06948
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 7474186.39 | 2.491% | 300000000 | 0.06948
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 12908784.78 | 4.303% | 300000000 | 0.068
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 8917186.03 | 2.972% | 300000000 | 0.07046
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 11655873.31 | 3.885% | 300000000 | 0.0921
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 2789309.97 | 0.9298% | 300000000 | 0.02755
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 11029417.58 | 3.676% | 300000000 | 0.06972
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 17405977.59 | 5.802% | 300000000 | 0.09169
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 14919138.17 | 4.973% | 300000000 | 0.07859
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 7812345.92 | 2.604% | 300000000 | 0.06173
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 4952322.39 | 1.651% | 300000000 | 0.06261
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 5791551.6 | 1.931% | 300000000 | 0.03661
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 21332399.63 | 7.111% | 300000000 | 0.08428
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter 345 kV STATCOM | Current Study | Build a 500 MVAR STATCOM at Potter 345 kV | 14829282.9 | 4.943% | 300000000 | 0.04687
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 4098841.25 | 0.4397% | 932100000 | 0.20808
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 38974744.44 | 4.181% | 932100000 | 0.17205
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 32936970.84 | 3.534% | 932100000 | 0.13063
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 4390771.41 | 0.4711% | 932100000 | 0.05944
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 44692497.97 | 4.795% | 932100000 | 0.16206
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 32936970.84 | 3.534% | 932100000 | 0.13063
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 121151261.84 | 13% | 932100000 | 0.19681
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 51652136.58 | 5.541% | 932100000 | 0.17481
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 18245634.88 | 1.957% | 932100000 | 0.0741
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 15150919.13 | 1.625% | 932100000 | 0.11833
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 45240753.44 | 4.854% | 932100000 | 0.16117
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 35381511.65 | 3.796% | 932100000 | 0.13063
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 25732008.47 | 2.761% | 932100000 | 0.13063
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 43203398.08 | 4.635% | 932100000 | 0.13094
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 21924112.46 | 2.352% | 932100000 | 0.13094
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 38598012.7 | 4.141% | 932100000 | 0.13063
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 26876485 | 2.883% | 932100000 | 0.13644
GEN-2023-183 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 6148941.47 | 0.6597% | 932100000 | 0.02877
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 41411927.89 | 4.443% | 932100000 | 0.21023
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 5414693.78 | 0.5809% | 932100000 | 0.03436
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 32787972.21 | 3.518% | 932100000 | 0.13316
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 55750386.87 | 5.981% | 932100000 | 0.18868
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 47051577.3 | 5.048% | 932100000 | 0.15924
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 33282401.83 | 3.571% | 932100000 | 0.16896
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 20345975.85 | 2.183% | 932100000 | 0.16526
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 2834106.04 | 0.3041% | 932100000 | 0.01151
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 71032398.79 | 7.621% | 932100000 | 0.1803
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Potter to Chisholm 765 kV Line | Current Study | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | 14852586.99 | 1.593% | 932100000 | 0.03016
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Build new Reno 345 kV Capbank | Current Study | Build a 100 MVAR Capacitor Bank at Reno 345 kV | 9608545 | 100% | 9608545 | 0.04453
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 824777.22 | 2.417% | 34125000 | 0.02431
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 755633 | 2.214% | 34125000 | 0.02001
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 755633 | 2.214% | 34125000 | 0.02001
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 811715.14 | 2.379% | 34125000 | 0.02001
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 590338.28 | 1.73% | 34125000 | 0.02001
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 16873629.37 | 49.45% | 34125000 | 0.34146
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 8562737.29 | 25.09% | 34125000 | 0.34146
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 885507.42 | 2.595% | 34125000 | 0.02001
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 620430.49 | 1.818% | 34125000 | 0.02103
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 870682.59 | 2.551% | 34125000 | 0.02361
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 1502397.65 | 4.403% | 34125000 | 0.03395
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build new Tolk to Needmore 230 kV Line | Current Study | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | 1071518.56 | 3.14% | 34125000 | 0.01816
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Current Study | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | 2243130.33 | 10.37% | 21623128 | 0.02612
GEN-2023-194 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Current Study | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | 17827926.67 | 82.45% | 21623128 | 0.36906
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Current Study | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | 1552071 | 7.178% | 21623128 | 0.02332
GEN-2023-149 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | Current Study | Build new STILWEL7 to G21-029-TAP 345 kV line to a minimum rating of 1792 MVA | 89000000 | 100% | 89000000 | 0.19557
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | Current Study | Upgrade Terminal Equipment on the DRYGULCH to G23-028-TAP line Ckt 1 to achieve a rating of 443 MVA | 166549 | 65.42% | 254602 | 0.63246
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | Current Study | Upgrade Terminal Equipment on the DRYGULCH to G23-028-TAP line Ckt 1 to achieve a rating of 443 MVA | 88053 | 34.58% | 254602 | 0.51271
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | HARRING_WST6 to HARRNG_MID6 230 kV Ckt 1 Terminal Upgrade | Current Study | Upgrade Terminal Equipment on the HARRING_WST6 to HARRNG_MID6 line Ckt 1 to achieve a rating of 650 MVA | 3600000 | 100% | 3600000 | 0.24945
GEN-2023-085 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) | Current Study | Rebuild 5MANSFDMN to G23-085-TAP 161 kV line 1 to a minimum rating of 231 MVA | 2220000 | 100% | 2220000 | 0.6865
GEN-2023-033 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | Current Study | Rebuild 5MOCITYB2 to G23-169-TAP 161 kV line 1 to a minimum rating of 278 MVA | 823058.65 | 41.15% | 2000000 | 0.28218
GEN-2023-169 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | Current Study | Rebuild 5MOCITYB2 to G23-169-TAP 161 kV line 1 to a minimum rating of 278 MVA | 1176941.35 | 58.85% | 2000000 | 0.64561
GEN-2023-034 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 1.09% | $- | 0.01902
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 48.49% | $- | 0.27492
GEN-2023-065 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 0.89% | $- | 0.01446
GEN-2023-073 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 3.6% | $- | 0.0327
GEN-2023-099 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 0.23% | $- | 0.00172
GEN-2023-149 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 3.71% | $- | 0.02804
GEN-2023-194 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 8.67% | $- | 0.08744
GEN-2023-219 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 0.14% | $- | 0.00253
GEN-2023-220 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 0.72% | $- | 0.00657
GEN-2023-221 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 0.75% | $- | 0.00684
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | $- | 31.7% | $- | 0.2319
GEN-2023-034 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 686834.09 | 1.09% | 63000000 | 0.01902
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 30546700.34 | 48.49% | 63000000 | 0.27492
GEN-2023-065 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 562333.95 | 0.8926% | 63000000 | 0.01446
GEN-2023-073 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 2270835.84 | 3.605% | 63000000 | 0.0327
GEN-2023-099 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 143333.49 | 0.2275% | 63000000 | 0.00172
GEN-2023-149 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 2336669.24 | 3.709% | 63000000 | 0.02804
GEN-2023-194 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 5465006.02 | 8.675% | 63000000 | 0.08744
GEN-2023-219 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 87847.32 | 0.1394% | 63000000 | 0.00253
GEN-2023-220 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 456250.5 | 0.7242% | 63000000 | 0.00657
GEN-2023-221 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 475000.52 | 0.754% | 63000000 | 0.00684
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | Current Study | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | 19969188.68 | 31.7% | 63000000 | 0.2319
GEN-2023-011 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1 | Current Study | Rebuild the existing BEATRCE7 to HARBINE7 115 kV line 1 (14.08 miles) to a minimum rating of 200 MVA | 14080000 | 100% | 14080000 | 0.5788
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the CAMPBELL 4 to GLENHAM4 230kV Line 1 | Current Study | Rebuild the existing CAMPBELL 4 to GLENHAM4 230 kV line 1 (14 miles) to a minimum rating of 260 MVA | 6000000 | 100% | 6000000 | 0.03188
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the COLMBUS4 to MEADOWGROVE4 230kV Line 1 | Current Study | Rebuild the existing COLMBUS4 to MEADOWGROVE4 230 kV line 1 (44.14 miles) to a minimum rating of 560 MVA | 11804179.03 | 14.08% | 83866000 | 0.05296
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the COLMBUS4 to MEADOWGROVE4 230kV Line 1 | Current Study | Rebuild the existing COLMBUS4 to MEADOWGROVE4 230 kV line 1 (44.14 miles) to a minimum rating of 560 MVA | 39828877.58 | 47.49% | 83866000 | 0.07076
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the COLMBUS4 to MEADOWGROVE4 230kV Line 1 | Current Study | Rebuild the existing COLMBUS4 to MEADOWGROVE4 230 kV line 1 (44.14 miles) to a minimum rating of 560 MVA | 32232943.39 | 38.43% | 83866000 | 0.04753
GEN-2023-006 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 1426382.04 | 2.593% | 55000000 | 0.02767
GEN-2023-023 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 3690657.04 | 6.71% | 55000000 | 0.07231
GEN-2023-032 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 993736.59 | 1.807% | 55000000 | 0.01947
GEN-2023-033 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 1435227.16 | 2.61% | 55000000 | 0.02812
GEN-2023-034 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 1415270.77 | 2.573% | 55000000 | 0.04266
GEN-2023-036 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 686351.97 | 1.248% | 55000000 | 0.0163
GEN-2023-037 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 3857555.79 | 7.014% | 55000000 | 0.07558
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 3812641.14 | 6.932% | 55000000 | 0.03735
GEN-2023-065 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 1710992.89 | 3.111% | 55000000 | 0.04789
GEN-2023-073 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 2818011.37 | 5.124% | 55000000 | 0.04417
GEN-2023-087 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 1982369.24 | 3.604% | 55000000 | 0.03884
GEN-2023-099 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 8942098.11 | 16.26% | 55000000 | 0.1168
GEN-2023-149 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 4758911.11 | 8.653% | 55000000 | 0.06216
GEN-2023-169 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 276888.6 | 0.5034% | 55000000 | 0.00868
GEN-2023-171 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 1233366.44 | 2.242% | 55000000 | 0.03222
GEN-2023-219 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 2664574.25 | 4.845% | 55000000 | 0.08353
GEN-2023-220 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 5006324.47 | 9.102% | 55000000 | 0.07847
GEN-2023-221 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 4986546.72 | 9.066% | 55000000 | 0.07816
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Current Study | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | 3302094.3 | 6.004% | 55000000 | 0.04174
GEN-2023-132 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line | Current Study | Rebuild the 5HEBER.N# to GREERSF5 161 kV line CKT1 (0 miles) to a minimum rating of 229 MVA | 2224000 | 100% | 2224000 | 0.15954
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Current Study | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | 7208377.87 | 49.96% | 14429000 | 0.17943
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Current Study | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | 5821701.92 | 40.35% | 14429000 | 0.2222
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Current Study | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | 1398920.21 | 9.695% | 14429000 | 0.08009
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line | Current Study | Rebuild the BIRDHOL4 to JAY 4 138 kV line CKT1 (15.58 miles) to a minimum rating of 185 MVA | 230000 | 100% | 230000 | 0.23982
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 413460.64 | 0.3101% | 133320000 | 0.114
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 4517057.47 | 3.388% | 133320000 | 0.1083
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 4847557.59 | 3.636% | 133320000 | 0.10442
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 1210052.4 | 0.9076% | 133320000 | 0.08897
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 7839286.23 | 5.88% | 133320000 | 0.15439
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 4847557.59 | 3.636% | 133320000 | 0.10442
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 12746102.88 | 9.561% | 133320000 | 0.11246
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 6570215.95 | 4.928% | 133320000 | 0.12077
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 4079296.95 | 3.06% | 133320000 | 0.08998
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 2479095.48 | 1.86% | 133320000 | 0.10516
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 7172508.41 | 5.38% | 133320000 | 0.13878
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 5207337.26 | 3.906% | 133320000 | 0.10442
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 3787154.37 | 2.841% | 133320000 | 0.10442
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 6266938.95 | 4.701% | 133320000 | 0.10316
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 3180237.67 | 2.385% | 133320000 | 0.10316
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 5680731.55 | 4.261% | 133320000 | 0.10442
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 3790055.85 | 2.843% | 133320000 | 0.1045
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 4146212.29 | 3.11% | 133320000 | 0.11432
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 1877256.37 | 1.408% | 133320000 | 0.0647
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 4708101.67 | 3.531% | 133320000 | 0.10385
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 6040333.5 | 4.531% | 133320000 | 0.11103
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 5778656.44 | 4.334% | 133320000 | 0.10622
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 4557859.5 | 3.419% | 133320000 | 0.12567
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 2801739.85 | 2.102% | 133320000 | 0.1236
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 3332619.68 | 2.5% | 133320000 | 0.07351
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 7948599.42 | 5.962% | 133320000 | 0.10958
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Current Study | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | 7493974.06 | 5.621% | 133320000 | 0.08265
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 9463.46 | 0.11% | 8607000 | 0.01384
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 201382.19 | 2.34% | 8607000 | 0.02561
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 986737.53 | 11.46% | 8607000 | 0.11274
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 986737.53 | 11.46% | 8607000 | 0.11274
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 430137.64 | 4.998% | 8607000 | 0.02013
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 1059971.96 | 12.32% | 8607000 | 0.11274
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 770888.7 | 8.957% | 8607000 | 0.11274
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 826924.11 | 9.608% | 8607000 | 0.0722
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 419633.13 | 4.875% | 8607000 | 0.0722
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 1156333.05 | 13.43% | 8607000 | 0.11274
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 318160.82 | 3.697% | 8607000 | 0.04653
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 89164.35 | 1.036% | 8607000 | 0.01304
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 526763.69 | 6.12% | 8607000 | 0.06163
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 215799.6 | 2.507% | 8607000 | 0.02104
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 303801.53 | 3.53% | 8607000 | 0.02962
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | Current Study | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | 305100.71 | 3.545% | 8607000 | 0.02231
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 157655.62 | 0.357% | 44160000 | 0.03592
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1658588.05 | 3.756% | 44160000 | 0.03286
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1730349.44 | 3.918% | 44160000 | 0.0308
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 2301807.18 | 5.212% | 44160000 | 0.03746
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1730349.44 | 3.918% | 44160000 | 0.0308
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 4808781.73 | 10.89% | 44160000 | 0.03506
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 2568926.36 | 5.817% | 44160000 | 0.03902
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 2152841.93 | 4.875% | 44160000 | 0.03924
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 898378.08 | 2.034% | 44160000 | 0.03149
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 2606222.54 | 5.902% | 44160000 | 0.04167
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1858773.82 | 4.209% | 44160000 | 0.0308
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1351835.5 | 3.061% | 44160000 | 0.0308
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 2214332.89 | 5.014% | 44160000 | 0.03012
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1123691.32 | 2.545% | 44160000 | 0.03012
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 2027753.25 | 4.592% | 44160000 | 0.0308
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1353591.13 | 3.065% | 44160000 | 0.03084
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1584456.55 | 3.588% | 44160000 | 0.0361
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1672786.71 | 3.788% | 44160000 | 0.03049
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 2258838.12 | 5.115% | 44160000 | 0.03431
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 2089639.23 | 4.732% | 44160000 | 0.03174
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1903103.49 | 4.31% | 44160000 | 0.04336
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 1163105.22 | 2.634% | 44160000 | 0.0424
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Current Study | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | 2944192.39 | 6.667% | 44160000 | 0.03354
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing ERLSBOR2 to FRSTHIL2 69 kV line | Current Study | Rebuild the ERLSBOR2 to FRSTHIL2 69 kV line CKT1 (8.31 miles) to a minimum rating of 143 MVA. | 8000000 | 100% | 8000000 | 0.03767
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 50215.6814 | 0.3101% | 16192000 | 0.114
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 548606.3194 | 3.388% | 16192000 | 0.1083
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 588746.2684 | 3.636% | 16192000 | 0.10442
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 146963.4597 | 0.9076% | 16192000 | 0.08897
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 952098.1294 | 5.88% | 16192000 | 0.15439
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 588746.2684 | 3.636% | 16192000 | 0.10442
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 1548041.5383 | 9.561% | 16192000 | 0.11246
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 797966.8216 | 4.928% | 16192000 | 0.12077
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 495439.3655 | 3.06% | 16192000 | 0.08998
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 301091.4638 | 1.86% | 16192000 | 0.10516
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 871116.5333 | 5.38% | 16192000 | 0.13878
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 632442.2805 | 3.906% | 16192000 | 0.10442
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 459958.0222 | 2.841% | 16192000 | 0.10442
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 761133.1788 | 4.701% | 16192000 | 0.10316
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 386246.6878 | 2.385% | 16192000 | 0.10316
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 689937.0333 | 4.261% | 16192000 | 0.10442
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 460310.4129 | 2.843% | 16192000 | 0.1045
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 503566.3771 | 3.11% | 16192000 | 0.11432
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 227996.8132 | 1.408% | 16192000 | 0.0647
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 571809.0477 | 3.531% | 16192000 | 0.10385
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 733611.4615 | 4.531% | 16192000 | 0.11103
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 701830.221 | 4.334% | 16192000 | 0.10622
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 553561.8143 | 3.419% | 16192000 | 0.12567
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 340277.3148 | 2.102% | 16192000 | 0.1236
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 404753.8093 | 2.5% | 16192000 | 0.07351
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 965374.4507 | 5.962% | 16192000 | 0.10958
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Current Study | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | 910159.2256 | 5.621% | 16192000 | 0.08265
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 5125.0542 | 0.3106% | 1650000 | 0.05723
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 55920.6724 | 3.389% | 1650000 | 0.0543
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 59961.0742 | 3.634% | 1650000 | 0.05231
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 14900.3137 | 0.903% | 1650000 | 0.04437
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 97753.0429 | 5.924% | 1650000 | 0.07797
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 59961.0742 | 3.634% | 1650000 | 0.05231
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 157947.1311 | 9.573% | 1650000 | 0.05644
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 81536.9882 | 4.942% | 1650000 | 0.0607
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 50249.7995 | 3.045% | 1650000 | 0.04489
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 30664.3553 | 1.858% | 1650000 | 0.05268
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 89264.1962 | 5.41% | 1650000 | 0.06995
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 64411.3102 | 3.904% | 1650000 | 0.05231
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 46844.5892 | 2.839% | 1650000 | 0.05231
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 77489.6909 | 4.696% | 1650000 | 0.05166
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 39323.1267 | 2.383% | 1650000 | 0.05166
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 70266.8839 | 4.259% | 1650000 | 0.05231
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 46880.41 | 2.841% | 1650000 | 0.05235
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 51393.8248 | 3.115% | 1650000 | 0.05739
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 22860.8043 | 1.386% | 1650000 | 0.03191
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 58219.917 | 3.528% | 1650000 | 0.05201
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 74820.5971 | 4.535% | 1650000 | 0.0557
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 71502.6998 | 4.333% | 1650000 | 0.05323
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 56614.6995 | 3.431% | 1650000 | 0.06322
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 34790.906 | 2.109% | 1650000 | 0.06216
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 40779.6881 | 2.471% | 1650000 | 0.03643
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 98435.4282 | 5.966% | 1650000 | 0.05496
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Current Study | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | 92081.7222 | 5.581% | 1650000 | 0.04113
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing GROVE 4 to JAY 4 138 kV line | Current Study | Rebuild the GROVE 4 to JAY 4 138 kV line CKT1 (13.03 miles) to a minimum rating of 177 MVA | 230000 | 100% | 230000 | 0.23982
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing HALE_CNTY3 to TUCO3 115 kV line | Current Study | Rebuild the HALE_CNTY to TUCO3 115 kV line CKT1 (20.73 miles) to a minimum rating of 152 | 20730000 | 100% | 20730000 | 0.12813
GEN-2023-194 | DISIS-2023-001 | 03 CENTRAL | TBD | NRIS | Rebuild the existing JOP 59 2 to RIV167 2 69 kV line | Current Study | Rebuild the JOP 59 2 to RIV167 2 69 kV line CKT1 (10.05 miles) to a minimum rating of 86 MVA. | 8542500 | 100% | 8542500 | 0.0218
GEN-2023-009 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Current Study | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | 21703477.69 | 14.49% | 149760000 | 0.0749
GEN-2023-038 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Current Study | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | 5551917.66 | 3.707% | 149760000 | 0.02395
GEN-2023-069 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Current Study | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | 3787821.9 | 2.529% | 149760000 | 0.03268
GEN-2023-092 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Current Study | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | 9805683.3773 | 6.548% | 149760000 | 0.06768
GEN-2023-135 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Current Study | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | 7509206.2391 | 5.014% | 149760000 | 0.12459
GEN-2023-151 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Current Study | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | 5895000.67 | 3.936% | 149760000 | 0.05086
GEN-2023-212 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Current Study | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | 54276659.72 | 36.24% | 149760000 | 0.11707
GEN-2023-227 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Current Study | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | 41230232.75 | 27.53% | 149760000 | 0.17786
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line | Current Study | Rebuild the MIAMI 5 to AFTON 5 161 kV line CKT1 (13.5 miles) to a minimum rating of 419 MVA | 7802215.3707 | 49.9% | 15635000 | 0.1659
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line | Current Study | Rebuild the MIAMI 5 to AFTON 5 161 kV line CKT1 (13.5 miles) to a minimum rating of 419 MVA | 6280602.41 | 40.17% | 15635000 | 0.20477
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line | Current Study | Rebuild the MIAMI 5 to AFTON 5 161 kV line CKT1 (13.5 miles) to a minimum rating of 419 MVA | 1552182.22 | 9.928% | 15635000 | 0.07591
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 112631.28 | 0.1497% | 75221000 | 0.02684
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 1763850.38 | 2.345% | 75221000 | 0.03655
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 8229502.9338 | 10.94% | 75221000 | 0.15321
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 8229502.9338 | 10.94% | 75221000 | 0.15321
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 4424575.62 | 5.882% | 75221000 | 0.03374
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 8840286.35 | 11.75% | 75221000 | 0.15321
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 6429299.17 | 8.547% | 75221000 | 0.15321
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 6800522.8976 | 9.041% | 75221000 | 0.09675
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 3451011.62 | 4.588% | 75221000 | 0.09675
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 9643948.75 | 12.82% | 75221000 | 0.15321
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 3744864.29 | 4.978% | 75221000 | 0.08924
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 1089804.19 | 1.449% | 75221000 | 0.02597
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 5064001.5468 | 6.732% | 75221000 | 0.09654
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 2104912.5137 | 2.798% | 75221000 | 0.03344
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 2475664.15 | 3.291% | 75221000 | 0.03933
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | Current Study | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | 2816621.37 | 3.744% | 75221000 | 0.03356
GEN-2023-064 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing NHUNTNT5 to G23-180-TAP 161 kV line | Current Study | Rebuild the NHUNTNT5 to G23-180-TAP 161 kV line CKT1 (3.03 miles) to a minimum rating of 184 MVA | 105258.46 | 1.51% | 6969000 | 0.00343
GEN-2023-180 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing NHUNTNT5 to G23-180-TAP 161 kV line | Current Study | Rebuild the NHUNTNT5 to G23-180-TAP 161 kV line CKT1 (3.03 miles) to a minimum rating of 184 MVA | 6863741.54 | 98.49% | 6969000 | 0.29822
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line | Current Study | Rebuild the PENSA 5 to G23-049-TAP 161 kV line CKT1 (6.5 miles) to a minimum rating of 449 MVA | 72830.9 | 53.63% | 135805 | 0.36754
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line | Current Study | Rebuild the PENSA 5 to G23-049-TAP 161 kV line CKT1 (6.5 miles) to a minimum rating of 449 MVA | 62974.1 | 46.37% | 135805 | 0.48729
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Current Study | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | 2643808.01 | 49.97% | 5291000 | 0.18241
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Current Study | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | 2136633.3 | 40.38% | 5291000 | 0.22604
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Current Study | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | 510558.69 | 9.65% | 5291000 | 0.08102
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 313506.86 | 0.2779% | 112794000 | 0.06322
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 3826598.65 | 3.393% | 112794000 | 0.0671
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 4461021.08 | 3.955% | 112794000 | 0.07028
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 1487322.75 | 1.319% | 112794000 | 0.07998
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 3687895.91 | 3.27% | 112794000 | 0.05312
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 4461021.08 | 3.955% | 112794000 | 0.07028
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 9967554.31 | 8.837% | 112794000 | 0.06432
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 4552345.7 | 4.036% | 112794000 | 0.0612
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 4022354.47 | 3.566% | 112794000 | 0.06489
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 2263428.27 | 2.007% | 112794000 | 0.07022
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 3944548.04 | 3.497% | 112794000 | 0.05582
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 4792112.49 | 4.249% | 112794000 | 0.07028
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 3485172.72 | 3.09% | 112794000 | 0.07028
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 5887502.08 | 5.22% | 112794000 | 0.07088
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 2987687.62 | 2.649% | 112794000 | 0.07088
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 5227759.08 | 4.635% | 112794000 | 0.07028
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 3474262.96 | 3.08% | 112794000 | 0.07006
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 3123662.91 | 2.769% | 112794000 | 0.06299
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 1322263.03 | 1.172% | 112794000 | 0.03333
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 4368243.48 | 3.873% | 112794000 | 0.07047
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 4854347.72 | 4.304% | 112794000 | 0.06526
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 5096098.1 | 4.518% | 112794000 | 0.06851
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 2890590.75 | 2.563% | 112794000 | 0.05829
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 1842261.9 | 1.633% | 112794000 | 0.05944
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 3475626.68 | 3.081% | 112794000 | 0.05607
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 6568667.88 | 5.824% | 112794000 | 0.06623
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Current Study | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | 10410143.47 | 9.229% | 112794000 | 0.08397
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 86508.1 | 0.11% | 78679000 | 0.01384
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 1840891.09 | 2.34% | 78679000 | 0.02561
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 9020044.42 | 11.46% | 78679000 | 0.11274
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 9020044.42 | 11.46% | 78679000 | 0.11274
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 3932008.72 | 4.998% | 78679000 | 0.02013
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 9689500.84 | 12.32% | 78679000 | 0.11274
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 7046909.7 | 8.957% | 78679000 | 0.11274
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 7559145.16 | 9.608% | 78679000 | 0.0722
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 3835984.11 | 4.875% | 78679000 | 0.0722
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 10570364.56 | 13.43% | 78679000 | 0.11274
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 2908397.27 | 3.697% | 78679000 | 0.04653
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 815076.3 | 1.036% | 78679000 | 0.01304
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 4815294.54 | 6.12% | 78679000 | 0.06163
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 1972684.68 | 2.507% | 78679000 | 0.02104
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 2777134.98 | 3.53% | 78679000 | 0.02962
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Current Study | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | 2789011.1 | 3.545% | 78679000 | 0.02231
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing RIV4525 to STL439_5 161 kV line | Current Study | Rebuild the RIV425 to STL439_5 161 kV line CKT1 (6.82 miles) to a minimum rating of 620 MVA | 398385.4 | 3.894% | 10230000 | 0.02913
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing RIV4525 to STL439_5 161 kV line | Current Study | Rebuild the RIV425 to STL439_5 161 kV line CKT1 (6.82 miles) to a minimum rating of 620 MVA | 335183.88 | 3.276% | 10230000 | 0.03758
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | TBD | NRIS | Rebuild the existing RIV4525 to STL439_5 161 kV line | Current Study | Rebuild the RIV425 to STL439_5 161 kV line CKT1 (6.82 miles) to a minimum rating of 620 MVA | 574634.92 | 5.617% | 10230000 | 0.02416
GEN-2023-194 | DISIS-2023-001 | 03 CENTRAL | TBD | NRIS | Rebuild the existing RIV4525 to STL439_5 161 kV line | Current Study | Rebuild the RIV425 to STL439_5 161 kV line CKT1 (6.82 miles) to a minimum rating of 620 MVA | 8921795.8 | 87.21% | 10230000 | 0.66686
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line | Current Study | Rebuild the SPEARMAN to PRINGLE 115 kV line CKT1 (17.76 miles) to a minimum rating of 196 MVA | 13616614.46 | 76.67% | 17760000 | 0.10834
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line | Current Study | Rebuild the SPEARMAN to PRINGLE 115 kV line CKT1 (17.76 miles) to a minimum rating of 196 MVA | 2605409.16 | 14.67% | 17760000 | 0.02954
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line | Current Study | Rebuild the SPEARMAN to PRINGLE 115 kV line CKT1 (17.76 miles) to a minimum rating of 196 MVA | 1537976.38 | 8.66% | 17760000 | 0.0279
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT2 line | Current Study | Rebuild the SPEARMAN to PRINGLE 115 kV line CKT2 (20.02 miles) to a minimum rating of 184 MVA | 20020000 | 100% | 20020000 | 0.09611
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 708426.74 | 5.632% | 12578000 | 0.02897
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 1514645.77 | 12.04% | 12578000 | 0.05663
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 708426.74 | 5.632% | 12578000 | 0.02897
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 1694190.19 | 13.47% | 12578000 | 0.05912
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 512861.25 | 4.077% | 12578000 | 0.0413
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 2378013.15 | 18.91% | 12578000 | 0.08735
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 761005.28 | 6.05% | 12578000 | 0.02897
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 553458.39 | 4.4% | 12578000 | 0.02897
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 830187.58 | 6.6% | 12578000 | 0.02897
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 1835945.84 | 14.6% | 12578000 | 0.0961
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Current Study | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | 1080839.08 | 8.593% | 12578000 | 0.09052
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 178724.18 | 0.3821% | 46778000 | 0.05544
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 2941002.37 | 6.287% | 46778000 | 0.07933
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 3036196.21 | 6.491% | 46778000 | 0.07358
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 3036196.21 | 6.491% | 46778000 | 0.07358
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 5770495.56 | 12.34% | 46778000 | 0.05728
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 3261538.89 | 6.972% | 46778000 | 0.07358
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 2372028.29 | 5.071% | 46778000 | 0.07358
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 3297096.75 | 7.048% | 46778000 | 0.06106
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 1673153.58 | 3.577% | 46778000 | 0.06106
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 3558042.43 | 7.606% | 46778000 | 0.07358
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 1746300.25 | 3.733% | 46778000 | 0.05417
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 1759195.21 | 3.761% | 46778000 | 0.05457
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 2165547.7 | 4.629% | 46778000 | 0.05374
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 3052237.54 | 6.525% | 46778000 | 0.06312
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 4544023.47 | 9.714% | 46778000 | 0.09397
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Current Study | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | 4386221.37 | 9.377% | 46778000 | 0.06803
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Current Study | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | 15811230.85 | 24.76% | 63860000 | 0.02697
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Current Study | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | 25034448.84 | 39.2% | 63860000 | 0.02697
GEN-2023-104 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Current Study | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | 5074992.77 | 7.947% | 63860000 | 0.02597
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Current Study | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | 17939327.54 | 28.09% | 63860000 | 0.03672
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line | Current Study | Rebuild the TAYLOR3 to W_BENDER3 115 kV line CKT1 (6.4 miles) to a minimum rating of 225 MVA | 6400000 | 100% | 6400000 | 0.14198
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 246313.57 | 0.2375% | 103702000 | 0.06157
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 2736452.96 | 2.639% | 103702000 | 0.05948
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 7124939.09 | 6.871% | 103702000 | 0.13914
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 2130530.38 | 2.054% | 103702000 | 0.03804
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 7124939.09 | 6.871% | 103702000 | 0.13914
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 8683683.54 | 8.374% | 103702000 | 0.06946
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 3227839.94 | 3.113% | 103702000 | 0.05379
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 923645.89 | 0.8907% | 103702000 | 0.03552
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 2319646.15 | 2.237% | 103702000 | 0.04069
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 7653743.16 | 7.381% | 103702000 | 0.13914
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 5566358.66 | 5.368% | 103702000 | 0.13914
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 10552598.26 | 10.18% | 103702000 | 0.15748
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 5355049.86 | 5.164% | 103702000 | 0.15748
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 8349538 | 8.051% | 103702000 | 0.13914
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 6148438 | 5.929% | 103702000 | 0.15369
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 2441132.71 | 2.354% | 103702000 | 0.06102
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 8133608.57 | 7.843% | 103702000 | 0.16265
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 3848324.51 | 3.711% | 103702000 | 0.06413
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 3413865.29 | 3.292% | 103702000 | 0.05689
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 1795044.65 | 1.731% | 103702000 | 0.04487
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 1153657.24 | 1.112% | 103702000 | 0.04614
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | Current Study | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | 4772650.49 | 4.602% | 103702000 | 0.05965
GEN-2023-138 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line | Current Study | Rebuild the TONECE7 to G23-138-TAP 345 kV line CKT1 (22.5 miles) to a minimum rating of 1317 MVA | 25749990 | 100% | 25749990 | 0.37238
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 10050.96 | 0.2986% | 3366000 | 0.11515
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 139988.09 | 4.159% | 3366000 | 0.13946
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 178817.17 | 5.312% | 3366000 | 0.16005
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 71896.22 | 2.136% | 3366000 | 0.21965
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 85051.28 | 2.527% | 3366000 | 0.0696
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 178817.17 | 5.312% | 3366000 | 0.16005
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 332995.31 | 9.893% | 3366000 | 0.12208
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 138588.02 | 4.117% | 3366000 | 0.10585
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 90953.11 | 2.702% | 3366000 | 0.16031
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 98734.64 | 2.933% | 3366000 | 0.07938
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 192088.76 | 5.707% | 3366000 | 0.16005
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 139700.92 | 4.15% | 3366000 | 0.16005
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 238969.96 | 7.1% | 3366000 | 0.16345
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 121268.34 | 3.603% | 3366000 | 0.16345
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 209551.38 | 6.226% | 3366000 | 0.16005
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 138286.89 | 4.108% | 3366000 | 0.15843
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 99278.87 | 2.949% | 3366000 | 0.11374
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 175662.67 | 5.219% | 3366000 | 0.161
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 167549.45 | 4.978% | 3366000 | 0.12797
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 194127.98 | 5.767% | 3366000 | 0.14827
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 77579.62 | 2.305% | 3366000 | 0.08888
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 52169.63 | 1.55% | 3366000 | 0.09563
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | 233873.56 | 6.948% | 3366000 | 0.13397
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 10050.96 | 0.2986% | 3366000 | 0.11515
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 139988.09 | 4.159% | 3366000 | 0.13946
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 178817.17 | 5.312% | 3366000 | 0.16005
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 71896.22 | 2.136% | 3366000 | 0.21965
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 85051.28 | 2.527% | 3366000 | 0.0696
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 178817.17 | 5.312% | 3366000 | 0.16005
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 332995.31 | 9.893% | 3366000 | 0.12208
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 138588.02 | 4.117% | 3366000 | 0.10585
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 90953.11 | 2.702% | 3366000 | 0.16031
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 98734.64 | 2.933% | 3366000 | 0.07938
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 192088.76 | 5.707% | 3366000 | 0.16005
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 139700.92 | 4.15% | 3366000 | 0.16005
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 238969.96 | 7.1% | 3366000 | 0.16345
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 121268.34 | 3.603% | 3366000 | 0.16345
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 209551.38 | 6.226% | 3366000 | 0.16005
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 138286.89 | 4.108% | 3366000 | 0.15843
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 99278.87 | 2.949% | 3366000 | 0.11374
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 175662.67 | 5.219% | 3366000 | 0.161
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 167549.45 | 4.978% | 3366000 | 0.12797
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 194127.98 | 5.767% | 3366000 | 0.14827
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 77579.62 | 2.305% | 3366000 | 0.08888
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 52169.63 | 1.55% | 3366000 | 0.09563
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Current Study | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | 233873.56 | 6.948% | 3366000 | 0.13397
GEN-2023-056 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Current Study | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | 2222433.24 | 61.73% | 3600000 | 0.74374
GEN-2023-064 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Current Study | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | 1268066.49 | 35.22% | 3600000 | 0.31827
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Current Study | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | 109500.27 | 3.042% | 3600000 | 0.04698
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Current Study | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | 87931.94 | 19.12% | 460000 | 0.10316
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Current Study | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | 167820 | 36.48% | 460000 | 0.09141
GEN-2023-205 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Current Study | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | 146347.79 | 31.81% | 460000 | 0.1116
GEN-2023-210 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Current Study | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | 57900.27 | 12.59% | 460000 | 0.04161
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line | Current Study | Rebuild the WHEELER 6 to G23-101-TAP 230 kV line CKT1 (7.3 miles) to a minimum rating of 487 MVA | 6449615.7 | 100% | 6449615.7 | 0.26693
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1 | Current Study | Rebuild the existing FTRANDL4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | 16728042.52 | 19.8% | 84500000 | 0.05023
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1 | Current Study | Rebuild the existing FTRANDL4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | 30871021.33 | 36.53% | 84500000 | 0.09307
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1 | Current Study | Rebuild the existing FTRANDL4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | 20132264.11 | 23.83% | 84500000 | 0.08636
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1 | Current Study | Rebuild the existing FTRANDL4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | 16768672.04 | 19.84% | 84500000 | 0.04196
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | Current Study | Rebuild the existing FTTHOM2-LNX3 to GRPRAR2-LNX3 345 kV line 1 (123.95 miles) to a minimum rating of 1060 MVA | 2202737.76 | 5.507% | 40000000 | 0.11944
GEN-2023-082 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | Current Study | Rebuild the existing FTTHOM2-LNX3 to GRPRAR2-LNX3 345 kV line 1 (123.95 miles) to a minimum rating of 1060 MVA | 3167814.58 | 7.92% | 40000000 | 0.09678
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | Current Study | Rebuild the existing FTTHOM2-LNX3 to GRPRAR2-LNX3 345 kV line 1 (123.95 miles) to a minimum rating of 1060 MVA | 6883097.24 | 17.21% | 40000000 | 0.1472
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | Current Study | Rebuild the existing FTTHOM2-LNX3 to GRPRAR2-LNX3 345 kV line 1 (123.95 miles) to a minimum rating of 1060 MVA | 13625900.88 | 34.06% | 40000000 | 0.29257
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | Current Study | Rebuild the existing FTTHOM2-LNX3 to GRPRAR2-LNX3 345 kV line 1 (123.95 miles) to a minimum rating of 1060 MVA | 6593558.26 | 16.48% | 40000000 | 0.20144
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | Current Study | Rebuild the existing FTTHOM2-LNX3 to GRPRAR2-LNX3 345 kV line 1 (123.95 miles) to a minimum rating of 1060 MVA | 7526891.28 | 18.82% | 40000000 | 0.13414
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | Current Study | Rebuild the existing FTTHOMP4 to FTRANDL4 230 kV line 1 (87.32 miles) to a minimum rating of 600 MVA | 33256966.33 | 19.8% | 168000000 | 0.04986
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | Current Study | Rebuild the existing FTTHOMP4 to FTRANDL4 230 kV line 1 (87.32 miles) to a minimum rating of 600 MVA | 61378272.66 | 36.53% | 168000000 | 0.09239
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | Current Study | Rebuild the existing FTTHOMP4 to FTRANDL4 230 kV line 1 (87.32 miles) to a minimum rating of 600 MVA | 40027753.84 | 23.83% | 168000000 | 0.08573
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | Current Study | Rebuild the existing FTTHOMP4 to FTRANDL4 230 kV line 1 (87.32 miles) to a minimum rating of 600 MVA | 33337007.17 | 19.84% | 168000000 | 0.04165
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1 | Current Study | Rebuild the existing FTTHOMP4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | 16728042.52 | 19.8% | 84500000 | 0.05023
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1 | Current Study | Rebuild the existing FTTHOMP4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | 30871021.33 | 36.53% | 84500000 | 0.09307
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1 | Current Study | Rebuild the existing FTTHOMP4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | 20132264.11 | 23.83% | 84500000 | 0.08636
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1 | Current Study | Rebuild the existing FTTHOMP4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | 16768672.04 | 19.84% | 84500000 | 0.04196
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Route second Ft. Thompson - Huron 230 kV circuit into G17-094-TAP | Current Study | Loop the second Ft. Thompson - Huron 230 kV circuit into G17-094-TAP and expand the G17-094-TAP substation | 4095456.2523 | 27.3% | 15000000 | 0.073
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Route second Ft. Thompson - Huron 230 kV circuit into G17-094-TAP | Current Study | Loop the second Ft. Thompson - Huron 230 kV circuit into G17-094-TAP and expand the G17-094-TAP substation | 10904543.7477 | 72.7% | 15000000 | 0.27656
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1 | Current Study | Rebuild the existing GROTON 7 to BRISTOL-ER7 115 kV line 1 (21.3 miles) to a minimum rating of 165 MVA | 22150000 | 100% | 22150000 | 0.03538
GEN-2023-033 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Current Study | Rebuild LBRTYST5 to BRMGHAM5 161 kV line 1 to a minimum rating of 275 MVA | 6860856.63 | 76.23% | 9000000 | 0.68618
GEN-2023-169 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Current Study | Rebuild LBRTYST5 to BRMGHAM5 161 kV line 1 to a minimum rating of 275 MVA | 2139143.37 | 23.77% | 9000000 | 0.34231
GEN-2023-011 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the MARSHAL3 to KNOB HL3 115kV Line 1 | Current Study | Rebuild the existing MARSHAL3 to KNOB HL3 115 kV line 1 (14.21 miles) to a minimum rating of 105 MVA | 20000000 | 100% | 20000000 | 0.11078
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1 | Current Study | Rebuild the existing MEADOWGROVE4 to FTRANDL4 230 kV line 1 (84.17 miles) to a minimum rating of 500 MVA | 13286255.71 | 8.205% | 161923000 | 0.05296
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1 | Current Study | Rebuild the existing MEADOWGROVE4 to FTRANDL4 230 kV line 1 (84.17 miles) to a minimum rating of 500 MVA | 33553682.3 | 20.72% | 161923000 | 0.05275
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1 | Current Study | Rebuild the existing MEADOWGROVE4 to FTRANDL4 230 kV line 1 (84.17 miles) to a minimum rating of 500 MVA | 44829602.37 | 27.69% | 161923000 | 0.07076
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1 | Current Study | Rebuild the existing MEADOWGROVE4 to FTRANDL4 230 kV line 1 (84.17 miles) to a minimum rating of 500 MVA | 33973500.88 | 20.98% | 161923000 | 0.0763
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1 | Current Study | Rebuild the existing MEADOWGROVE4 to FTRANDL4 230 kV line 1 (84.17 miles) to a minimum rating of 500 MVA | 36279958.74 | 22.41% | 161923000 | 0.04753
GEN-2023-006 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 647940.49 | 2.09% | 31000000 | 0.05511
GEN-2023-023 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 1362208.01 | 4.394% | 31000000 | 0.11702
GEN-2023-032 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 1182124.62 | 3.813% | 31000000 | 0.10155
GEN-2023-033 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 1259768.85 | 4.064% | 31000000 | 0.10822
GEN-2023-036 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 1009729.99 | 3.257% | 31000000 | 0.10514
GEN-2023-037 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 1360927.52 | 4.39% | 31000000 | 0.11691
GEN-2023-065 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 117339.4 | 0.3785% | 31000000 | 0.0144
GEN-2023-087 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 1213904.04 | 3.916% | 31000000 | 0.10428
GEN-2023-099 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 1383277.88 | 4.462% | 31000000 | 0.07922
GEN-2023-149 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 3547596.15 | 11.44% | 31000000 | 0.20317
GEN-2023-169 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 753160.64 | 2.43% | 31000000 | 0.10352
GEN-2023-170 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 511526.45 | 1.65% | 31000000 | 0.05859
GEN-2023-171 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 958795.61 | 3.093% | 31000000 | 0.10982
GEN-2023-219 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 515688.04 | 1.664% | 31000000 | 0.07088
GEN-2023-220 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 1150839.94 | 3.712% | 31000000 | 0.07909
GEN-2023-221 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 1136870.96 | 3.667% | 31000000 | 0.07813
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Current Study | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | 12888301.4 | 41.58% | 31000000 | 0.7143
GEN-2023-065 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the NEWTON 2 to ADAMS 2 69 kV Line 1 | Current Study | Rebuild NEWTON 2 to ADAMS 2 69 kV line 1 to a minimum rating of 82 MVA | 4500000 | 100% | 4500000 | 0.22474
GEN-2023-194 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | Current Study | Rebuild ORO110 to RIV4525 161 kV line 1 line to a minimum rating of 558 MVA | 25592475 | 100% | 25592475 | 0.16073
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1 | Current Study | Rebuild the existing PAHOJA__-BE4 to EAGLE___-NI4 230 kV line 1 (22.24 miles) to a minimum rating of 450 MVA | 6011864.53 | 13.33% | 45100000 | 0.08677
GEN-2023-082 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1 | Current Study | Rebuild the existing PAHOJA__-BE4 to EAGLE___-NI4 230 kV line 1 (22.24 miles) to a minimum rating of 450 MVA | 7754515.85 | 17.19% | 45100000 | 0.06306
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1 | Current Study | Rebuild the existing PAHOJA__-BE4 to EAGLE___-NI4 230 kV line 1 (22.24 miles) to a minimum rating of 450 MVA | 7436198.09 | 16.49% | 45100000 | 0.04233
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1 | Current Study | Rebuild the existing PAHOJA__-BE4 to EAGLE___-NI4 230 kV line 1 (22.24 miles) to a minimum rating of 450 MVA | 7948858.34 | 17.62% | 45100000 | 0.04543
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1 | Current Study | Rebuild the existing PAHOJA__-BE4 to EAGLE___-NI4 230 kV line 1 (22.24 miles) to a minimum rating of 450 MVA | 7016693.22 | 15.56% | 45100000 | 0.05706
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1 | Current Study | Rebuild the existing PAHOJA__-BE4 to EAGLE___-NI4 230 kV line 1 (22.24 miles) to a minimum rating of 450 MVA | 8931869.97 | 19.8% | 45100000 | 0.04237
GEN-2023-116 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Current Study | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | 2829388.34 | 9.108% | 31064000 | 0.04301
GEN-2023-117 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Current Study | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | 1697633.01 | 5.465% | 31064000 | 0.04301
GEN-2023-133 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Current Study | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | 1007488.55 | 3.243% | 31064000 | 0.03063
GEN-2023-153 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Current Study | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | 742837.79 | 2.391% | 31064000 | 0.04705
GEN-2023-199 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Current Study | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | 6438322.18 | 20.73% | 31064000 | 0.19574
GEN-2023-216 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Current Study | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | 6116110.04 | 19.69% | 31064000 | 0.23243
GEN-2023-217 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Current Study | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | 6116110.04 | 19.69% | 31064000 | 0.23243
GEN-2023-218 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Current Study | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | 6116110.04 | 19.69% | 31064000 | 0.23243
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1 | Current Study | Rebuild the existing SIOUXFL4 to PAHOJA__-BE4 230 kV line 1 (20.19 miles) to a minimum rating of 500 MVA | 5598632.15 | 13.33% | 42000000 | 0.08677
GEN-2023-082 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1 | Current Study | Rebuild the existing SIOUXFL4 to PAHOJA__-BE4 230 kV line 1 (20.19 miles) to a minimum rating of 500 MVA | 7221500.35 | 17.19% | 42000000 | 0.06306
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1 | Current Study | Rebuild the existing SIOUXFL4 to PAHOJA__-BE4 230 kV line 1 (20.19 miles) to a minimum rating of 500 MVA | 6925062.52 | 16.49% | 42000000 | 0.04233
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1 | Current Study | Rebuild the existing SIOUXFL4 to PAHOJA__-BE4 230 kV line 1 (20.19 miles) to a minimum rating of 500 MVA | 7402484.48 | 17.62% | 42000000 | 0.04543
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1 | Current Study | Rebuild the existing SIOUXFL4 to PAHOJA__-BE4 230 kV line 1 (20.19 miles) to a minimum rating of 500 MVA | 6534392.8 | 15.56% | 42000000 | 0.05706
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1 | Current Study | Rebuild the existing SIOUXFL4 to PAHOJA__-BE4 230 kV line 1 (20.19 miles) to a minimum rating of 500 MVA | 8317927.69 | 19.8% | 42000000 | 0.04237
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Rebuild the SUMMIT-7 to BRISTOL-ER7 115kV Line 1 | Current Study | Rebuild the existing SUMMIT-7 to BRISTOL-ER7 115 kV line 1 (32.56 miles) to a minimum rating of 160 MVA | 33150000 | 100% | 33150000 | 0.03538
GEN-2023-116 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1 | Current Study | Rebuild the existing SWEET W3 to GR ISLD3 345 kV line 1 (63.14 miles) to a minimum rating of 815 MVA | 48807065.86 | 35.14% | 138908000 | 0.16961
GEN-2023-117 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1 | Current Study | Rebuild the existing SWEET W3 to GR ISLD3 345 kV line 1 (63.14 miles) to a minimum rating of 815 MVA | 29284239.52 | 21.08% | 138908000 | 0.16961
GEN-2023-133 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1 | Current Study | Rebuild the existing SWEET W3 to GR ISLD3 345 kV line 1 (63.14 miles) to a minimum rating of 815 MVA | 50369605.62 | 36.26% | 138908000 | 0.35008
GEN-2023-153 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1 | Current Study | Rebuild the existing SWEET W3 to GR ISLD3 345 kV line 1 (63.14 miles) to a minimum rating of 815 MVA | 10447089 | 7.521% | 138908000 | 0.15127
GEN-2023-006 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 1944418.747 | 9.889% | 19662160 | 0.01536
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 8871310.264 | 45.12% | 19662160 | 0.03539
GEN-2023-062 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 91508.1043 | 0.4654% | 19662160 | 0.00149
GEN-2023-077 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 298833.3074 | 1.52% | 19662160 | 0.00187
GEN-2023-078 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 298833.3074 | 1.52% | 19662160 | 0.00187
GEN-2023-079 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 355084.2829 | 1.806% | 19662160 | 0.00187
GEN-2023-183 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 386211.5774 | 1.964% | 19662160 | 0.00284
GEN-2023-222 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 470299.7669 | 2.392% | 19662160 | 0.00157
GEN-2023-223 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 235149.8835 | 1.196% | 19662160 | 0.00157
GEN-2023-224 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 485277.4665 | 2.468% | 19662160 | 0.00162
GEN-2023-225 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 220303.7871 | 1.12% | 19662160 | 0.00162
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Reconfigure the Neosho Transformers | Current Study | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | 6004929.5056 | 30.54% | 19662160 | 0.03091
GEN-2023-085 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI) | Current Study | Upgrade Terminal Equipment at 5MANSFDMN to achieve a minimum rating of 231 MVA (Owned by AECI, will be addressed in the AFS) | $- | 100% | $- | 0.6865
GEN-2023-061 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1 | Current Study | Upgrade Terminal Equipment at CARTHAG5 to achieve a minimum summer/winter rating of 303/326 MVA | 250000 | 100% | 250000 | 0.23958
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line 1 | Current Study | Upgrade Terminal Equipment on the RIV4525 to G20-079-TAP 161 kV Line 1 to a minimum Rate B of 607 MVA | 535810.82 | 10.37% | 5165042 | 0.02575
GEN-2023-194 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line 1 | Current Study | Upgrade Terminal Equipment on the RIV4525 to G20-079-TAP 161 kV Line 1 to a minimum Rate B of 607 MVA | 4258486.51 | 82.45% | 5165042 | 0.36383
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line 1 | Current Study | Upgrade Terminal Equipment on the RIV4525 to G20-079-TAP 161 kV Line 1 to a minimum Rate B of 607 MVA | 370744.67 | 7.178% | 5165042 | 0.02299
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 28917.81 | 0.357% | 8100000 | 0.03592
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 304224.71 | 3.756% | 8100000 | 0.03286
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 317387.47 | 3.918% | 8100000 | 0.0308
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 422206.48 | 5.212% | 8100000 | 0.03746
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 317387.47 | 3.918% | 8100000 | 0.0308
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 882045.56 | 10.89% | 8100000 | 0.03506
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 471202.53 | 5.817% | 8100000 | 0.03902
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 394882.69 | 4.875% | 8100000 | 0.03924
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 164784.02 | 2.034% | 8100000 | 0.03149
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 478043.54 | 5.902% | 8100000 | 0.04167
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 340943.57 | 4.209% | 8100000 | 0.0308
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 247958.96 | 3.061% | 8100000 | 0.0308
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 406161.6 | 5.014% | 8100000 | 0.03012
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 206111.86 | 2.545% | 8100000 | 0.03012
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 371938.44 | 4.592% | 8100000 | 0.0308
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 248280.98 | 3.065% | 8100000 | 0.03084
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 290627.22 | 3.588% | 8100000 | 0.0361
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 306829.08 | 3.788% | 8100000 | 0.03049
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 414324.93 | 5.115% | 8100000 | 0.03431
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 383289.8 | 4.732% | 8100000 | 0.03174
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 349074.69 | 4.31% | 8100000 | 0.04336
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 213341.31 | 2.634% | 8100000 | 0.0424
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | Current Study | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | 540035.29 | 6.667% | 8100000 | 0.03354
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Upgrade the existing FIXICO4 138/69 kV Transformer | Current Study | Upgrade the existing FIXICO 138/69 kV Transformer to a minimum rating of 75 MVA | 7000000 | 100% | 7000000 | 0.07482
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Upgrade the existing GROVE 161/138 kV Transformer | Current Study | Upgrade the GROVE 161/138 kV Transformer to a minimum rating of 136 MVA | 7000000 | 100% | 7000000 | 0.20537
GEN-2023-032 | DISIS-2023-001 | 03 CENTRAL | TBD | NRIS | Upgrade the existing LEX161 5 161/69 kV Transformer | Current Study | Upgrade the existing LEX161 5 161/69 kV Transformer CKT1 to a minimum MVA of 83 | 4832450 | 100% | 4832450 | 0.03866
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing PLANTX 230/115 kV Transformer | Current Study | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | 1385444.2 | 17.1% | 8100000 | 0.06083
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing PLANTX 230/115 kV Transformer | Current Study | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | 1385444.2 | 17.1% | 8100000 | 0.06083
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing PLANTX 230/115 kV Transformer | Current Study | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | 1488270.13 | 18.37% | 8100000 | 0.06083
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing PLANTX 230/115 kV Transformer | Current Study | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | 1082378.28 | 13.36% | 8100000 | 0.06083
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing PLANTX 230/115 kV Transformer | Current Study | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | 752851.65 | 9.294% | 8100000 | 0.02526
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing PLANTX 230/115 kV Transformer | Current Study | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | 382044.12 | 4.717% | 8100000 | 0.02526
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing PLANTX 230/115 kV Transformer | Current Study | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | 1623567.42 | 20.04% | 8100000 | 0.06083
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 39132.21 | 0.2386% | 16400000 | 0.05916
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 505093.97 | 3.08% | 16400000 | 0.0664
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 995519.31 | 6.07% | 16400000 | 0.11758
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 468142.93 | 2.855% | 16400000 | 0.18873
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 437928.91 | 2.67% | 16400000 | 0.04729
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 995519.31 | 6.07% | 16400000 | 0.11758
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 1318794 | 8.041% | 16400000 | 0.0638
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 758831.59 | 4.627% | 16400000 | 0.07648
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 544404.78 | 3.32% | 16400000 | 0.12662
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 521061.71 | 3.177% | 16400000 | 0.05528
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 1069405.51 | 6.521% | 16400000 | 0.11758
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 777749.46 | 4.742% | 16400000 | 0.11758
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 1265170.76 | 7.714% | 16400000 | 0.11419
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 642026.96 | 3.915% | 16400000 | 0.11419
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 1166624.19 | 7.114% | 16400000 | 0.11758
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 751158.61 | 4.58% | 16400000 | 0.11356
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 387750.24 | 2.364% | 16400000 | 0.05862
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 965902.92 | 5.89% | 16400000 | 0.11682
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 616649.89 | 3.76% | 16400000 | 0.06215
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 674494.92 | 4.113% | 16400000 | 0.06798
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 414737.98 | 2.529% | 16400000 | 0.0627
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 283396.02 | 1.728% | 16400000 | 0.06855
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | Current Study | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | 800503.83 | 4.881% | 16400000 | 0.06051
GEN-2023-056 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Upgrade the existing VBI2 161/69 kV Transformer | Current Study | Upgrade the existing VBI2 161/69 kV Transformer to a minimum rating of 123 MVA. | 50000 | 100% | 50000 | 0.04042
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Upgrade the existing WLK X1 161/138 kV Transformer | Current Study | Upgrade the existing WLK X1 161/138 kV Transformer to a minimum rating of 129 MVA | 1542292.5 | 42.77% | 3606166 | 0.08751
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Upgrade the existing WLK X1 161/138 kV Transformer | Current Study | Upgrade the existing WLK X1 161/138 kV Transformer to a minimum rating of 129 MVA | 2063873.5 | 57.23% | 3606166 | 0.05437
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the exsting PRINGLE6 230/115 kV Transformer | Current Study | Upgrade the PRINGLE6 230/115 kV Transformer to a minimum rating of 287 MVA | 8100000 | 100% | 8100000 | 0.41449
GEN-2023-006 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 321054.62 | 2.675% | 12000000 | 0.03287
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 2322514.98 | 19.35% | 12000000 | 0.12008
GEN-2023-059 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 330351.06 | 2.753% | 12000000 | 0.03416
GEN-2023-062 | DISIS-2023-001 | 01 NORTH | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 204425.03 | 1.704% | 12000000 | 0.04314
GEN-2023-077 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 573968.05 | 4.783% | 12000000 | 0.04655
GEN-2023-078 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 573968.05 | 4.783% | 12000000 | 0.04655
GEN-2023-079 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 682009.1 | 5.683% | 12000000 | 0.04655
GEN-2023-183 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 524215.69 | 4.368% | 12000000 | 0.04996
GEN-2023-204 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 1657990.02 | 13.82% | 12000000 | 0.03598
GEN-2023-222 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 1099946.23 | 9.166% | 12000000 | 0.04759
GEN-2023-223 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 549973.11 | 4.583% | 12000000 | 0.04759
GEN-2023-224 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 1095323.63 | 9.128% | 12000000 | 0.04739
GEN-2023-225 | DISIS-2023-001 | 02 NEBRASKA | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 497249.43 | 4.144% | 12000000 | 0.04739
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | Upgrade the Neosho 345/161 kV Transformer | Current Study | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | 1567010.99 | 13.06% | 12000000 | 0.10454
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | TBD | NRIS | WARD4 to BISMARK4 230 kV Ckt 1 Terminal Upgrade | Current Study | Upgrade Terminal Equipment on the WARD4 to BISMARK4 230 kV line Ckt 1 to achieve a rating of 382 MVA | 4000000 | 100% | 4000000 | 0.0278
GEN-2023-087 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | Contingent | Upgrade Terminal Equipment at ARCHIE 5 161 kV to achieve a minimum rating of 249 MVA | $- | 0% | 150000 | N/A
GEN-2023-219 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | Contingent | Build a 2nd LANG 3 to G22-007-TAP 115 kV line (0.41mi approx.) | $- | 0% | 22000000 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Contingent | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | $- | 0% | 6222750 | N/A
GEN-2023-107 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Contingent | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | $- | 0% | 6222750 | N/A
GEN-2023-172 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Contingent | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | $- | 0% | 6222750 | N/A
GEN-2023-173 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Contingent | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | $- | 0% | 6222750 | N/A
GEN-2023-199 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | $- | 0% | 61000000 | N/A
GEN-2023-216 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | $- | 0% | 61000000 | N/A
GEN-2023-217 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | $- | 0% | 61000000 | N/A
GEN-2023-218 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | $- | 0% | 61000000 | N/A
GEN-2023-222 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | $- | 0% | 61000000 | N/A
GEN-2023-223 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | $- | 0% | 61000000 | N/A
GEN-2023-199 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | $- | 0% | 83000000 | N/A
GEN-2023-216 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | $- | 0% | 83000000 | N/A
GEN-2023-217 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | $- | 0% | 83000000 | N/A
GEN-2023-218 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | $- | 0% | 83000000 | N/A
GEN-2023-222 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | $- | 0% | 83000000 | N/A
GEN-2023-223 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | Contingent | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | $- | 0% | 83000000 | N/A
GEN-2023-006 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-009 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-022 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-027 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-028 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-030 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-034 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-035 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-038 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-049 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-055 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-056 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-057 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-059 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-063 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-064 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-065 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-073 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-075 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-076 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-088 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-092 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-132 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-135 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-138 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-151 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-161 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-166 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-167 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-168 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-174 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-177 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-180 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-193 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-204 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-205 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-206 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-210 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-211 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-212 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-213 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-227 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-230 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-241 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Contingent | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | $- | 0% | 83000000 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Contingent | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | $- | 0% | 102596000 | N/A
GEN-2023-107 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Contingent | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | $- | 0% | 102596000 | N/A
GEN-2023-172 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Contingent | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | $- | 0% | 102596000 | N/A
GEN-2023-173 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Contingent | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | $- | 0% | 102596000 | N/A
GEN-2023-199 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Contingent | Build a new AXTELL 7 to KEARNEY7 115 kV line 2 (10.74 miles) to a standard rating of 229/390 MVA | $- | 0% | 78000000 | N/A
GEN-2023-216 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Contingent | Build a new AXTELL 7 to KEARNEY7 115 kV line 2 (10.74 miles) to a standard rating of 229/390 MVA | $- | 0% | 78000000 | N/A
GEN-2023-217 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Contingent | Build a new AXTELL 7 to KEARNEY7 115 kV line 2 (10.74 miles) to a standard rating of 229/390 MVA | $- | 0% | 78000000 | N/A
GEN-2023-218 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Contingent | Build a new AXTELL 7 to KEARNEY7 115 kV line 2 (10.74 miles) to a standard rating of 229/390 MVA | $- | 0% | 78000000 | N/A
GEN-2023-222 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Contingent | Build a new AXTELL 7 to KEARNEY7 115 kV line 2 (10.74 miles) to a standard rating of 229/390 MVA | $- | 0% | 78000000 | N/A
GEN-2023-223 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Contingent | Build a new AXTELL 7 to KEARNEY7 115 kV line 2 (10.74 miles) to a standard rating of 229/390 MVA | $- | 0% | 78000000 | N/A
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.05617
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.04669
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.03641
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.01609
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.04794
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.03641
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.05354
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.05122
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.02298
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.03368
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.04768
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.03641
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.03641
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.03613
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.03613
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.03641
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.03773
GEN-2023-183 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.00733
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.05672
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.00967
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.03682
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.05124
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.04325
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.04992
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.04869
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.00365
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.04891
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line | Contingent | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | 0.00776
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-035 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | Contingent | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 428620878 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Contingent | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | $- | 0% | 44046000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Crossroads to Potter County 345 kV Line | Contingent | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | $- | 0% | 261000000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-009 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-027 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-035 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-038 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-056 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-061 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-063 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-064 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-085 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-088 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-092 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-135 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-151 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-161 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-172 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-173 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-177 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-180 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-205 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-210 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-212 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-213 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | Contingent | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | $- | 0% | 2104646400 | N/A
GEN-2023-062 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Contingent | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | $- | 0% | 250000000 | N/A
GEN-2023-097 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Contingent | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | $- | 0% | 250000000 | N/A
GEN-2023-105 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Contingent | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | $- | 0% | 250000000 | N/A
GEN-2023-182 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Contingent | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | $- | 0% | 250000000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Contingent | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | $- | 0% | 100000000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | Contingent | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | $- | 0% | 184680000 | N/A
GEN-2023-194 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Contingent | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | $- | 0% | 29709558.63 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | $- | 0% | 230353500 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Contingent | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | $- | 0% | 168086100 | N/A
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.52942
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.38356
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.18459
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.12204
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.06642
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.18459
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.42747
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.01324
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.00066
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.093
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.05307
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.18459
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.18459
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.22394
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.22394
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.18459
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.22549
GEN-2023-183 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.1072
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.55927
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.00883
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.21976
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.41915
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.3492
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.04226
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.0282
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.04152
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.40515
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | TBD | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | Contingent | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | $- | 0% | 1301149472 | 0.09288
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build new Tolk to Needmore 230 kV Line | Contingent | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | $- | 0% | 34125000 | N/A
GEN-2023-050 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Contingent | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | $- | 0% | 21623128 | N/A
GEN-2023-057 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Contingent | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | $- | 0% | 21623128 | N/A
GEN-2023-075 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Contingent | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | $- | 0% | 21623128 | N/A
GEN-2023-076 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Contingent | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | $- | 0% | 21623128 | N/A
GEN-2023-194 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Contingent | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | $- | 0% | 21623128 | N/A
GEN-2023-211 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Contingent | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | $- | 0% | 21623128 | N/A
GEN-2023-149 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | Contingent | Build new STILWEL7 to G21-029-TAP 345 kV line to a minimum rating of 1792 MVA | $- | 0% | 89000000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-009 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-027 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-035 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-038 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-056 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-061 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-063 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-064 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-085 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-088 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-092 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-135 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-151 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-161 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-172 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-173 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-177 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-180 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-205 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-210 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-212 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-213 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build the Crawfish Draw 345 kV Substation | Contingent | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | $- | 0% | 18427752 | N/A
GEN-2023-097 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Build Third Ft Thompson 345-230 kV Transformer | Contingent | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | $- | 0% | 16500000 | N/A
GEN-2023-105 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Build Third Ft Thompson 345-230 kV Transformer | Contingent | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | $- | 0% | 16500000 | N/A
GEN-2023-174 | DISIS-2023-001 CF | 04 SOUTHEAST | 143256 143254 143253 143255 | ERIS | Canadian Switch138 kV Terminal Upgrades Lexington - Lil Axe 138 kV Paoli - Lexington kV 138 kV Paoli 138 kV Terminal Upgrades | Contingent | Convert 69 kV terminal equipment at Canadian Switch to 138 kV Convert 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV Rebuild 14.3 miles of 69 kV line from Paoli to Lexington to 138 kV Convert 69 kV terminal equipment at Paoli Switch to 138 kV | $- | 0% | 21382126 | N/A
GEN-2023-063 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Catoosa Terminal Upgrade | Contingent | Replace switch, jumpers, and CTs at Catoosa 138 kV to achieve a minimum rating of 348 MVA | $- | 0% | 4765714 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-035 | DISIS-2023-001 CF | 04 SOUTHEAST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | 143182 | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Contingent | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | $- | 0% | 12238460 | N/A
GEN-2023-009 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | 82111 | NRIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-022 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-027 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-028 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-030 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-035 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-038 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-049 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-055 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-056 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-057 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-059 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-063 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-064 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-075 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-076 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-088 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-092 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-132 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-135 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-138 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-151 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-161 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-166 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-167 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-168 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-172 | DISIS-2023-001 CF | 03 CENTRAL | 82111 | NRIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-173 | DISIS-2023-001 CF | 03 CENTRAL | 82111 | NRIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-174 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-177 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-180 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-193 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-204 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-205 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-206 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-210 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-211 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-212 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-213 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-227 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-230 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-241 | DISIS-2023-001 CF | 04 SOUTHEAST | 82111 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Contingent | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | $- | 0% | 37489652 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Curry - Deafsmith 115 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum normal/emergency rating of 90/90 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 4852215 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Czech Hall 138 kV Terminal Upgrade | Contingent | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | $- | 0% | 154916 | N/A
GEN-2023-161 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Czech Hall 138 kV Terminal Upgrade | Contingent | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | $- | 0% | 154916 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Czech Hall 138 kV Terminal Upgrade | Contingent | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | $- | 0% | 154916 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Czech Hall 138 kV Terminal Upgrade | Contingent | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | $- | 0% | 154916 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Czech Hall 138 kV Terminal Upgrade | Contingent | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | $- | 0% | 154916 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Czech Hall 138 kV Terminal Upgrade | Contingent | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | $- | 0% | 154916 | N/A
GEN-2023-028 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | Contingent | Upgrade Terminal Equipment on the DRYGULCH to G23-028-TAP line Ckt 1 to achieve a rating of 443 MVA | $- | 0% | 254602 | N/A
GEN-2023-049 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | Contingent | Upgrade Terminal Equipment on the DRYGULCH to G23-028-TAP line Ckt 1 to achieve a rating of 443 MVA | $- | 0% | 254602 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-035 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | Contingent | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | $- | 0% | 117410790.53 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to G16-037-Tap 345 kV New Line | Contingent | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | $- | 0% | 88218000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to G22-114-Tap 345 kV New Line | Contingent | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | $- | 0% | 140400000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Minco 345 kV New Line | Contingent | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | $- | 0% | 37206000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-009 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-088 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-092 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-210 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Gracemont to Treasure Island 345 kV New Line | Contingent | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | $- | 0% | 17442000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Hobbs to Andrews Voltage Conversion | Contingent | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | $- | 0% | 53295780 | N/A
GEN-2023-027 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | HOC404 5 to BAX488 5 161kV Line Rebuild | Contingent | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | $- | 0% | 2543382.4 | N/A
GEN-2023-028 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | HOC404 5 to BAX488 5 161kV Line Rebuild | Contingent | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | $- | 0% | 2543382.4 | N/A
GEN-2023-049 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | HOC404 5 to BAX488 5 161kV Line Rebuild | Contingent | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | $- | 0% | 2543382.4 | N/A
GEN-2023-055 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | HOC404 5 to BAX488 5 161kV Line Rebuild | Contingent | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | $- | 0% | 2543382.4 | N/A
GEN-2023-063 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | HOC404 5 to BAX488 5 161kV Line Rebuild | Contingent | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | $- | 0% | 2543382.4 | N/A
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | 156301 | NRIS | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Contingent | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.12159
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | 156301 | NRIS | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Contingent | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.0521
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | 156301 | NRIS | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Contingent | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.08381
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | 156301 | NRIS | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Contingent | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.39658
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | 156301 | NRIS | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Contingent | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.01933
GEN-2023-061 | DISIS-2023-001 | 03 CENTRAL | 156301 | NRIS | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Contingent | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.01955
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | 156301 | NRIS | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Contingent | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.03605
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | 156304 | NRIS | Kerr - Maid 161 kV Ckt 2 Rebuild | Contingent | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.12159
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | 156304 | NRIS | Kerr - Maid 161 kV Ckt 2 Rebuild | Contingent | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.0521
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | 156304 | NRIS | Kerr - Maid 161 kV Ckt 2 Rebuild | Contingent | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.08381
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | 156304 | NRIS | Kerr - Maid 161 kV Ckt 2 Rebuild | Contingent | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.39658
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | 156304 | NRIS | Kerr - Maid 161 kV Ckt 2 Rebuild | Contingent | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.01933
GEN-2023-061 | DISIS-2023-001 | 03 CENTRAL | 156304 | NRIS | Kerr - Maid 161 kV Ckt 2 Rebuild | Contingent | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.01955
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | 156304 | NRIS | Kerr - Maid 161 kV Ckt 2 Rebuild | Contingent | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | $- | 0% | 4923250 | 0.03605
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to Draper 345 kV New Line | Contingent | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | $- | 0% | 352800000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-009 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-022 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-027 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-038 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-063 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-088 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-092 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-161 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-177 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-210 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-213 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | Contingent | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | $- | 0% | 184860000 | N/A
GEN-2023-150 | DISIS-2023-001 | 04 SOUTHEAST | 158637, 157395, 157396, 157897, 157879 | NRIS | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Contingent | Build new 15-mile 138 kV Ckt 2 & Ckt 3 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | $- | 0% | 27744395 | 0.16134
GEN-2023-164 | DISIS-2023-001 | 04 SOUTHEAST | 158637, 157395, 157396, 157897, 157879 | NRIS | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Contingent | Build new 15-mile 138 kV Ckt 2 & Ckt 3 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | $- | 0% | 27744395 | 0.02784
GEN-2023-165 | DISIS-2023-001 | 04 SOUTHEAST | 158637, 157395, 157396, 157897, 157879 | NRIS | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Contingent | Build new 15-mile 138 kV Ckt 2 & Ckt 3 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | $- | 0% | 27744395 | 0.02784
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | 158637, 157395, 157396, 157897, 157879 | NRIS | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Contingent | Build new 15-mile 138 kV Ckt 2 & Ckt 3 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | $- | 0% | 27744395 | 0.02634
GEN-2023-009 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01242
GEN-2023-022 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01969
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.04162
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.04148
GEN-2023-030 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01498
GEN-2023-035 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.001
GEN-2023-038 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01137
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.04167
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.04096
GEN-2023-056 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.02619
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.02209
GEN-2023-059 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01464
GEN-2023-063 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.04458
GEN-2023-064 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.02634
GEN-2023-069 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01218
GEN-2023-075 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.1096
GEN-2023-076 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.1096
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.02212
GEN-2023-092 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01194
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.03685
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01345
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.03685
GEN-2023-104 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.02707
GEN-2023-132 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01651
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01805
GEN-2023-135 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.0137
GEN-2023-138 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.04028
GEN-2023-150 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.00106
GEN-2023-151 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01507
GEN-2023-161 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.0051
GEN-2023-164 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.00195
GEN-2023-165 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.00195
GEN-2023-166 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.00303
GEN-2023-167 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.00375
GEN-2023-168 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.00281
GEN-2023-174 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.00409
GEN-2023-177 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.00744
GEN-2023-180 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.02503
GEN-2023-193 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01446
GEN-2023-204 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.18
GEN-2023-205 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.02197
GEN-2023-206 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.02527
GEN-2023-210 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01259
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.02785
GEN-2023-212 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01376
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.03904
GEN-2023-227 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01437
GEN-2023-229 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.00098
GEN-2023-230 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01475
GEN-2023-241 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Contingent | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | $- | 0% | 484090326 | 0.01438
GEN-2023-009 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.01572
GEN-2023-011 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.08513
GEN-2023-022 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02327
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02454
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02435
GEN-2023-030 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.00223
GEN-2023-035 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02898
GEN-2023-038 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02435
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02417
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02454
GEN-2023-056 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.00934
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.03433
GEN-2023-059 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.0006
GEN-2023-063 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02878
GEN-2023-064 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.0121
GEN-2023-069 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02266
GEN-2023-075 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.03083
GEN-2023-076 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.03083
GEN-2023-077 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.07664
GEN-2023-078 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.07664
GEN-2023-079 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.07664
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02529
GEN-2023-092 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.01699
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.0327
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.0258
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.0327
GEN-2023-104 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.03414
GEN-2023-116 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.0864
GEN-2023-117 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.0864
GEN-2023-132 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.01573
GEN-2023-133 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.10872
GEN-2023-134 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02622
GEN-2023-135 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.0084
GEN-2023-138 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02315
GEN-2023-150 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.0285
GEN-2023-151 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.00307
GEN-2023-153 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.07854
GEN-2023-161 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.0304
GEN-2023-164 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02846
GEN-2023-165 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02846
GEN-2023-166 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.03077
GEN-2023-167 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.03026
GEN-2023-168 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.03041
GEN-2023-174 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02761
GEN-2023-177 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02686
GEN-2023-180 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.00735
GEN-2023-193 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.00215
GEN-2023-199 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.06798
GEN-2023-204 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.0925
GEN-2023-205 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02495
GEN-2023-206 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.00756
GEN-2023-210 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02817
GEN-2023-211 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.05819
GEN-2023-212 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.00834
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.0216
GEN-2023-216 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.10582
GEN-2023-217 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.10582
GEN-2023-218 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.10582
GEN-2023-222 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.15047
GEN-2023-223 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.15047
GEN-2023-224 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.1279
GEN-2023-225 | DISIS-2023-001 | 02 NEBRASKA | 170380/170392/170393 | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 137721276 | 0.1279
GEN-2023-227 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.00335
GEN-2023-229 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.02842
GEN-2023-230 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.00016
GEN-2023-241 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Contingent | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | $- | 0% | 148419672 | 0.00314
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02872
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02775
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02706
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02449
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.03459
GEN-2023-011 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.03374
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | 169968/170009/170008/170565/170568 | NRIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | N/A
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02706
GEN-2023-077 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01664
GEN-2023-078 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01664
GEN-2023-079 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01664
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02846
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.0297
GEN-2023-100 | DISIS-2023-001 | 04 SOUTHEAST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01931
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02179
GEN-2023-102 | DISIS-2023-001 | 04 SOUTHEAST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01931
GEN-2023-110 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02547
GEN-2023-116 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.12896
GEN-2023-117 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.12896
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02715
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.03237
GEN-2023-133 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.06888
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02706
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02706
GEN-2023-150 | DISIS-2023-001 | 04 SOUTHEAST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.013
GEN-2023-153 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.11971
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02686
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02686
GEN-2023-161 | DISIS-2023-001 | 04 SOUTHEAST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01357
GEN-2023-164 | DISIS-2023-001 | 04 SOUTHEAST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01346
GEN-2023-165 | DISIS-2023-001 | 04 SOUTHEAST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01346
GEN-2023-172 | DISIS-2023-001 CF | 03 CENTRAL | 169968/170009/170008/170565/170568 | NRIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | N/A
GEN-2023-173 | DISIS-2023-001 CF | 03 CENTRAL | 169968/170009/170008/170565/170568 | NRIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | N/A
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02706
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02708
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02877
GEN-2023-188 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02054
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02697
GEN-2023-199 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.0369
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02821
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.0274
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.03049
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.03016
GEN-2023-216 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.04404
GEN-2023-217 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.04404
GEN-2023-218 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.04404
GEN-2023-222 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01827
GEN-2023-223 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01827
GEN-2023-224 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01896
GEN-2023-225 | DISIS-2023-001 | 02 NEBRASKA | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.01896
GEN-2023-228 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02203
GEN-2023-229 | DISIS-2023-001 | 04 SOUTHEAST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.013
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02797
GEN-2023-237 | DISIS-2023-001 | 05 SOUTHWEST | 169968/170009/170008/170565/170568 | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Contingent | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | $- | 0% | 977728865 | 0.02344
GEN-2023-199 | DISIS-2023-001 | 02 NEBRASKA | 170229, 170230, 170231 | ERIS | Line - Holt County 345 kV - Antelope 345 kV New Line | Contingent | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Holt County 345 kV Ck1 substation to support a new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ckt1 substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Antelope 345 kV Ck1 substation to support a new line from Antelope 345 kV Ck1 substation to Holt County 345 kV Ck1 substation with a summer emergency rating of 1792 MVA. | $- | 0% | 94400000 | 0.11585
GEN-2023-216 | DISIS-2023-001 | 02 NEBRASKA | 170229, 170230, 170231 | ERIS | Line - Holt County 345 kV - Antelope 345 kV New Line | Contingent | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Holt County 345 kV Ck1 substation to support a new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ckt1 substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Antelope 345 kV Ck1 substation to support a new line from Antelope 345 kV Ck1 substation to Holt County 345 kV Ck1 substation with a summer emergency rating of 1792 MVA. | $- | 0% | 94400000 | 0.20583
GEN-2023-217 | DISIS-2023-001 | 02 NEBRASKA | 170229, 170230, 170231 | ERIS | Line - Holt County 345 kV - Antelope 345 kV New Line | Contingent | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Holt County 345 kV Ck1 substation to support a new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ckt1 substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Antelope 345 kV Ck1 substation to support a new line from Antelope 345 kV Ck1 substation to Holt County 345 kV Ck1 substation with a summer emergency rating of 1792 MVA. | $- | 0% | 94400000 | 0.20583
GEN-2023-218 | DISIS-2023-001 | 02 NEBRASKA | 170229, 170230, 170231 | ERIS | Line - Holt County 345 kV - Antelope 345 kV New Line | Contingent | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Holt County 345 kV Ck1 substation to support a new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ckt1 substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Antelope 345 kV Ck1 substation to support a new line from Antelope 345 kV Ck1 substation to Holt County 345 kV Ck1 substation with a summer emergency rating of 1792 MVA. | $- | 0% | 94400000 | 0.20583
GEN-2023-012 | DISIS-2023-001 CF | 01 NORTH | TBD | NRIS | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Contingent | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. Increase ground clearance of the Whitlock - Glenham 230 kV. | $- | 0% | 389405 | N/A
GEN-2023-105 | DISIS-2023-001 CF | 01 NORTH | TBD | NRIS | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Contingent | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. Increase ground clearance of the Whitlock - Glenham 230 kV. | $- | 0% | 389405 | N/A
GEN-2023-153 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | NRIS | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Contingent | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. Increase ground clearance of the Whitlock - Glenham 230 kV. | $- | 0% | 389405 | N/A
GEN-2023-077 | DISIS-2023-001 | 02 NEBRASKA | 143660 | ERIS | Line - S3454 - S3740 345 kV | Contingent | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | $- | 0% | 64071687 | 0.26283
GEN-2023-078 | DISIS-2023-001 | 02 NEBRASKA | 143660 | ERIS | Line - S3454 - S3740 345 kV | Contingent | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | $- | 0% | 64071687 | 0.26283
GEN-2023-079 | DISIS-2023-001 | 02 NEBRASKA | 143660 | ERIS | Line - S3454 - S3740 345 kV | Contingent | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | $- | 0% | 64071687 | 0.26283
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.05575
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.06111
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.06103
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.06092
GEN-2023-057 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.01785
GEN-2023-063 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.03989
GEN-2023-075 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.05916
GEN-2023-076 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.05916
GEN-2023-088 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.02175
GEN-2023-138 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.06857
GEN-2023-213 | DISIS-2023-001 | 04 SOUTHEAST | 122598 | ERIS | Line - Wolf Creek - Blackberry 345 kV | Contingent | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | $- | 0% | 87298154 | 0.05737
GEN-2023-204 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | LYDIA7 to WELSH Line Rebuild | Contingent | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | $- | 0% | 126087000 | N/A
GEN-2023-033 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Contingent | Terminal Upgrade on Martin City East to Martin City West 161 kV line | $- | 0% | 786451 | N/A
GEN-2023-149 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Contingent | Terminal Upgrade on Martin City East to Martin City West 161 kV line | $- | 0% | 786451 | N/A
GEN-2023-169 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Contingent | Terminal Upgrade on Martin City East to Martin City West 161 kV line | $- | 0% | 786451 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Maud Tap 138 kV Terminal Upgrade | Contingent | Terminal Upgrade on Maud Tap 138 kV | $- | 0% | 736625 | N/A
GEN-2023-027 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | MIAMI to HOC404 5 161kV Line Rebuild | Current Study | Rebuild the MIAMI 5 to HOC404 5 161 kV line CKT1 (9.9 miles) to a minimum rating of 359 MVA | 856618.23 | 8.284% | 10340522 | 0.04431
GEN-2023-028 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | MIAMI to HOC404 5 161kV Line Rebuild | Current Study | Rebuild the MIAMI 5 to HOC404 5 161 kV line CKT1 (9.9 miles) to a minimum rating of 359 MVA | 4724204.7505 | 45.69% | 10340522 | 0.15937
GEN-2023-049 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | MIAMI to HOC404 5 161kV Line Rebuild | Current Study | Rebuild the MIAMI 5 to HOC404 5 161 kV line CKT1 (9.9 miles) to a minimum rating of 359 MVA | 3784702.1179 | 36.6% | 10340522 | 0.19577
GEN-2023-055 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | MIAMI to HOC404 5 161kV Line Rebuild | Current Study | Rebuild the MIAMI 5 to HOC404 5 161 kV line CKT1 (9.9 miles) to a minimum rating of 359 MVA | 974996.9 | 9.429% | 10340522 | 0.07565
GEN-2023-027 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | MIAMI to HOC404 5 161kV Line Rebuild | Contingent | Rebuild the MIAMI 5 to HOC404 5 161 kV line CKT1 (9.9 miles) to a minimum rating of 359 MVA | $- | 0% | 10340522 | N/A
GEN-2023-028 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | MIAMI to HOC404 5 161kV Line Rebuild | Contingent | Rebuild the MIAMI 5 to HOC404 5 161 kV line CKT1 (9.9 miles) to a minimum rating of 359 MVA | $- | 0% | 10340522 | N/A
GEN-2023-049 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | MIAMI to HOC404 5 161kV Line Rebuild | Contingent | Rebuild the MIAMI 5 to HOC404 5 161 kV line CKT1 (9.9 miles) to a minimum rating of 359 MVA | $- | 0% | 10340522 | N/A
GEN-2023-055 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | MIAMI to HOC404 5 161kV Line Rebuild | Contingent | Rebuild the MIAMI 5 to HOC404 5 161 kV line CKT1 (9.9 miles) to a minimum rating of 359 MVA | $- | 0% | 10340522 | N/A
GEN-2023-149 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Multi - Atlantic- Craig - West Gardener 345/115 kV | Contingent | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | $- | 0% | 28123307 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Contingent | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | $- | 0% | 359465155 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Contingent | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | $- | 0% | 359465155 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Contingent | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | $- | 0% | 359465155 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Contingent | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | $- | 0% | 359465155 | N/A
GEN-2023-012 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | $- | 0% | 496505813 | N/A
GEN-2023-082 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | $- | 0% | 496505813 | N/A
GEN-2023-097 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | $- | 0% | 496505813 | N/A
GEN-2023-105 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | $- | 0% | 496505813 | N/A
GEN-2023-154 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | $- | 0% | 496505813 | N/A
GEN-2023-182 | DISIS-2023-001 CF | 01 NORTH | TBD | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Contingent | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | $- | 0% | 496505813 | N/A
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | 1.697e+77 | ERIS | Multi - Hanson County 115 kV System Reconfig | Contingent | Build a new18.4-mile 69 kV Ckt 1 line from Mount Vernon to Mitchell and upgrade any necessary terminal equipment to achieve a summer emergency rating of 84 MVA. Install 69 kV new substation at Mitchell Build a new 6.2-mile 115 kV Ckt 1 line from Letcher 115 kV substation to Plano 115 kV motor-operated switch and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. Build a new 18.3-mile 69 kV Ckt 1 line from Mitchell 69 kV substation to Hanson County 69 kV substation with a summer emergency rating of 84 MVA. Build a new 18.6-mile 115 kV Ckt 1 line from Plano 115 kV substation to Hanson County 115 kV substation with a summer emergency rating of 139 MVA. Extend the 115 kV line from Letcher to Miner County 3.25 miles to reroute around the new lines to Letcher. Install 115 kV new substation at Hanson County Install 69 kV new Substation at Hanson County Install 9.6 MVAR Capacitor at Hanson County 69 kV substation Install new 115/69 transformer at Hanson County 69 kV substation | $- | 0% | 38232000 | 0.00628
GEN-2023-082 | DISIS-2023-001 | 01 NORTH | 1.697e+77 | ERIS | Multi - Hanson County 115 kV System Reconfig | Contingent | Build a new18.4-mile 69 kV Ckt 1 line from Mount Vernon to Mitchell and upgrade any necessary terminal equipment to achieve a summer emergency rating of 84 MVA. Install 69 kV new substation at Mitchell Build a new 6.2-mile 115 kV Ckt 1 line from Letcher 115 kV substation to Plano 115 kV motor-operated switch and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. Build a new 18.3-mile 69 kV Ckt 1 line from Mitchell 69 kV substation to Hanson County 69 kV substation with a summer emergency rating of 84 MVA. Build a new 18.6-mile 115 kV Ckt 1 line from Plano 115 kV substation to Hanson County 115 kV substation with a summer emergency rating of 139 MVA. Extend the 115 kV line from Letcher to Miner County 3.25 miles to reroute around the new lines to Letcher. Install 115 kV new substation at Hanson County Install 69 kV new Substation at Hanson County Install 9.6 MVAR Capacitor at Hanson County 69 kV substation Install new 115/69 transformer at Hanson County 69 kV substation | $- | 0% | 38232000 | 0.00155
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | 1.697e+77 | ERIS | Multi - Hanson County 115 kV System Reconfig | Contingent | Build a new18.4-mile 69 kV Ckt 1 line from Mount Vernon to Mitchell and upgrade any necessary terminal equipment to achieve a summer emergency rating of 84 MVA. Install 69 kV new substation at Mitchell Build a new 6.2-mile 115 kV Ckt 1 line from Letcher 115 kV substation to Plano 115 kV motor-operated switch and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. Build a new 18.3-mile 69 kV Ckt 1 line from Mitchell 69 kV substation to Hanson County 69 kV substation with a summer emergency rating of 84 MVA. Build a new 18.6-mile 115 kV Ckt 1 line from Plano 115 kV substation to Hanson County 115 kV substation with a summer emergency rating of 139 MVA. Extend the 115 kV line from Letcher to Miner County 3.25 miles to reroute around the new lines to Letcher. Install 115 kV new substation at Hanson County Install 69 kV new Substation at Hanson County Install 9.6 MVAR Capacitor at Hanson County 69 kV substation Install new 115/69 transformer at Hanson County 69 kV substation | $- | 0% | 38232000 | 0.00037
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | 1.697e+77 | ERIS | Multi - Hanson County 115 kV System Reconfig | Contingent | Build a new18.4-mile 69 kV Ckt 1 line from Mount Vernon to Mitchell and upgrade any necessary terminal equipment to achieve a summer emergency rating of 84 MVA. Install 69 kV new substation at Mitchell Build a new 6.2-mile 115 kV Ckt 1 line from Letcher 115 kV substation to Plano 115 kV motor-operated switch and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. Build a new 18.3-mile 69 kV Ckt 1 line from Mitchell 69 kV substation to Hanson County 69 kV substation with a summer emergency rating of 84 MVA. Build a new 18.6-mile 115 kV Ckt 1 line from Plano 115 kV substation to Hanson County 115 kV substation with a summer emergency rating of 139 MVA. Extend the 115 kV line from Letcher to Miner County 3.25 miles to reroute around the new lines to Letcher. Install 115 kV new substation at Hanson County Install 69 kV new Substation at Hanson County Install 9.6 MVAR Capacitor at Hanson County 69 kV substation Install new 115/69 transformer at Hanson County 69 kV substation | $- | 0% | 38232000 | 0.00099
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | 1.697e+77 | ERIS | Multi - Hanson County 115 kV System Reconfig | Contingent | Build a new18.4-mile 69 kV Ckt 1 line from Mount Vernon to Mitchell and upgrade any necessary terminal equipment to achieve a summer emergency rating of 84 MVA. Install 69 kV new substation at Mitchell Build a new 6.2-mile 115 kV Ckt 1 line from Letcher 115 kV substation to Plano 115 kV motor-operated switch and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. Build a new 18.3-mile 69 kV Ckt 1 line from Mitchell 69 kV substation to Hanson County 69 kV substation with a summer emergency rating of 84 MVA. Build a new 18.6-mile 115 kV Ckt 1 line from Plano 115 kV substation to Hanson County 115 kV substation with a summer emergency rating of 139 MVA. Extend the 115 kV line from Letcher to Miner County 3.25 miles to reroute around the new lines to Letcher. Install 115 kV new substation at Hanson County Install 69 kV new Substation at Hanson County Install 9.6 MVAR Capacitor at Hanson County 69 kV substation Install new 115/69 transformer at Hanson County 69 kV substation | $- | 0% | 38232000 | 0.00146
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | 1.697e+77 | ERIS | Multi - Hanson County 115 kV System Reconfig | Contingent | Build a new18.4-mile 69 kV Ckt 1 line from Mount Vernon to Mitchell and upgrade any necessary terminal equipment to achieve a summer emergency rating of 84 MVA. Install 69 kV new substation at Mitchell Build a new 6.2-mile 115 kV Ckt 1 line from Letcher 115 kV substation to Plano 115 kV motor-operated switch and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. Build a new 18.3-mile 69 kV Ckt 1 line from Mitchell 69 kV substation to Hanson County 69 kV substation with a summer emergency rating of 84 MVA. Build a new 18.6-mile 115 kV Ckt 1 line from Plano 115 kV substation to Hanson County 115 kV substation with a summer emergency rating of 139 MVA. Extend the 115 kV line from Letcher to Miner County 3.25 miles to reroute around the new lines to Letcher. Install 115 kV new substation at Hanson County Install 69 kV new Substation at Hanson County Install 9.6 MVAR Capacitor at Hanson County 69 kV substation Install new 115/69 transformer at Hanson County 69 kV substation | $- | 0% | 38232000 | 3e-05
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | 169974,169933,169935,169937,169940,169951,169953,169969,169970,169972,169973,169975,169977,169978,169979 | ERIS | Multi - Madison, SD Area 115 kV System Voltage Conversion | Contingent | Install 115 kV new substation at Lake County Install 115 kV new substation at Madison SE Install 115 kV new substation at Howard Build a 3-mile 115 kV Ckt 1 line from Madison SE 115 kV substation to Lake County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Convert the 0.9-mile Ckt 1 69kV line from Madison SE to Lakeview to 115 kV Build a 22.2-mile 115 kV Ckt 1 line from Lake County 115 kV substation to Howard 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Build a 6.0-mile 115 kV Ckt 1 line from Howard 115kV substation to Howard City 115kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Build a 12.4-mile 115 kV Ckt 1 line from Howard City 115 kV MOS to Miner County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Convert the 24-mile Ckt 1 69 kV line from Hanlon to Lakeview to 115 kV Install new 115/69 transformer at Lake County 69 kV substation Install 20 MVAR capacitor bank at Hutchinson 115 kV substation | $- | 0% | 34894000 | 0.17149
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | 159230,159073,159118,159121,159123,159144,159162,159166,159176,159181,159183,159185,159192,159195,159212,159214,159220 | ERIS | Multi - Marion Area 115 kV Voltage Conversion Reconfig | Contingent | Install 115 kV new substation at Lake County Install 115 kV new substation at Madison SE Install 115 kV new substation at Howard Build a 3-mile 115 kV Ckt 1 line from Madison SE 115 kV substation to Lake County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Convert the 0.9-mile Ckt 1 69kV line from Madison SE to Lakeview to 115 kV Build a 22.2-mile 115 kV Ckt 1 line from Lake County 115 kV substation to Howard 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Build a 6.0-mile 115 kV Ckt 1 line from Howard 115kV substation to Howard City 115kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Build a 12.4-mile 115 kV Ckt 1 line from Howard City 115 kV MOS to Miner County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Convert the 24-mile Ckt 1 69 kV line from Hanlon to Lakeview to 115 kV Install new 115/69 transformer at Lake County 69 kV substation | $- | 0% | 31469000 | 0.02583
GEN-2023-082 | DISIS-2023-001 | 01 NORTH | 159230,159073,159118,159121,159123,159144,159162,159166,159176,159181,159183,159185,159192,159195,159212,159214,159220 | ERIS | Multi - Marion Area 115 kV Voltage Conversion Reconfig | Contingent | Install 115 kV new substation at Lake County Install 115 kV new substation at Madison SE Install 115 kV new substation at Howard Build a 3-mile 115 kV Ckt 1 line from Madison SE 115 kV substation to Lake County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Convert the 0.9-mile Ckt 1 69kV line from Madison SE to Lakeview to 115 kV Build a 22.2-mile 115 kV Ckt 1 line from Lake County 115 kV substation to Howard 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Build a 6.0-mile 115 kV Ckt 1 line from Howard 115kV substation to Howard City 115kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Build a 12.4-mile 115 kV Ckt 1 line from Howard City 115 kV MOS to Miner County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Convert the 24-mile Ckt 1 69 kV line from Hanlon to Lakeview to 115 kV Install new 115/69 transformer at Lake County 69 kV substation | $- | 0% | 31469000 | 0.0066
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | 159230,159073,159118,159121,159123,159144,159162,159166,159176,159181,159183,159185,159192,159195,159212,159214,159220 | ERIS | Multi - Marion Area 115 kV Voltage Conversion Reconfig | Contingent | Install 115 kV new substation at Lake County Install 115 kV new substation at Madison SE Install 115 kV new substation at Howard Build a 3-mile 115 kV Ckt 1 line from Madison SE 115 kV substation to Lake County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Convert the 0.9-mile Ckt 1 69kV line from Madison SE to Lakeview to 115 kV Build a 22.2-mile 115 kV Ckt 1 line from Lake County 115 kV substation to Howard 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Build a 6.0-mile 115 kV Ckt 1 line from Howard 115kV substation to Howard City 115kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Build a 12.4-mile 115 kV Ckt 1 line from Howard City 115 kV MOS to Miner County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Convert the 24-mile Ckt 1 69 kV line from Hanlon to Lakeview to 115 kV Install new 115/69 transformer at Lake County 69 kV substation | $- | 0% | 31469000 | 0.00296
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | 159230,159073,159118,159121,159123,159144,159162,159166,159176,159181,159183,159185,159192,159195,159212,159214,159220 | ERIS | Multi - Marion Area 115 kV Voltage Conversion Reconfig | Contingent | Install 115 kV new substation at Lake County Install 115 kV new substation at Madison SE Install 115 kV new substation at Howard Build a 3-mile 115 kV Ckt 1 line from Madison SE 115 kV substation to Lake County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Convert the 0.9-mile Ckt 1 69kV line from Madison SE to Lakeview to 115 kV Build a 22.2-mile 115 kV Ckt 1 line from Lake County 115 kV substation to Howard 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Build a 6.0-mile 115 kV Ckt 1 line from Howard 115kV substation to Howard City 115kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Build a 12.4-mile 115 kV Ckt 1 line from Howard City 115 kV MOS to Miner County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Convert the 24-mile Ckt 1 69 kV line from Hanlon to Lakeview to 115 kV Install new 115/69 transformer at Lake County 69 kV substation | $- | 0% | 31469000 | 0.0023
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | 159230,159073,159118,159121,159123,159144,159162,159166,159176,159181,159183,159185,159192,159195,159212,159214,159220 | ERIS | Multi - Marion Area 115 kV Voltage Conversion Reconfig | Contingent | Install 115 kV new substation at Lake County Install 115 kV new substation at Madison SE Install 115 kV new substation at Howard Build a 3-mile 115 kV Ckt 1 line from Madison SE 115 kV substation to Lake County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Convert the 0.9-mile Ckt 1 69kV line from Madison SE to Lakeview to 115 kV Build a 22.2-mile 115 kV Ckt 1 line from Lake County 115 kV substation to Howard 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Build a 6.0-mile 115 kV Ckt 1 line from Howard 115kV substation to Howard City 115kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Build a 12.4-mile 115 kV Ckt 1 line from Howard City 115 kV MOS to Miner County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Convert the 24-mile Ckt 1 69 kV line from Hanlon to Lakeview to 115 kV Install new 115/69 transformer at Lake County 69 kV substation | $- | 0% | 31469000 | 0.00351
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | 159230,159073,159118,159121,159123,159144,159162,159166,159176,159181,159183,159185,159192,159195,159212,159214,159220 | ERIS | Multi - Marion Area 115 kV Voltage Conversion Reconfig | Contingent | Install 115 kV new substation at Lake County Install 115 kV new substation at Madison SE Install 115 kV new substation at Howard Build a 3-mile 115 kV Ckt 1 line from Madison SE 115 kV substation to Lake County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Convert the 0.9-mile Ckt 1 69kV line from Madison SE to Lakeview to 115 kV Build a 22.2-mile 115 kV Ckt 1 line from Lake County 115 kV substation to Howard 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Build a 6.0-mile 115 kV Ckt 1 line from Howard 115kV substation to Howard City 115kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Build a 12.4-mile 115 kV Ckt 1 line from Howard City 115 kV MOS to Miner County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Convert the 24-mile Ckt 1 69 kV line from Hanlon to Lakeview to 115 kV Install new 115/69 transformer at Lake County 69 kV substation | $- | 0% | 31469000 | 0.00377
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-009 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-009 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-027 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-035 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-035 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-038 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-038 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-063 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-088 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-092 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-092 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-135 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-135 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-161 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-172 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-173 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-174 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-177 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-210 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-212 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-213 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | Contingent | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | $- | 0% | 16516041 | N/A
GEN-2023-035 | DISIS-2023-001 CF | 04 SOUTHEAST | 72018 72019 72020 72021 72022 72023 72024 72025 72026 72027 72028 72029 72030 72031 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | $- | 0% | 34866355 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | 72018 72019 72020 72021 72022 72023 72024 72025 72026 72027 72028 72029 72030 72031 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | $- | 0% | 34866355 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | 72018 72019 72020 72021 72022 72023 72024 72025 72026 72027 72028 72029 72030 72031 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | $- | 0% | 34866355 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | 72018 72019 72020 72021 72022 72023 72024 72025 72026 72027 72028 72029 72030 72031 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | $- | 0% | 34866355 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | 72018 72019 72020 72021 72022 72023 72024 72025 72026 72027 72028 72029 72030 72031 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | $- | 0% | 34866355 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | 72018 72019 72020 72021 72022 72023 72024 72025 72026 72027 72028 72029 72030 72031 | ERIS | Multi - Park Community - Sunshine 138 kV | Contingent | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | $- | 0% | 34866355 | N/A
GEN-2023-011 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-077 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-078 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-079 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-199 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | NRIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-216 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | NRIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-217 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | NRIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-218 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | NRIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-222 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-222 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | NRIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-223 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-223 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | NRIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-224 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-225 | DISIS-2023-001 CF | 02 NEBRASKA | 71963/71964/71965/71966/71967/71968 | ERIS | Multi - Sheldon - Monolith 115 kV | Contingent | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | $- | 0% | 60975092 | N/A
GEN-2023-012 | DISIS-2023-001 | 01 NORTH | 1.5924e+41 | ERIS | Multi - Sioux Falls 115 kV System Reconfig | Contingent | Install 115 kV new substation at Lincoln County | $- | 0% | 15441002 | 0.01506
GEN-2023-082 | DISIS-2023-001 | 01 NORTH | 1.5924e+41 | ERIS | Multi - Sioux Falls 115 kV System Reconfig | Contingent | Install 115 kV new substation at Lincoln County | $- | 0% | 15441002 | 0.01516
GEN-2023-097 | DISIS-2023-001 | 01 NORTH | 1.5924e+41 | ERIS | Multi - Sioux Falls 115 kV System Reconfig | Contingent | Install 115 kV new substation at Lincoln County | $- | 0% | 15441002 | 0.00466
GEN-2023-105 | DISIS-2023-001 | 01 NORTH | 1.5924e+41 | ERIS | Multi - Sioux Falls 115 kV System Reconfig | Contingent | Install 115 kV new substation at Lincoln County | $- | 0% | 15441002 | 0.0016
GEN-2023-154 | DISIS-2023-001 | 01 NORTH | 1.5924e+41 | ERIS | Multi - Sioux Falls 115 kV System Reconfig | Contingent | Install 115 kV new substation at Lincoln County | $- | 0% | 15441002 | 0.00404
GEN-2023-182 | DISIS-2023-001 | 01 NORTH | 1.5924e+41 | ERIS | Multi - Sioux Falls 115 kV System Reconfig | Contingent | Install 115 kV new substation at Lincoln County | $- | 0% | 15441002 | 0.00563
GEN-2023-168 | DISIS-2023-001 CF | 04 SOUTHEAST | 144297/144281 | ERIS | Multi - West Oaks - Council - Classen 138 kV Reconductor | Contingent | Upgrade any necessary terminal equipment at Classen substation. Reconductor of Douglas Tap to Classen 138 kV transmission line. | $- | 0% | 1390000 | N/A
GEN-2023-168 | DISIS-2023-001 CF | 04 SOUTHEAST | 144297/144281 | NRIS | Multi - West Oaks - Council - Classen 138 kV Reconductor | Contingent | Upgrade any necessary terminal equipment at Classen substation. Reconductor of Douglas Tap to Classen 138 kV transmission line. | $- | 0% | 1390000 | N/A
GEN-2023-168 | DISIS-2023-001 CF | 04 SOUTHEAST | 144297/144281 | NRIS | Multi - West Oaks - Council - Classen 138 kV Reconductor | Contingent | Upgrade any necessary terminal equipment at Classen substation. Reconductor of Douglas Tap to Classen 138 kV transmission line. | $- | 0% | 1390000 | N/A
GEN-2023-050 | DISIS-2023-001 CF | 03 CENTRAL | 157403 | ERIS | Neosho 345 kV Terminal Upgrade | Contingent | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA. | $- | 0% | 1534495 | N/A
GEN-2023-231 | DISIS-2023-001 CF | 03 CENTRAL | 157403 | ERIS | Neosho 345 kV Terminal Upgrade | Contingent | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA. | $- | 0% | 1534495 | N/A
GEN-2023-057 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Contingent | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | $- | 0% | 96314434 | N/A
GEN-2023-063 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Contingent | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | $- | 0% | 96314434 | N/A
GEN-2023-075 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Contingent | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | $- | 0% | 96314434 | N/A
GEN-2023-076 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Contingent | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | $- | 0% | 96314434 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | Contingent | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | $- | 0% | 697513 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-015 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Oklaunion to G22-011-TAP 345kV New Line | Contingent | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | $- | 0% | 87780000 | N/A
GEN-2023-006 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.03157
GEN-2023-006 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-033 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-034 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.03486
GEN-2023-034 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-050 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.04866
GEN-2023-050 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-056 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-061 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-064 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-065 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.03322
GEN-2023-065 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-073 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.04113
GEN-2023-073 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-099 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-149 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.14243
GEN-2023-149 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-149 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-194 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.03024
GEN-2023-194 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-219 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.04221
GEN-2023-220 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.05632
GEN-2023-220 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-221 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.05594
GEN-2023-221 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-231 | DISIS-2023-001 | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | -2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | 0.06408
GEN-2023-231 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-006 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-050 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-073 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-087 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-099 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-149 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-219 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-220 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-221 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-231 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Contingent | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | $- | 0% | 150000 | N/A
GEN-2023-151 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Contingent | Rebuild the PATMOS to FULTON 115kV line CKT1 (14.95 miles) to a minimum rating of 172 MVA | $- | 0% | 5093561 | N/A
GEN-2023-212 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Contingent | Rebuild the PATMOS to FULTON 115kV line CKT1 (14.95 miles) to a minimum rating of 172 MVA | $- | 0% | 5093561 | N/A
GEN-2023-085 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 | Contingent | Rebuild 5MANSFDMN to G23-085-TAP 161 kV line 1 to a minimum rating of 231 MVA | $- | 0% | 2200000 | N/A
GEN-2023-033 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | Contingent | Rebuild 5MOCITYB2 to G23-169-TAP 161 kV line 1 to a minimum rating of 278 MVA | $- | 0% | 2000000 | N/A
GEN-2023-169 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | Contingent | Rebuild 5MOCITYB2 to G23-169-TAP 161 kV line 1 to a minimum rating of 278 MVA | $- | 0% | 2000000 | N/A
GEN-2023-219 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1 | Contingent | Rebuild the existing EAST ST3 to WEMPORI3 115 kV line 1 (5.1 miles) to a minimum rating of 120 MVA | $- | 0% | 38625284 | N/A
GEN-2023-132 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line | Contingent | Rebuild the 5HEBER.N# to GREERSF5 161 kV line CKT1 (0 miles) to a minimum rating of 229 MVA | $- | 0% | 2224000 | N/A
GEN-2023-028 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Contingent | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | $- | 0% | 14429000 | N/A
GEN-2023-049 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Contingent | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | $- | 0% | 14429000 | N/A
GEN-2023-194 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Contingent | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | $- | 0% | 14429000 | N/A
GEN-2023-104 | DISIS-2023-001 | 04 SOUTHEAST | TBD | ERIS | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line | Contingent | Rebuild the NOELSW4 to G23-104-TAP 138 kV line CKT1 (7.05 miles) to a minimum rating of 360 MVA | $- | 0% | 7857895.85 | 0.71705
GEN-2023-028 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line | Contingent | Rebuild the PENSA 5 to G23-049-TAP 161 kV line CKT1 (6.5 miles) to a minimum rating of 449 MVA | $- | 0% | 135805 | N/A
GEN-2023-049 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line | Contingent | Rebuild the PENSA 5 to G23-049-TAP 161 kV line CKT1 (6.5 miles) to a minimum rating of 449 MVA | $- | 0% | 135805 | N/A
GEN-2023-028 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Contingent | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | $- | 0% | 5291000 | N/A
GEN-2023-049 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Contingent | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | $- | 0% | 5291000 | N/A
GEN-2023-194 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Contingent | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | $- | 0% | 5291000 | N/A
GEN-2023-056 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Contingent | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | $- | 0% | 3600000 | N/A
GEN-2023-064 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Contingent | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | $- | 0% | 3600000 | N/A
GEN-2023-088 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Contingent | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | $- | 0% | 3600000 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Contingent | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | $- | 0% | 3600000 | N/A
GEN-2023-205 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Contingent | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | $- | 0% | 3600000 | N/A
GEN-2023-038 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Contingent | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | $- | 0% | 460000 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Contingent | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | $- | 0% | 460000 | N/A
GEN-2023-088 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Contingent | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | $- | 0% | 460000 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Contingent | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | $- | 0% | 460000 | N/A
GEN-2023-205 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Contingent | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | $- | 0% | 460000 | N/A
GEN-2023-210 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Contingent | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | $- | 0% | 460000 | N/A
GEN-2023-033 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Contingent | Rebuild LBRTYST5 to BRMGHAM5 161 kV line 1 to a minimum rating of 275 MVA | $- | 0% | 9000000 | N/A
GEN-2023-169 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Contingent | Rebuild LBRTYST5 to BRMGHAM5 161 kV line 1 to a minimum rating of 275 MVA | $- | 0% | 9000000 | N/A
GEN-2023-194 | DISIS-2023-001 CF | 03 CENTRAL | TBD | ERIS | Rebuild the NEO SPA5 to TIP292 5 161kV Line 1 (EMDE) | Contingent | Rebuild the existing NEO SPA5 to TIP292 5 161 kV line 1 (10.6 miles) to a minimum rating of 270/315 MVA | $- | 0% | 10369174.4 | N/A
GEN-2023-028 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | Contingent | Rebuild ORO110 to RIV4525 161 kV line 1 line to a minimum rating of 558 MVA | $- | 0% | 25592475 | N/A
GEN-2023-049 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | Contingent | Rebuild ORO110 to RIV4525 161 kV line 1 line to a minimum rating of 558 MVA | $- | 0% | 25592475 | N/A
GEN-2023-194 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | Contingent | Rebuild ORO110 to RIV4525 161 kV line 1 line to a minimum rating of 558 MVA | $- | 0% | 25592475 | N/A
GEN-2023-116 | DISIS-2023-001 CF | 02 NEBRASKA | 158605 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate) | Contingent | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | $- | 0% | 1101824 | 0.04301
GEN-2023-117 | DISIS-2023-001 CF | 02 NEBRASKA | 158605 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate) | Contingent | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | $- | 0% | 1101824 | 0.04301
GEN-2023-153 | DISIS-2023-001 CF | 02 NEBRASKA | 158605 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate) | Contingent | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | $- | 0% | 1101824 | 0.04705
GEN-2023-199 | DISIS-2023-001 CF | 02 NEBRASKA | 158605 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate) | Contingent | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | $- | 0% | 1101824 | 0.19574
GEN-2023-216 | DISIS-2023-001 CF | 02 NEBRASKA | 158605 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate) | Contingent | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | $- | 0% | 1101824 | 0.23243
GEN-2023-217 | DISIS-2023-001 CF | 02 NEBRASKA | 158605 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate) | Contingent | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | $- | 0% | 1101824 | 0.23243
GEN-2023-218 | DISIS-2023-001 CF | 02 NEBRASKA | 158605 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate) | Contingent | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | $- | 0% | 1101824 | 0.23243
GEN-2023-199 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | ERIS | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Contingent | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | $- | 0% | 20859647.5 | 0.64633
GEN-2023-216 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | ERIS | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Contingent | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | $- | 0% | 20859647.5 | 0.05935
GEN-2023-217 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | ERIS | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Contingent | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | $- | 0% | 20859647.5 | 0.05935
GEN-2023-218 | DISIS-2023-001 CF | 02 NEBRASKA | TBD | ERIS | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Contingent | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | $- | 0% | 20859647.5 | 0.05935
GEN-2023-194 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Reconfigure the Neosho Transformers | Contingent | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | $- | 0% | 19662160 | N/A
GEN-2023-135 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Contingent | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | $- | 0% | 8302968 | N/A
GEN-2023-151 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Contingent | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | $- | 0% | 8302968 | N/A
GEN-2023-212 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Contingent | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | $- | 0% | 8302968 | N/A
GEN-2023-227 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Contingent | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | $- | 0% | 8302968 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Contingent | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | $- | 0% | 8302968 | N/A
GEN-2023-027 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | RIV4525 to BAX488 5 161kV Line Rebuild | Contingent | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | $- | 0% | 5076982.56 | N/A
GEN-2023-028 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | RIV4525 to BAX488 5 161kV Line Rebuild | Contingent | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | $- | 0% | 5076982.56 | N/A
GEN-2023-049 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | RIV4525 to BAX488 5 161kV Line Rebuild | Contingent | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | $- | 0% | 5076982.56 | N/A
GEN-2023-055 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | RIV4525 to BAX488 5 161kV Line Rebuild | Contingent | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | $- | 0% | 5076982.56 | N/A
GEN-2023-077 | DISIS-2023-001 | 02 NEBRASKA | 170036 | ERIS | S3458 to S3740 345 kV Ckt 2 New Line | Contingent | Build an approximately 38 mile 345 kV line from S3458 to S3740 Ckt 2. | $- | 0% | 98650000 | 0.25621
GEN-2023-078 | DISIS-2023-001 | 02 NEBRASKA | 170036 | ERIS | S3458 to S3740 345 kV Ckt 2 New Line | Contingent | Build an approximately 38 mile 345 kV line from S3458 to S3740 Ckt 2. | $- | 0% | 98650000 | 0.25621
GEN-2023-079 | DISIS-2023-001 | 02 NEBRASKA | 170036 | ERIS | S3458 to S3740 345 kV Ckt 2 New Line | Contingent | Build an approximately 38 mile 345 kV line from S3458 to S3740 Ckt 2. | $- | 0% | 98650000 | 0.25621
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | 170509 | NRIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-101 | DISIS-2023-001 | 04 SOUTHEAST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | 0.73307
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | 170509 | NRIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | 170509 | NRIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | 170509 | NRIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-172 | DISIS-2023-001 CF | 03 CENTRAL | 170509 | NRIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-173 | DISIS-2023-001 CF | 03 CENTRAL | 170509 | NRIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | NRIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | 170509 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | $- | 0% | 25920000 | N/A
GEN-2023-100 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Sweetwater to Demarcation 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | $- | 0% | 25920000 | N/A
GEN-2023-101 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Sweetwater to Demarcation 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | $- | 0% | 25920000 | N/A
GEN-2023-102 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Sweetwater to Demarcation 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | $- | 0% | 25920000 | N/A
GEN-2023-104 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | Sweetwater to Demarcation 230 kV Line Rebuild | Contingent | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | $- | 0% | 25920000 | N/A
GEN-2023-216 | DISIS-2023-001 | 02 NEBRASKA | 158043 | NRIS | Upgrade existing HOSKINS T1 230/115 kV Transformer | Contingent | Upgrade the existing HOSKINS T1 230/115 kV Transformer CKT1 to a minimum MVA of 217 | $- | 0% | 11617895 | 0.02827
GEN-2023-217 | DISIS-2023-001 | 02 NEBRASKA | 158043 | NRIS | Upgrade existing HOSKINS T1 230/115 kV Transformer | Contingent | Upgrade the existing HOSKINS T1 230/115 kV Transformer CKT1 to a minimum MVA of 217 | $- | 0% | 11617895 | 0.02827
GEN-2023-218 | DISIS-2023-001 | 02 NEBRASKA | 158043 | NRIS | Upgrade existing HOSKINS T1 230/115 kV Transformer | Contingent | Upgrade the existing HOSKINS T1 230/115 kV Transformer CKT1 to a minimum MVA of 217 | $- | 0% | 11617895 | 0.02827
GEN-2023-061 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1 | Contingent | Upgrade Terminal Equipment at CARTHAG5 to achieve a minimum summer/winter rating of 303/326 MVA | $- | 0% | 250000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | Contingent | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | $- | 0% | 8100000 | N/A
GEN-2023-009 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-009 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-022 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-027 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-038 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-038 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-056 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-061 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-063 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-064 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-069 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-085 | DISIS-2023-001 CF | 03 CENTRAL | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-092 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-092 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-134 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-135 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-135 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-151 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-151 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-177 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-180 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-204 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-205 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-212 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-212 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-213 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | Contingent | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | $- | 0% | 119457000 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-110 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-183 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-228 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
GEN-2023-237 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Woodward EHV to Beckham 345 kV New Line | Contingent | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | $- | 0% | 134640000 | N/A
ASGI-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-001 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-005 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-008 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-010 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-060 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-081 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-086 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | N/A
GEN-2023-120 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-123 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-142 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-143 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-150 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | N/A
GEN-2023-158 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-159 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-164 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | N/A
GEN-2023-165 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | N/A
GEN-2023-176 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-178 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-184 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | N/A
GEN-2023-195 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-201 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-203 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-208 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-209 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | NRIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | N/A
GEN-2023-229 | DISIS-2023-001 CF | 04 SOUTHEAST | TBD | NRIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | N/A
GEN-2023-236 | DISIS-2023-001 | 05 SOUTHWEST | 158630 | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Contingent | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | $- | 0% | 37534234 | 0
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Build New G17-151-Tap to Border 345 kV Line | Contingent | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | $- | 0% | 335411258 | N/A
ASGI-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-001 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-005 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-008 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-010 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-060 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-081 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-086 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-120 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-123 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-142 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-143 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-158 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-159 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-176 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-178 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-184 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-188 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-195 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-201 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-203 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-208 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-209 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
GEN-2023-236 | DISIS-2023-001 CF | 05 SOUTHWEST | TBD | ERIS | Border to Beckham 345 kV New Line | Contingent | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | $- | 0% | 35352000 | N/A
10330517232.2208

## Upgrade Summary
Upgrade Type | Study Name | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Model Correction | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | NRIS | ADORA2 to ADORAT2 Ckt 1 Rating Update | N/A | Update the existing ADORA2 to ADORAT2 Ckt 1 to a Summer Emergency rating of 243 MVA. | AEPW | 0 | 0
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | AFTON2 to FAIRTAP2 69 kV Ckt 1 Terminal Upgrade | TBD | Upgrade Terminal Equipment on the AFTON2 to FAIRTAP line Ckt 1 to achieve a rating of 157 MVA | GRDA | TBD (36-month lead time) | 170340
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | NRIS | Brown Substation Expansion | TBD | Move COLBRTP4 138 kV from SBROWN4 to BROWN4. Move Little City to Brown 138 kV Substation from Brown Tap 138 kV Substation Upgrade BROWN Substation to a breaker-and-a-half configuration. | OKGE | TBD (36-month lead time) | 18406321
Current Study | DISIS-2023-001 | Steady State / Stability | 03 CENTRAL | DISIS-2023-001 | ERIS | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | TBD | Build a 2nd LANG 3 to G22-007-TAP 115 kV line (0.41mi approx.) | WERE | TBD (36-month lead time) | 22000000
Current Study | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Build a new 30MVAR Switched Shunt at RUBART 3 115kV | TBD | Install a new 30 MVAR Switched Shunt at RUBART 3 115kV | SUNC | TBD (36-month lead time) | 4000000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | TBD | Build a new 36 MVAR cap bank at SHARNSP3 115 kV | SUNC | TBD (36-month lead time) | 6500000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | TBD | Build a new switched shunt at HANLON1-ER8 69 kV with a capacity of 7.5 MVAR; Build a new switched shunt at HANLON2-ER8 69 kV with a capacity of 7.5 MVAR | EREC | TBD (36-month lead time) | 818000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build a new 7.5MVAR Switched Shunt at PUKWANA-ER8 69kV | TBD | Build a new switched shunt at PUKWANA-ER8 69 kV with a capacity of 7.5 MVAR | EREC | TBD (36-month lead time) | 409000
Current Study | DISIS-2023-001 | Steady State / Stability | 02 NEBRASKA | DISIS-2023-001 | ERIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | TBD | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | NPPD | TBD (36-month lead time) | 61000000
Current Study | DISIS-2023-001 | Steady State / Stability | 02 NEBRASKA | DISIS-2023-001 | ERIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | TBD | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | NPPD | TBD (36-month lead time) | 83000000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | TBD | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | WERE/ITCGP | TBD (36-month lead time) | 483363656
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | TBD | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | WERE/OKGE | TBD (36-month lead time) | 247391685
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | TBD | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | WERE/OKGE | TBD (36-month lead time) | 195647827
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | TBD | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 1486 MVA | SPS/SUNC | TBD (36-month lead time) | 23105000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new TOLK6 to TUCO6 230 kV line 2 | TBD | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | SPS | TBD (36-month lead time) | 136450000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new TOLK7 345/230 kV Transformer 3 | TBD | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | SPS | TBD (36-month lead time) | 16400000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new TUCO7 345/230 kV Transformer 3 | TBD | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | SPS | TBD (36-month lead time) | 16400000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new TUCO7 345/230 kV Transformer 4 | TBD | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | SPS | TBD (36-month lead time) | 16400000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build a new TUCO7 to CRAWFISH 345 kV line 3 | TBD | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | SPS | TBD (36-month lead time) | 4743000
Contingent | DISIS-2023-001 | Steady State | 05 SOUTHWEST | 2024 ITP | ERIS | Build New Beckham to Potter 345 kV Line | 170625, 170624 | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | OKGE/SPS | 36 | 428620878
Current Study | DISIS-2023-001 | Stability | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build new Benton 345 kV STATCOM | TBD | Build a 500 MVAR STATCOM at Benton 345 kV | WERE | TBD (36-month lead time) | 198936942
Current Study | DISIS-2023-001 | Stability | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build new Border 345 kV STATCOM | TBD | Build a 500 MVAR STATCOM at Border 345 kV | OKGE | TBD (36-month lead time) | 300000000
Current Study | DISIS-2023-001 | Stability | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build new Crawfish 345 kV STATCOM | TBD | Build a 500 MVAR STATCOM at Crawfish 345 kV | SPS | TBD (36-month lead time) | 300000000
Current Study | DISIS-2023-001 | Steady State / Stability | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | TBD | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | AEPW/SPS | TBD (36-month lead time) | 2104646400
Current Study | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | TBD | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | NPPD | TBD (36-month lead time) | 308987400
Current Study | DISIS-2023-001 | Stability | 02 NEBRASKA / 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build new ELMCREEK7 345kV Capbank | TBD | Install a new 349.80 MVAR Cap Bank at Elm Creek 7 345 kV | ITC-GP | TBD (36-month lead time) | 11000000
Current Study | DISIS-2023-001 | Steady State / Stability | 02 NEBRASKA | DISIS-2023-001 | ERIS | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | TBD | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | NPPD | TBD (36-month lead time) | 192504000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | TBD | Build a new GR PRAIRIE 3 to ANTELOPE 3 345 kV line 1 (50 miles) to a standard rating of 1792 MVA | NPPD/WAPA | TBD (36-month lead time) | 130000000
Contingent | DISIS-2023-001 | Steady State / Stability | 05 SOUTHWEST | 2024 ITP | ERIS | Build New Phantom to Crossroads to Potter 765 kV Line | 170626 | Expand the existing Phantom 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Phantom 765 kV substation Expand the existing Crossroads 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Crossroads 765 kV substation Expand the existing Potter County 345 kV substation to 765 kV with new terminals to accommodate new line from Phantom to Crossroads to Potter County. Install new 765/345 transformer at Potter County 765 kV substation Build a new Phantom to Crossroads 765 kV line (144.57 miles) to a minimum rating of 5300 MVA Build a new Crossroads to Potter County 765 kV line (148.47 miles) to a minimum rating of 5300 MVA | SPS | 36 | 1301149472
Current Study | DISIS-2023-001 | Stability | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build new Potter 345 kV STATCOM | TBD | Build a 500 MVAR STATCOM at Potter 345 kV | SPS | TBD (36-month lead time) | 300000000
Current Study | DISIS-2023-001 | Steady State / Stability | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build new Potter to Chisholm 765 kV Line | TBD | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | AEPW/SPS | TBD (36-month lead time) | 932100000
Current Study | DISIS-2023-001 | Stability | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Build new Reno 345 kV Capbank | TBD | Build a 100 MVAR Capacitor Bank at Reno 345 kV | WERE | TBD (36-month lead time) | 9608545
Current Study | DISIS-2023-001 | Steady State / Stability | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Build new Tolk to Needmore 230 kV Line | TBD | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | SPS | TBD (36-month lead time) | 34125000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | TBD | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | EMDE | TBD (36-month lead time) | 21623128
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | TBD | Build new STILWEL7 to G21-029-TAP 345 kV line to a minimum rating of 1792 MVA | KCPL | TBD (36-month lead time) | 89000000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | TBD | Upgrade Terminal Equipment on the DRYGULCH to G23-028-TAP line Ckt 1 to achieve a rating of 443 MVA | GRDA | TBD (36-month lead time) | 254602
Model Correction | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | FTTHOMP3 to FTTHOM1-LNX3 345 kV Line Z Rating Update | N/A | Update the existing FTTHOMP3 to FTTHOM1-LNX3 345 kV line Z (0 miles) to a rating of 1091/1091 MVA | BEPC | 0 | 0
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | HARRING_WST6 to HARRNG_MID6 230 kV Ckt 1 Terminal Upgrade | TBD | Upgrade Terminal Equipment on the HARRING_WST6 to HARRNG_MID6 line Ckt 1 to achieve a rating of 650 MVA | SPS | TBD (36-month lead time) | 3600000
Contingent | DISIS-2023-001 | Steady State | 03 CENTRAL / 04 SOUTHEAST | 2023 ITP | NRIS | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | 156301 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | GRDA | 46387 | 4923250
Contingent | DISIS-2023-001 | Steady State | 03 CENTRAL / 04 SOUTHEAST | 2023 ITP | NRIS | Kerr - Maid 161 kV Ckt 2 Rebuild | 156304 | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | GRDA | 46387 | 4923250
Contingent | DISIS-2023-001 | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | 2023 ITP | NRIS | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | 158637, 157395, 157396, 157897, 157879 | Build new 15-mile 138 kV Ckt 2 & Ckt 3 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | OKGE/WFEC | 46904 | 27744395
Contingent | DISIS-2023-001 | Steady State / Stability | 04 SOUTHEAST | 2024 ITP | ERIS | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line |  | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | WERE/AEPW | TBD | 484090326
Contingent | DISIS-2023-001 | Steady State / Stability | 02 NEBRASKA / 04 SOUTHEAST | 2024 ITP | ERIS | Line - Elm Creek 345 kV - Tobias 345 kV New Line | 170380/170392/170393 | Build a new TOBIAS 3 to ELMCREEK7 345 kV line 1 (85.2 miles) to a standard rating of 1792 MVA | NPPD/ITC-GP | 2028-11-12 | 137721276
Contingent | DISIS-2023-001 | Steady State / Stability | 02 NEBRASKA / 04 SOUTHEAST / 05 SOUTHWEST | 2024 ITP | ERIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 169968/170009/170008/170565/170568 | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | AMIL/SUNC | 2029-11-12 | 977728865
Contingent | DISIS-2023-001 | Steady State | 02 NEBRASKA | 2024 ITP | ERIS | Line - Holt County 345 kV - Antelope 345 kV New Line | 170229, 170230, 170231 | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Holt County 345 kV Ck1 substation to support a new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ckt1 substation with a summer emergency rating of 1792 MVA. Install any necessary terminal equipment at Antelope 345 kV Ck1 substation to support a new line from Antelope 345 kV Ck1 substation to Holt County 345 kV Ck1 substation with a summer emergency rating of 1792 MVA. | NPPD | 2028-11-12 | 94400000
Contingent | DISIS-2023-001 | Steady State | 02 NEBRASKA | 2021 ITP | ERIS | Line - S3454 - S3740 345 kV | 143660 | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | OPPD | 18 | 64071687
Contingent | DISIS-2023-001 | Steady State | 04 SOUTHEAST | 2019 ITP | ERIS | Line - Wolf Creek - Blackberry 345 kV | 122598 | Build a new 345kV line from Wolf Creek to Blackberry with a summer emergency rating of 1792 MVA | NEET | 7 | 87298154
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | MIAMI to HOC404 5 161kV Line Rebuild | TBD | Rebuild the MIAMI 5 to HOC404 5 161 kV line CKT1 (9.9 miles) to a minimum rating of 359 MVA | GRDA/EMDE | TBD (36-month lead time) | 10340522
Contingent | DISIS-2023-001 | Steady State | 01 NORTH | 2024 ITP | ERIS | Multi - Hanson County 115 kV System Reconfig | 169696,169697,169698,169699,169675,169676,169677,169678,169686,169692,169694,169695,169701 | Build a new18.4-mile 69 kV Ckt 1 line from Mount Vernon to Mitchell and upgrade any necessary terminal equipment to achieve a summer emergency rating of 84 MVA. Install 69 kV new substation at Mitchell Build a new 6.2-mile 115 kV Ckt 1 line from Letcher 115 kV substation to Plano 115 kV motor-operated switch and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. Build a new 18.3-mile 69 kV Ckt 1 line from Mitchell 69 kV substation to Hanson County 69 kV substation with a summer emergency rating of 84 MVA. Build a new 18.6-mile 115 kV Ckt 1 line from Plano 115 kV substation to Hanson County 115 kV substation with a summer emergency rating of 139 MVA. Extend the 115 kV line from Letcher to Miner County 3.25 miles to reroute around the new lines to Letcher. Install 115 kV new substation at Hanson County Install 69 kV new Substation at Hanson County Install 9.6 MVAR Capacitor at Hanson County 69 kV substation Install new 115/69 transformer at Hanson County 69 kV substation | EREC | 2026-02-02 | 38232000
Contingent | DISIS-2023-001 | Steady State | 01 NORTH | 2024 ITP | ERIS | Multi - Madison, SD Area 115 kV System Voltage Conversion | 169974,169933,169935,169937,169940,169951,169953,169969,169970,169972,169973,169975,169977,169978,169979 | Install 115 kV new substation at Lake County Install 115 kV new substation at Madison SE Install 115 kV new substation at Howard Build a 3-mile 115 kV Ckt 1 line from Madison SE 115 kV substation to Lake County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Convert the 0.9-mile Ckt 1 69kV line from Madison SE to Lakeview to 115 kV Build a 22.2-mile 115 kV Ckt 1 line from Lake County 115 kV substation to Howard 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Build a 6.0-mile 115 kV Ckt 1 line from Howard 115kV substation to Howard City 115kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Build a 12.4-mile 115 kV Ckt 1 line from Howard City 115 kV MOS to Miner County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Convert the 24-mile Ckt 1 69 kV line from Hanlon to Lakeview to 115 kV Install new 115/69 transformer at Lake County 69 kV substation Install 20 MVAR capacitor bank at Hutchinson 115 kV substation | EREC | 2026-12-01 | 34894000
Contingent | DISIS-2023-001 | Steady State | 01 NORTH | 2024 ITP | ERIS | Multi - Marion Area 115 kV Voltage Conversion Reconfig | 159230,159073,159118,159121,159123,159144,159162,159166,159176,159181,159183,159185,159192,159195,159212,159214,159220 | Install 115 kV new substation at Lake County Install 115 kV new substation at Madison SE Install 115 kV new substation at Howard Build a 3-mile 115 kV Ckt 1 line from Madison SE 115 kV substation to Lake County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Convert the 0.9-mile Ckt 1 69kV line from Madison SE to Lakeview to 115 kV Build a 22.2-mile 115 kV Ckt 1 line from Lake County 115 kV substation to Howard 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA Build a 6.0-mile 115 kV Ckt 1 line from Howard 115kV substation to Howard City 115kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Build a 12.4-mile 115 kV Ckt 1 line from Howard City 115 kV MOS to Miner County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 139 MVA. Convert the 24-mile Ckt 1 69 kV line from Hanlon to Lakeview to 115 kV Install new 115/69 transformer at Lake County 69 kV substation | EREC | 2027-11-12 | 31469000
Contingent | DISIS-2023-001 | Steady State | 01 NORTH | 2024 ITP | ERIS | Multi - Sioux Falls 115 kV System Reconfig | 159237,159238,159239,159240,159234,159235,170518 | Install 115 kV new substation at Lincoln County | EREC | 2028-06-30 | 15441002
Model Correction | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | OKMULGE to ECHEN4 Ckt 1 Rating Update | N/A | Update the existing OKMULGE to ECHEN4 Ckt 1 to a Summer Emergency rating of 201 MVA. | AEPW | 0 | 0
Model Correction | DISIS-2023-001 | Steady State | 01 NORTH / 02 NEBRASKA / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2023-001 | ERIS | ORO11505 to RIV4525 Ckt 1 Rating Update | N/A | Update the existing ORO11505 to RIV4525 Ckt 1 to a SN/SE/WN/WE of 404/420/479/493 MVA | EMDE | 0 | 0
Contingent | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2021-001 | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | TBD | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | KCPL | TBD (36-month lead time) | 150000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) | TBD | Rebuild 5MANSFDMN to G23-085-TAP 161 kV line 1 to a minimum rating of 231 MVA | SWPA | TBD (36-month lead time) | 2220000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | TBD | Rebuild 5MOCITYB2 to G23-169-TAP 161 kV line 1 to a minimum rating of 278 MVA | KCPL | TBD (36-month lead time) | 2000000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI) | TBD | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA (Owned by AECI, will be addressed in the AFS) | AECI | N/A | 0
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) | TBD | Rebuild 7BLACKBERRY to NEOSHO 7 345 kV line 1 to a minimum rating of 1145 MVA | WERE | TBD (36-month lead time) | 63000000
Current Study | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1 | TBD | Rebuild the existing BEATRCE7 to HARBINE7 115 kV line 1 (14.08 miles) to a minimum rating of 200 MVA | NPPD | TBD (36-month lead time) | 14080000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the CAMPBELL 4 to GLENHAM4 230kV Line 1 | TBD | Rebuild the existing CAMPBELL 4 to GLENHAM4 230 kV line 1 (14 miles) to a minimum rating of 260 MVA | WAPA | TBD (36-month lead time) | 6000000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the COLMBUS4 to MEADOWGROVE4 230kV Line 1 | TBD | Rebuild the existing COLMBUS4 to MEADOWGROVE4 230 kV line 1 (44.14 miles) to a minimum rating of 560 MVA | NPPD | TBD (36-month lead time) | 83866000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | TBD | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | KCPL | TBD (36-month lead time) | 55000000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line | TBD | Rebuild the 5HEBER.N# to GREERSF5 161 kV line CKT1 (0 miles) to a minimum rating of 229 MVA | EES-EAI/SWPA | TBD (36-month lead time) | 2224000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | TBD | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | GRDA | TBD (36-month lead time) | 14429000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line | TBD | Rebuild the BIRDHOL4 to JAY 4 138 kV line CKT1 (15.58 miles) to a minimum rating of 185 MVA | AEPW | TBD (36-month lead time) | 230000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | TBD | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | SPS | TBD (36-month lead time) | 133320000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing DEAFSMITH6 to G17-146-TAP 230 kV line | TBD | Rebuild the DEAFSMITH6 to G17-146-TAP 230 kV line CKT1 (4.53 miles) to a minimum rating of 509 MVA | SPS | TBD (36-month lead time) | 8607000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | TBD | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | AEPW | TBD (36-month lead time) | 44160000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | NRIS | Rebuild the existing ERLSBOR2 to FRSTHIL2 69 kV line | TBD | Rebuild the ERLSBOR2 to FRSTHIL2 69 kV line CKT1 (8.31 miles) to a minimum rating of 143 MVA. | OKGE | TBD (36-month lead time) | 8000000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | TBD | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | SPS | TBD (36-month lead time) | 16192000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | TBD | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | SPS/SUNC | TBD (36-month lead time) | 1650000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing GROVE 4 to JAY 4 138 kV line | TBD | Rebuild the GROVE 4 to JAY 4 138 kV line CKT1 (13.03 miles) to a minimum rating of 177 MVA | AEPW | TBD (36-month lead time) | 230000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing HALE_CNTY3 to TUCO3 115 kV line | TBD | Rebuild the HALE_CNTY to TUCO3 115 kV line CKT1 (20.73 miles) to a minimum rating of 152 | SPS | TBD (36-month lead time) | 20730000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | NRIS | Rebuild the existing JOP 59 2 to RIV167 2 69 kV line | TBD | Rebuild the JOP 59 2 to RIV167 2 69 kV line CKT1 (10.05 miles) to a minimum rating of 86 MVA. | EMDE | TBD (36-month lead time) | 8542500
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | TBD | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | AEPW | TBD (36-month lead time) | 149760000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line | TBD | Rebuild the MIAMI 5 to AFTON 5 161 kV line CKT1 (13.5 miles) to a minimum rating of 419 MVA | GRDA | TBD (36-month lead time) | 15635000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing NEWHART to PLANTX 230 kV line | TBD | Rebuild the NEWHART to PLANTX 230 kV line CKT1 (39.59 miles) to a minimum rating of 586 MVA | SPS | TBD (36-month lead time) | 75221000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing NHUNTNT5 to G23-180-TAP 161 kV line | TBD | Rebuild the NHUNTNT5 to G23-180-TAP 161 kV line CKT1 (3.03 miles) to a minimum rating of 184 MVA | AEPW | TBD (36-month lead time) | 6969000
Contingent | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line | TBD | Rebuild the NOELSW4 to G23-104-TAP 138 kV line CKT1 (7.05 miles) to a minimum rating of 360 MVA | WFEC | 36 | 7857895.85
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line | TBD | Rebuild the PENSA 5 to G23-049-TAP 161 kV line CKT1 (6.5 miles) to a minimum rating of 449 MVA | GRDA | TBD (36-month lead time) | 135805
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | TBD | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | GRDA | TBD (36-month lead time) | 5291000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | TBD | Rebuild the PITTSB-7 to SEMINOL7 345 kV CKT 1 (51.27 miles) to a minimum rating of 1135 MVA | OKGE/AEPW | TBD (36-month lead time) | 112794000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | TBD | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | SPS | TBD (36-month lead time) | 78679000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL / 04 SOUTHEAST | DISIS-2023-001 | NRIS | Rebuild the existing RIV4525 to STL439_5 161 kV line | TBD | Rebuild the RIV425 to STL439_5 161 kV line CKT1 (6.82 miles) to a minimum rating of 620 MVA | EMDE | TBD (36-month lead time) | 10230000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT1 line | TBD | Rebuild the SPEARMAN to PRINGLE 115 kV line CKT1 (17.76 miles) to a minimum rating of 196 MVA | SPS | TBD (36-month lead time) | 17760000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing SPEARMAN3 to PRINGLE3 115 kV CKT2 line | TBD | Rebuild the SPEARMAN to PRINGLE 115 kV line CKT2 (20.02 miles) to a minimum rating of 184 MVA | SPS | TBD (36-month lead time) | 20020000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | TBD | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | SPS | TBD (36-month lead time) | 12578000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | TBD | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | SPS | TBD (36-month lead time) | 46778000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | TBD | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | WERE | TBD (36-month lead time) | 63860000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line | TBD | Rebuild the TAYLOR3 to W_BENDER3 115 kV line CKT1 (6.4 miles) to a minimum rating of 225 MVA | SPS | TBD (36-month lead time) | 6400000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing TOLK6 to TUCO6 230 kV line 1 | TBD | Rebuild the TOLK6 to TUCO6 230 kV line CKT1 (54.58 miles) to a minimum rating of 840 MVA | SPS | TBD (36-month lead time) | 103702000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line | TBD | Rebuild the TONECE7 to G23-138-TAP 345 kV line CKT1 (22.5 miles) to a minimum rating of 1317 MVA | GRDA | TBD (36-month lead time) | 25749990
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | TBD | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | SPS | TBD (36-month lead time) | 3366000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | TBD | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | SPS | TBD (36-month lead time) | 3366000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | TBD | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | SWPA/OKGE | TBD (36-month lead time) | 3600000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | TBD | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | AEPW | TBD (36-month lead time) | 460000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Rebuild the existing WHEELER 6 to G23-101-TAP 230 kV line | TBD | Rebuild the WHEELER 6 to G23-101-TAP 230 kV line CKT1 (7.3 miles) to a minimum rating of 487 MVA | SPS | TBD (36-month lead time) | 6449615.7
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1 | TBD | Rebuild the existing FTRANDL4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | WAPA/EREC | TBD (36-month lead time) | 84500000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | TBD | Rebuild the existing FTTHOM2-LNX3 to GRPRAR2-LNX3 345 kV line 1 (123.95 miles) to a minimum rating of 1060 MVA | WAPA | TBD (36-month lead time) | 40000000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | TBD | Rebuild the existing FTTHOMP4 to FTRANDL4 230 kV line 1 (87.32 miles) to a minimum rating of 600 MVA | WAPA | TBD (36-month lead time) | 168000000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1 | TBD | Rebuild the existing FTTHOMP4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | WAPA/EREC | TBD (36-month lead time) | 84500000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Route second Ft. Thompson - Huron 230 kV circuit into G17-094-TAP | TBD | Loop the second Ft. Thompson - Huron 230 kV circuit into G17-094-TAP and expand the G17-094-TAP substation | WAPA | TBD (36-month lead time) | 15000000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1 | TBD | Rebuild the existing GROTON 7 to BRISTOL-ER7 115 kV line 1 (21.3 miles) to a minimum rating of 165 MVA | WAPA/EREC | TBD (36-month lead time) | 22150000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | TBD | Rebuild LBRTYST5 to BRMGHAM5 161 kV line 1 to a minimum rating of 275 MVA | KCPL | TBD (36-month lead time) | 9000000
Current Study | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the MARSHAL3 to KNOB HL3 115kV Line 1 | TBD | Rebuild the existing MARSHAL3 to KNOB HL3 115 kV line 1 (14.21 miles) to a minimum rating of 105 MVA | WERE | TBD (36-month lead time) | 20000000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1 | TBD | Rebuild the existing MEADOWGROVE4 to FTRANDL4 230 kV line 1 (84.17 miles) to a minimum rating of 500 MVA | NPPD/WAPA | TBD (36-month lead time) | 161923000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | TBD | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | WERE | TBD (36-month lead time) | 31000000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the NEWTON 2 to ADAMS 2 69 kV Line 1 | TBD | Rebuild NEWTON 2 to ADAMS 2 69 kV line 1 to a minimum rating of 82 MVA | WERE | TBD (36-month lead time) | 4500000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | TBD | Rebuild ORO110 to RIV4525 161 kV line 1 line to a minimum rating of 558 MVA | EMDE | TBD (36-month lead time) | 25592475
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1 | TBD | Rebuild the existing PAHOJA__-BE4 to EAGLE___-NI4 230 kV line 1 (22.24 miles) to a minimum rating of 450 MVA | WAPA/NIPCO | TBD (36-month lead time) | 45100000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line 1 | TBD | Upgrade Terminal Equipment on the RIV4525 to G20-079-TAP 161 kV Line 1 to a minimum Rate B of 607 MVA | EMDE | TBD (36-month lead time) | 5165042
Current Study | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | TBD | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | OPPD | TBD (36-month lead time) | 31064000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1 | TBD | Rebuild the existing SIOUXFL4 to PAHOJA__-BE4 230 kV line 1 (20.19 miles) to a minimum rating of 500 MVA | WAPA/L&O | TBD (36-month lead time) | 42000000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Rebuild the SUMMIT-7 to BRISTOL-ER7 115kV Line 1 | TBD | Rebuild the existing SUMMIT-7 to BRISTOL-ER7 115 kV line 1 (32.56 miles) to a minimum rating of 160 MVA | WAPA/EREC | TBD (36-month lead time) | 33150000
Current Study | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1 | TBD | Rebuild the existing SWEET W3 to GR ISLD3 345 kV line 1 (63.14 miles) to a minimum rating of 815 MVA | NPPD | TBD (36-month lead time) | 138908000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH / 02 NEBRASKA / 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2023-001 | ERIS | Reconfigure the Neosho Transformers | TBD | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | WERE | TBD (36-month lead time) | 19662160
Model Correction | DISIS-2023-001 | Steady State | 01 NORTH / 02 NEBRASKA / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2023-001 | ERIS | RIV4525 to STL439 Ckt 1 Rating Update | N/A | Update the existing RIV4525 to STL439 Ckt 1 to a SN/SE/WN/WE of 463/481/548/558 MVA | EMDE | 0 | 0
Model Correction | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | ROKHILL4 to G23-059-TAP Ckt 1 Rating Update | N/A | Update the existing ROKHILL4 to G23-059-TAP Ckt 1 to a Winter rating of 348 MVA | AEPW | 0 | 0
Contingent | DISIS-2023-001 | Steady State | 02 NEBRASKA | 2024 ITP | ERIS | S3458 to S3740 345 kV Ckt 2 New Line | 170036 | Build an approximately 38 mile 345 kV line from S3458 to S3740 Ckt 2. | OPPD | 48 | 98650000
Model Correction | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | SEDALA to SEDALIA5 161 kV Line 1 Rating Update | N/A | Update the existing 5SEDALA to SEDALIA5 161 kV line 1 to a rating of 228/259 MVA | KCPL | 0 | 0
Contingent | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | 170509 | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | AEPW | TBD (36 month lead time) | 25920000
Contingent | DISIS-2023-001 | Steady State | 02 NEBRASKA | DPA-2021 | NRIS | Upgrade existing HOSKINS T1 230/115 kV Transformer | 158043 | Upgrade the existing HOSKINS T1 230/115 kV Transformer CKT1 to a minimum MVA of 217 | NPPD | 36 | 11617895
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI) | TBD | Upgrade Terminal Equipment at 5MANSFDMN to achieve a minimum rating of 231 MVA (Owned by AECI, will be addressed in the AFS) | AECI | N/A | 0
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1 | TBD | Upgrade Terminal Equipment at CARTHAG5 to achieve a minimum summer/winter rating of 303/326 MVA | SWPA | TBD (36-month lead time) | 250000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Upgrade the existing ELKCITY6 230/138 kV Transformer | TBD | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | AEPW | TBD (36-month lead time) | 8100000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the existing FIXICO4 138/69 kV Transformer | TBD | Upgrade the existing FIXICO 138/69 kV Transformer to a minimum rating of 75 MVA | OKGE | TBD (36-month lead time) | 7000000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the existing GROVE 161/138 kV Transformer | TBD | Upgrade the GROVE 161/138 kV Transformer to a minimum rating of 136 MVA | AEPW | TBD (36-month lead time) | 7000000
Current Study | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | NRIS | Upgrade the existing LEX161 5 161/69 kV Transformer | TBD | Upgrade the existing LEX161 5 161/69 kV Transformer CKT1 to a minimum MVA of 83 | KCPL | TBD (36-month lead time) | 4832450
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Upgrade the existing PLANTX 230/115 kV Transformer | TBD | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | SPS | TBD (36-month lead time) | 8100000
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Upgrade the existing TUCO7 345/230 kV Transformer 1 | TBD | Upgrade the existing TUCO7 345/230 kV Transformer 1 to a minimum rating of 725 MVA | SPS | TBD (36-month lead time) | 16400000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the existing VBI2 161/69 kV Transformer | TBD | Upgrade the existing VBI2 161/69 kV Transformer to a minimum rating of 123 MVA. | OKGE | TBD (36-month lead time) | 50000
Current Study | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Upgrade the existing WLK X1 161/138 kV Transformer | TBD | Upgrade the existing WLK X1 161/138 kV Transformer to a minimum rating of 129 MVA | SWPA | TBD (36-month lead time) | 3606166
Current Study | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Upgrade the exsting PRINGLE6 230/115 kV Transformer | TBD | Upgrade the PRINGLE6 230/115 kV Transformer to a minimum rating of 287 MVA | SPS | TBD (36-month lead time) | 8100000
Current Study | DISIS-2023-001 | Steady State | 01 NORTH / 02 NEBRASKA / 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2023-001 | ERIS | Upgrade the Neosho 345/161 kV Transformer | TBD | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | WERE | TBD (36-month lead time) | 12000000
Model Correction | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | VALIANT to HUGO 138 kV Ckt 1 Rating Update | N/A | Update the exsting VALIANT4 to HUGOPP4 to a SN/SE/WN/WE rating of 299/353/381/421 MVA | AEPW/WFEC | 0 | 0
Current Study | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | NRIS | WARD4 to BISMARK4 230 kV Ckt 1 Terminal Upgrade | TBD | Upgrade Terminal Equipment on the WARD4 to BISMARK4 230 kV line Ckt 1 to achieve a rating of 382 MVA | WAPA | TBD (36-month lead time) | 4000000
Contingent | DISIS-2023-001 | Steady State | 05 SOUTHWEST | 2023 ITP | ERIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | 158629, 158630, 158631, 158632 | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | SPS | 2028-12-15 | 37534234
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2021-001 | ERIS | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | TBD | Upgrade Terminal Equipment at ARCHIE 5 161 kV to achieve a minimum rating of 249 MVA | KCPL | TBD (36-month lead time) | 150000
Contingent | DISIS-2023-001 CF | Steady State / Stability | 04 SOUTHEAST | DPA-2017-December-815 | ERIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | 82111 | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | WFEC | 2026-05-31 | 37489652
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DPA-2017-December-815 | NRIS | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | 82111 | Convert 2.1 mile 69 kV line from Blanchard - OU SW to 138 kV. Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | WFEC | 2026-05-31 | 37489652
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2023-001 | NRIS | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | TBD | Build a 2nd LANG 3 to G22-007-TAP 115 kV line (0.41mi approx.) | WERE | TBD (36-month lead time) | 22000000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | SPS | TBD (36-month lead time) | 6222750
Contingent | DISIS-2023-001 CF | Steady State | 02 NEBRASKA | DISIS-2023-001 | NRIS | Build a new Beatrice Power Station 345/115 kV to MONOLITH 3 345 kV line 1 | TBD | Build a new Beatrice Power Station to Monolith 345 kV line 1 (aproximately 23 miles) to a standard rating of 1793 MVA | NPPD | TBD (36-month lead time) | 61000000
Contingent | DISIS-2023-001 CF | Steady State | 02 NEBRASKA | DISIS-2023-001 | NRIS | Build a new Beatrice Power Station 345/115 kV to TOBIAS 3 345 kV line 1 | TBD | Build a new Beatrice Power Station to Tobias 345 kV line 1 (aproximately 32 miles) to a standard rating of 1793 MVA | NPPD | TBD (36-month lead time) | 83000000
Contingent | DISIS-2023-001 CF | Stability | 03 CENTRAL / 04 SOUTHEAST | DISIS-2022-001 | ERIS | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | WERE | TBD (36-month lead time) | 83000000
Contingent | DISIS-2023-001 CF | Steady State / Stability | 03 CENTRAL | DISIS-2021-001 | ERIS | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | TBD | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | SUNC | TBD (36-month lead time) | 102596000
Contingent | DISIS-2023-001 CF | Steady State | 02 NEBRASKA | DISIS-2022-001 | NRIS | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | TBD | Build a new AXTELL 7 to KEARNEY7 115 kV line 2 (10.74 miles) to a standard rating of 229/390 MVA | NPPD | TBD (36 month lead time) | 78000000
Contingent | DISIS-2023-001 CF | Steady State / Stability | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Beckham to Potter 345 kV Line Ckt 2 | TBD | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | OKGE/SPS | 36 | 428620878
Contingent | DISIS-2023-001 CF | Steady State / Stability | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | TBD | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | SPS | 36 | 44046000
Contingent | DISIS-2023-001 CF | Steady State / Stability | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Crossroads to Potter County 345 kV Line | TBD | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | SPS | 36 | 261000000
Contingent | DISIS-2023-001 CF | Steady State | 05 SOUTHWEST | DISIS-2020-001 | NRIS | Build New Crossroads to Potter County 345 kV Line | TBD | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | SPS | 36 | 261000000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2020-001 | NRIS | Build new Double Circuit Crawfish to Seminole 765 kV Line | TBD | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | AEPW/SPS | 36 | 2104646400
Contingent | DISIS-2023-001 CF | Steady State / Stability | 01 NORTH | DISIS-2022-001 | ERIS | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | TBD | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | WAPA/BEPC | TBD (36-month lead time) | 250000000
Contingent | DISIS-2023-001 CF | Steady State / Stability | 05 SOUTHWEST | DISIS-2022-001 | ERIS | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | TBD | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | SPS | TBD (36 month lead time) | 100000000
Contingent | DISIS-2023-001 CF | Steady State / Stability | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Hitchland to Potter 345 kV Line Ckt 2 | TBD | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | SPS | 36 | 184680000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Build new NEOSHO 5 to RIV4525 161kV Line 2 | TBD | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | WERE/EMDE | TBD (36-month lead time) | 29709558.63
Contingent | DISIS-2023-001 CF | Stability | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | TBD | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | OKGE | TBD (36-month lead time) | 230353500
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2020-001 | NRIS | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | TBD | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | OKGE | TBD (36-month lead time) | 230353500
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2020-001 | NRIS | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 |  | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | OKGE | TBD (36-month lead time) | 168086100
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2023-001 | NRIS | Build new Tolk to Needmore 230 kV Line | TBD | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | SPS | TBD (36-month lead time) | 34125000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST | DISIS-2023-001 | NRIS | Build RIV4525 to G20-079-TAP 161 kV Line 2 | TBD | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | EMDE | TBD (36-month lead time) | 21623128
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2023-001 | NRIS | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | TBD | Build new STILWEL7 to G21-029-TAP 345 kV line to a minimum rating of 1792 MVA | KCPL | TBD (36-month lead time) | 89000000
Contingent | DISIS-2023-001 CF | Steady State / Stability | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build the Crawfish Draw 345 kV Substation | TBD | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | SPS | 36 | 18427752
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2020-001 | NRIS | Build the Crawfish Draw 345 kV Substation | TBD | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | SPS | 36 | 18427752
Contingent | DISIS-2023-001 CF | Steady State | 01 NORTH | DISIS-2022-001 | ERIS | Build Third Ft Thompson 345-230 kV Transformer | TBD | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | WAPA | TBD (36-month lead time) | 16500000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DPA STUDIES | ERIS | Canadian Switch138 kV Terminal Upgrades Lexington - Lil Axe 138 kV Paoli - Lexington kV 138 kV Paoli 138 kV Terminal Upgrades | 143256 143254 143253 143255 | Convert 69 kV terminal equipment at Canadian Switch to 138 kV Convert 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV Rebuild 14.3 miles of 69 kV line from Paoli to Lexington to 138 kV Convert 69 kV terminal equipment at Paoli Switch to 138 kV | WFEC | 2026-09-30 | 21382126
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | Catoosa Terminal Upgrade | TBD | Replace switch, jumpers, and CTs at Catoosa 138 kV to achieve a minimum rating of 348 MVA | AEPW/GRDA | TBD | 4765714
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | 2020 ITP | ERIS | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | 143182 | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | AEPW/OKGE | 45939 | 12238460
Contingent | DISIS-2023-001 CF | Steady State | 05 SOUTHWEST | DISIS-2016-002 | NRIS | Curry - Deafsmith 115 kV Ckt 1 Rebuild | 122645 | Rebuild line to achieve minimum normal/emergency rating of 90/90 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | SPS | TBD | 4852215
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | 2023 ITP | NRIS | Czech Hall 138 kV Terminal Upgrade | 122761 | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | OKGE | 2025-12-01 | 154916
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2023-001 | NRIS | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | TBD | Upgrade Terminal Equipment on the DRYGULCH to G23-028-TAP line Ckt 1 to achieve a rating of 443 MVA | GRDA | TBD (36-month lead time) | 254602
Contingent | DISIS-2023-001 CF | Steady State / Stability | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | ERIS | G17-151-Tap to G18-015-Tap 345 kV New Line | TBD | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | SPS | TBD (36 month lead time) | 117410790.53
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | NRIS | G17-151-Tap to G18-015-Tap 345 kV New Line | TBD | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | SPS | TBD (36 month lead time) | 117410790.53
Contingent | DISIS-2023-001 CF | Steady State / Stability | 05 SOUTHWEST | DISIS-2022-001 | ERIS | Gracemont to G16-037-Tap 345 kV New Line | TBD | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | OKGE/AEPW | 36 | 88218000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | NRIS | Gracemont to G22-114-Tap 345 kV New Line | TBD | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | AEPW/OKGE | 36 | 140400000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | ERIS | Gracemont to Minco 345 kV New Line | TBD | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | OKGE | 36 | 37206000
Contingent | DISIS-2023-001 CF | Steady State | 05 SOUTHWEST | DISIS-2022-001 | ERIS | Gracemont to Treasure Island 345 kV New Line | TBD | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | AEPW | 36 | 17442000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | NRIS | Gracemont to Treasure Island 345 kV New Line | TBD | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | AEPW | 36 | 17442000
Contingent | DISIS-2023-001 CF | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Hobbs to Andrews Voltage Conversion | TBD | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | SPS | 36 | 53295780
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | HOC404 5 to BAX488 5 161kV Line Rebuild | TBD | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | EMDE | TBD (36 month lead time) | 2543382.4
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | 2024 ITP | NRIS | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | 169968/170009/170008/170565/170568 | Build a new SIDNEY__-MB3 to HOLCOMB7 345 kV line 1 (300 miles) to a standard rating of 1792 MVA | AMIL/SUNC | 2029-11-12 | 977728865
Contingent | DISIS-2023-001 CF | Steady State / Stability | 05 SOUTHWEST | DISIS-2022-001 | ERIS | Lawton Eastside to Draper 345 kV New Line | TBD | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | AEPW/OKGE | TBD (36 month lead time) | 352800000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | NRIS | Lawton Eastside to Draper 345 kV New Line | TBD | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | AEPW/OKGE | TBD (36 month lead time) | 352800000
Contingent | DISIS-2023-001 CF | Steady State / Stability | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | ERIS | Lawton Eastside to G20-009-TAP 345kV New Line | TBD | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | AEPW | 36 | 184860000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | NRIS | Lawton Eastside to G20-009-TAP 345kV New Line | TBD | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | AEPW | 36 | 184860000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | LYDIA7 to WELSH Line Rebuild | TBD | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | AEPW | TBD (36 month lead time) | 126087000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | 2024 ITP | NRIS | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | TBD | Terminal Upgrade on Martin City East to Martin City West 161 kV line | KCPL | TBD | 786451
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | 2024 ITP | ERIS | Maud Tap 138 kV Terminal Upgrade | TBD | Terminal Upgrade on Maud Tap 138 kV | AEPW/OKGE | 2026-05-31 | 736625
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | MIAMI to HOC404 5 161kV Line Rebuild | TBD | Rebuild the MIAMI 5 to HOC404 5 161 kV line CKT1 (9.9 miles) to a minimum rating of 359 MVA | GRDA/EMDE | TBD (36 month lead time) | 10340522
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | 2023 ITP | NRIS | Multi - Atlantic- Craig - West Gardener 345/115 kV | 158641 | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | KCPL | 2025-04-02 | 28123307
Contingent | DISIS-2023-001 CF | Steady State | 05 SOUTHWEST | 2021 ITP | NRIS | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | 156407, 156408, 156409, 156110, 156111, 156112 | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | SPS | 2026-05-15 | 359465155
Contingent | DISIS-2023-001 CF | Steady State | 01 NORTH | 2021 ITP10 | ERIS | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | 50442, 50444, 50445, 50446 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | NPPD | 12/31/2027 (Delay - Mitigation) | 496505813
Contingent | DISIS-2023-001 CF | Steady State / Stability | 04 SOUTHEAST / 05 SOUTHWEST | 2020 ITP | ERIS | Multi - Minco - Pleasant Valley - Draper 345 kV | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | OKGE | 2025-01-23 | 16516041
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | 2020 ITP | NRIS | Multi - Minco - Pleasant Valley - Draper 345 kV | 122863, 122848, 122849, 12285TBD, 122851, 122858, 133TBD85, 1331TBD6, 143176, 143257 | Install terminal equipment at Minco substation 345 kV to support a new 345 kV line from Minco with a summer emergency rating of 1792 MVA Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper and terminals to accommodate cut in of existing Cimarron to Draper 345 kV line. Tie into existing Cimarron to Draper 345 kV line. This description is specific to the 345 kV components. Upgrade any necessary terminal equipment on the Cimarron to Draper 345 kV line to achieve a summer emergency rating of 1540 MVA Build 34.8 miles of 345 kV line from Minco to Pleasant Valley 345 kV to achieve a 1792 MVA summer emergency rating. Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA Install a new line terminal at Draper 345 kV to accommodate new 345 kV line from Pleasant Valley. Expand the existing Pleasant Valley 138 kV substation to 345 kV with new terminals to accommodate new line from Minco to Pleasant Valley to Draper. This description is specific to the 138 kV components. (NTC 210616, 210656) | OKGE | 2025-01-23 | 16516041
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DPA-2017-August-767-774-776 | ERIS | Multi - Park Community - Sunshine 138 kV | 72018 72019 72020 72021 72022 72023 72024 72025 72026 72027 72028 72029 72030 72031 | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. New Calumet 138 kV substation with 4-terminal ring bus. Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | WFEC | 2025-10-30 | 34866355
Contingent | DISIS-2023-001 CF | Steady State / Stability | 02 NEBRASKA | DPA-2016-December-703 | ERIS | Multi - Sheldon - Monolith 115 kV | 71963/71964/71965/71966/71967/71968 | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | NPPD | 2026-01-01 | 60975092
Contingent | DISIS-2023-001 CF | Steady State | 02 NEBRASKA | DPA-2016-December-703 | NRIS | Multi - Sheldon - Monolith 115 kV | 71963/71964/71965/71966/71967/71968 | Add new 345/115 kV ckt 1 and ckt 2 transformers at Monolith substation and make the necessary terminal upgrades and re-terminations Monolith 345-115 kV substation. | NPPD | 2026-01-01 | 60975092
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DPA-2021-March-1296 | ERIS | Multi - West Oaks - Council - Classen 138 kV Reconductor | 144297/144281 | Upgrade any necessary terminal equipment at Classen substation. Reconductor of Douglas Tap to Classen 138 kV transmission line. | OKGE | 2025-11-28 | 1390000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DPA-2021-March-1296 | NRIS | Multi - West Oaks - Council - Classen 138 kV Reconductor | 144297/144281 | Upgrade any necessary terminal equipment at Classen substation. Reconductor of Douglas Tap to Classen 138 kV transmission line. | OKGE | 2025-11-28 | 1390000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | 2023 ITP | ERIS | Neosho 345 kV Terminal Upgrade | 157403 | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA. | WERE | 5 | 1534495
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | TBD | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | WERE | TBD (36 month lead time) | 96314434
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2016-002 | NRIS | Newhart - Plant X 230 kV Ckt 1 Rebuild | 122641 | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | SPS | TBD | 697513
Contingent | DISIS-2023-001 CF | Steady State | 01 NORTH / 02 NEBRASKA | 2021 ITP | NRIS | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | 143613, 143614 | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. Increase ground clearance of the Whitlock - Glenham 230 kV. | WAPA | 2025-09-01 | 389405
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | NRIS | Oklaunion to G22-011-TAP 345kV New Line | TBD | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | AEPW | TBD (36 month lead time) | 87780000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2021-001 | ERIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | TBD | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | KCPL | TBD (36-month lead time) | 150000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST | DISIS-2021-001 | NRIS | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | TBD | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A/B of 765/890 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | KCPL | TBD (36-month lead time) | 150000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2021-001 | ERIS | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | TBD | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA (Minimum Rate B of 765 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | KCPL | TBD (36-month lead time) | 150000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | 2023 ITP | NRIS | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | 158629, 158630, 158631, 158632 | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Install new 345/230 transformer at Potter County 345 kV substation ckt 2 Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 Replace existing 345/230 kV transformer at Potter County substation ckt 1 | SPS | 2028-12-15 | 37534234
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2021-001 | ERIS | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | TBD | Rebuild the PATMOS to FULTON 115kV line CKT1 (14.95 miles) to a minimum rating of 172 MVA | EES-EAI/AEPW | TBD (36 month lead time) | 5093561
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2023-001 | NRIS | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 | TBD | Rebuild 5MANSFDMN to G23-085-TAP 161 kV line 1 to a minimum rating of 231 MVA | SWPA/AECI | TBD (36-month lead time) | 2200000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2023-001 | NRIS | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | TBD | Rebuild 5MOCITYB2 to G23-169-TAP 161 kV line 1 to a minimum rating of 278 MVA | KCPL | TBD (36-month lead time) | 2000000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2022-001 | NRIS | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1 | TBD | Rebuild the existing EAST ST3 to WEMPORI3 115 kV line 1 (5.1 miles) to a minimum rating of 120 MVA | WERE | 48 | 38625284
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2023-001 | NRIS | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line | TBD | Rebuild the 5HEBER.N# to GREERSF5 161 kV line CKT1 (1.6 miles) to a minimum rating of 229 MVA | EES-EAI/SWPA | TBD (36-month lead time) | 2224000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST | DISIS-2023-001 | NRIS | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | TBD | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | GRDA | TBD (36-month lead time) | 14429000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2023-001 | NRIS | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line | TBD | Rebuild the PENSA 5 to G23-049-TAP 161 kV line CKT1 (6.5 miles) to a minimum rating of 449 MVA | GRDA | TBD (36-month lead time) | 135805
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST | DISIS-2023-001 | NRIS | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | TBD | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | GRDA | TBD (36-month lead time) | 5291000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2023-001 | NRIS | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | TBD | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | SWPA/OKGE | TBD (36-month lead time) | 3600000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2023-001 | NRIS | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | TBD | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 175 MVA | AEPW | TBD (36-month lead time) | 460000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2023-001 | NRIS | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | TBD | Rebuild LBRTYST5 to BRMGHAM5 161 kV line 1 to a minimum rating of 275 MVA | KCPL | TBD (36-month lead time) | 9000000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2022-001 | ERIS | Rebuild the NEO SPA5 to TIP292 5 161kV Line 1 (EMDE) | TBD | Rebuild the existing NEO SPA5 to TIP292 5 161 kV line 1 (10.6 miles) to a minimum rating of 270/315 MVA | EMDE | TBD (36-month lead time) | 10369174.4
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST | DISIS-2023-001 | NRIS | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | TBD | Rebuild ORO110 to RIV4525 161 kV line 1 line to a minimum rating of 558 MVA | EMDE | TBD (36-month lead time) | 25592475
Contingent | DISIS-2023-001 CF | Steady State | 02 NEBRASKA | DISIS-2020-001 | ERIS | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate) | 158605 | Conductor uprate of the existing S3451-RAUN 3 to G18-043 TAP 345 kV Line 1 (14.12 miles) and S3451 terminal upgrades to achieve a minimum rating of 1000 MVA. | OPPD | TBD (36-month lead time) | 1101824
Contingent | DISIS-2023-001 CF | Steady State | 02 NEBRASKA | DISIS-2021-001 | ERIS | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | TBD | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | NPPD/WAPA | TBD (36-month lead time) | 20859647.5
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2023-001 | NRIS | Reconfigure the Neosho Transformers | TBD | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | WERE | TBD (36-month lead time) | 19662160
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2022-001 | NRIS | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | TBD | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | AEPW | 36 | 8302968
Contingent | DISIS-2023-001 CF | Steady State | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | SPS | 36 | 8302968
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2022-001 | ERIS | RIV4525 to BAX488 5 161kV Line Rebuild | TBD | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | EMDE | 36 | 5076982.56
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2018-002/2019-001 | ERIS | Sweetwater to Chisholm 230 kV Line Rebuild | 170509 | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | AEPW | TBD (36 month lead time) | 25920000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2018-002/2019-001 | NRIS | Sweetwater to Chisholm 230 kV Line Rebuild | 170509 | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | AEPW | TBD (36 month lead time) | 25920000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST | DISIS-2018-002/2019-001 | NRIS | Sweetwater to Demarcation 230 kV Line Rebuild | TBD | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | AEPW/SPS | TBD (36 month lead time) | 25920000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL | DISIS-2023-001 | NRIS | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1 | TBD | Upgrade Terminal Equipment at CARTHAG5 to achieve a minimum summer/winter rating of 303/326 MVA | SWPA | TBD (36-month lead time) | 250000
Contingent | DISIS-2023-001 CF | Steady State | 05 SOUTHWEST | DISIS-2023-001 | NRIS | Upgrade the existing PLANTX 230/115 kV Transformer | TBD | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | SPS | TBD (36-month lead time) | 8100000
Contingent | DISIS-2023-001 CF | Steady State | 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | ERIS | WELSH 7 to WILKES 7 345kV Line Rebuild | TBD | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | AEPW | TBD (36 month lead time) | 119457000
Contingent | DISIS-2023-001 CF | Steady State | 03 CENTRAL / 04 SOUTHEAST / 05 SOUTHWEST | DISIS-2022-001 | NRIS | WELSH 7 to WILKES 7 345kV Line Rebuild | TBD | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | AEPW | TBD (36 month lead time) | 119457000
Contingent | DISIS-2023-001 CF | Steady State / Stability | 05 SOUTHWEST | DISIS-2022-001 | ERIS | Woodward EHV to Beckham 345 kV New Line | TBD | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | OKGE | TBD (36 month lead time) | 134640000
Contingent | DISIS-2023-001 CF | Stability | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Border to Beckham 345 kV New Line | TBD | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | OKGE | TBD (36 month lead time) | 35352000
Contingent | DISIS-2023-001 CF | Stability | 05 SOUTHWEST | DISIS-2020-001 | ERIS | Build New G17-151-Tap to Border 345 kV Line | TBD | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | OKGE | TBD (36 month lead time) | 335411258
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Chappelle Creek 345 kV Substation Interconnection (Non-Shared NU) (BEPC) | 158661 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-105(249 MW/Wind), into Chappelle Creek 345 kV Substation | BEPC | 66 | 11207272
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Groton - Leland Olds 345 kV Line Interconnection (Non-Shared NU) (BEPC) | 158665 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-182 (300MW/Wind), into Groton - Leland Olds 345 kV Line | BEPC | 66 | 22697499
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Kingsbury County 115kV Substation GEN-2023-012 Interconnection (TOIF) (EREP) | 158696 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-012 (98.6MW/Wind), into Kingsbury County 115kV Substation | EREP | 18 | 5135000
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Kingsbury County 115kV Substation GEN-2023-012 Interconnection (Non-Shared NU) (EREP) | 158697 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-012 (98.6MW/Wind), into Kingsbury County 115kV Substation | EREP | 0 | 0
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | REN 115 kV Substation GEN-2023-062 Interconnection (TOIF) (LYREC) | 158779 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-062 (98MW/Thermal), into REN 115 kV Substation | LYREC | 66 | 407172
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | REN 115 kV Substation GEN-2023-062 Interconnection (Non-Shared NU) (LYREC) | 158780 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-062 (98MW/Thermal), into REN 115 kV Substation | LYREC | 66 | 4940802
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | White 115 kV Substation GEN-2023-082 Interconnection (TOIF) (WAPA) | 158810 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-082 (175MW/Battery/Storage), into White 115 kV Substation | WAPA | 75 | 4790000
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | White 115 kV Substation GEN-2023-082 Interconnection (Non-Shared NU) (WAPA) | 158811 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-082 (175MW/Battery/Storage), into White 115 kV Substation | WAPA | 75 | 0
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Judson 345 kV Substation GEN-2023-097 Interconnection (TOIF) (BEPC) | 158833 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-097 (250MW/Battery/Storage), into Judson 345 kV Substation | BEPC | 66 | 3010423
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Judson 345 kV Substation GEN-2023-097 Interconnection (Non-Shared NU) (BEPC) | 158834 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-097 (250MW/Battery/Storage), into Judson 345 kV Substation | BEPC | 66 | 3197203
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Chappelle Creek 345 kV Substation GEN-2023-105 Interconnection (TOIF) (BEPC) | 158847 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-105 (249MW/Wind), into Chappelle Creek 345 Kv Substation | BEPC | 66 | 2041297
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Fort Thompson - Huron 230 kV Tap GEN-2023-154 Interconnection (TOIF) (WAPA) | 158910 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-154 (175MW/Solar), into Fort Thompson - Huron 230 kV Tap | WAPA | 75 | 641000
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Fort Thompson - Huron 230 kV Tap GEN-2023-154 Interconnection (Non-Shared NU) (WAPA) | 158911 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-154 (175MW/Solar), into Fort Thompson - Huron 230 kV Tap | WAPA | 75 | 9974000
Interconnection | DISIS-2023-001 | Steady State | 01 NORTH | DISIS-2023-001 | ERIS | Groton - Leland Olds 345 kV Line GEN-2023-182 Interconnection (TOIF) (BEPC) | 158956 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-182 (300MW/Wind), into Groton - Leland Olds 345 kV Line | BEPC | 66 | 4110843
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Keystone 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | 158667 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-116/117 (500/300MW/Wind), into Keystone 345 kV Substation | NPPD | 60 | 7500000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | New Beatrice Power Station 345 kV Interconnection (DISIS-2023-001) (NPPD) | 158670 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222/223 (478/239MW/Thermal), into New Beatrice Power Station 345 kV | NPPD | 60 | 58400000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Olive Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | 158671 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224/225 (478/217MW/Thermal), into Olive Creek 345 kV Substation | NPPD | 60 | 110800000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Substation 3740 345 kV Interconnection (DISIS-2023-001) (OPPD) | 158676 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077/078/079 (255MW/255MW/303MW/Thermal), into Substation 3740 345 kV | OPPD | 48 | 41127486
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Turtle Creek 345 kV Substation Interconnection (DISIS-2023-001) (NPPD) | 158678 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216/217/218 (200MW/Wind), into Turtle Creek 345 kV Substation | NPPD | 60 | 11700000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Harbine 115 kV Substation GEN-2023-011 Interconnection (TOIF) (NPPD) | 158694 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-011 (190MW/Wind), into Harbine 115 kV Substation | NPPD | 36 | 500000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Harbine 115 kV Substation GEN-2023-011 Interconnection (Non-Shared NU) (NPPD) | 158695 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-011 (190MW/Wind), into Harbine 115 kV Substation | NPPD | 36 | 2300000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Substation 3740 345 kV GEN-2023-077 Interconnection (TOIF) (OPPD) | 158803 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-077 (255MW/Thermal), into Substation 3740 345 kV | OPPD | 42 | 3348775
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Substation 3740 345 kV GEN-2023-078 Interconnection (TOIF) (OPPD) | 158804 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-078 (255MW/Thermal), into Substation 3740 345 kV | OPPD | 42 | 3004365
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Substation 3740 345 kV GEN-2023-079 Interconnection (TOIF) (OPPD) | 158805 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-079 (303MW/Thermal), into Substation 3740 345 kV | OPPD | 42 | 3004365
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Keystone 345 kV Substation GEN-2023-116 Interconnection (TOIF) (NPPD) | 158859 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-116 (500MW/Wind), into Keystone 345 kV Substation | NPPD | 60 | 1000000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Keystone 345 kV Substation GEN-2023-117 Interconnection (TOIF) (NPPD) | 158860 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-117 (300MW/Wind), into Keystone 345 kV Substation | NPPD | 60 | 1000000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Sweetwater 345 kV Substation GEN-2023-133 Interconnection (TOIF) (NPPD) | 158876 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-133 (250MW/Wind), into Sweetwater 345 kV Substation | NPPD | 60 | 0
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Sweetwater 345 kV Substation GEN-2023-133 Interconnection (Non-Shared NU) (NPPD) | 158877 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-133 (250MW/Wind), into Sweetwater 345 kV Substation | NPPD | 60 | 100000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Grant 115 kV Substation GEN-2023-153 Interconnection (TOIF) (Tri-State) | 158908 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-153 (120MW/Hybrid), into Grant 115 kV Substation | TSGT | 36 | 1250000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Grant 115 kV Substation GEN-2023-153 Interconnection (Non-Shared NU) (Tri-State) | 158909 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-153 (120MW/Hybrid), into Grant 115 kV Substation | TSGT | 36 | 5250000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Twin Church 230 kV Substation GEN-2023-199 Interconnection (TOIF) (NPPD) | 158981 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-199 (250MW/Hybrid), into Twin Church 230 kV Substation | NPPD | 36 | 500000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Twin Church 230 kV Substation GEN-2023-199 Interconnection (Non-Shared NU) (NPPD) | 158982 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-199 (250MW/Hybrid), into Twin Church 230 kV Substation | NPPD | 36 | 1200000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Turtle Creek 345 kV Substation GEN-2023-216 Interconnection (TOIF) (NPPD) | 159013 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-216 (200MW/Wind), into Turtle Creek 345 kV Substation | NPPD | 60 | 1000000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Turtle Creek 345 kV Substation GEN-2023-217 Interconnection (TOIF) (NPPD) | 159014 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-217 (200MW/Wind), into Turtle Creek 345 kV Substation | NPPD | 60 | 1000000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Turtle Creek 345 kV Substation GEN-2023-218 Interconnection (TOIF) (NPPD) | 159015 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-218 (200MW/Wind), into Turtle Creek 345 kV Substation | NPPD | 60 | 1000000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | New Beatrice Power Station 345 kV GEN-2023-222 Interconnection (TOIF) (NPPD) | 159022 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-222 (478MW/Thermal), into New Beatrice Power Station 345 kV | NPPD | 60 | 1000000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | New Beatrice Power Station 345 kV GEN-2023-223 Interconnection (TOIF) (NPPD) | 159023 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-223 (239MW/Thermal), into New Beatrice Power Station 345 kV | NPPD | 60 | 1000000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Olive Creek 345 kV Substation GEN-2023-224 Interconnection (TOIF) (NPPD) | 159024 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-224 (478MW/Thermal), into Olive Creek 345 kV Substation | NPPD | 60 | 1000000
Interconnection | DISIS-2023-001 | Steady State | 02 NEBRASKA | DISIS-2023-001 | ERIS | Olive Creek 345 kV Substation GEN-2023-225 Interconnection (TOIF) (NPPD) | 159025 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-225 (217MW/Thermal), into Olive Creek 345 kV Substation | NPPD | 60 | 1000000
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Holcomb 345 kV Interconnection (DISIS-2023-001) (SUNC) | 158666 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172/173 (200/100MW/Wind), into Holcomb 345 kV | SUNC | 48 | 9008488
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rose Hill 345 kV Substation Interconnection GEN-2023-073 (Non-Shared NU) (Evergy) | 158674 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-073 250MW/Battery/Storage), into Rose Hill 345 kV Substation | Evergy | 56 | 16154742
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Setab 345 kV Substation Interconnection (DISIS-2023-001) (SUNC) | 158675 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-107 (300MW/Wind), into Setab 345 kV Substation | SUNC | 48 | 5338489
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Wolf Creek- Blackberry 345 kV Line Break GEN-2023-006 Interconnection (TOIF) (NEET) | 158686 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-006 (202MW/Wind), into Wolf Creek- Blackberry 345 kV Line Break | NEET | 42 | 0
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Wolf Creek- Blackberry 345 kV Line Break GEN-2023-006 Interconnection (Non-Shared NU) (NEET) | 158687 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-006 (202MW/Wind), into Wolf Creek- Blackberry 345 kV Line Break | NEET | 42 | 26745964
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Finney-Carpenter 345 KV line GEN-2023-015 Interconnection (TOIF) (SPS) | 158700 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-015 (330MW/Solar), into Finney-Carpenter 345 KV line | SPS | TBD (48-month lead time) | 3480128
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Finney-Carpenter 345 KV line GEN-2023-015 Interconnection (Non-Shared NU) (SPS) | 158701 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-015 (330MW/Solar), into Finney-Carpenter 345 KV line | SPS | TBD (48-month lead time) | 42358867
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Center City 161 kV Substation GEN-2023-023 Interconnection (TOIF) (KACY) | 158714 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-023 (200MW/Battery/Storage), into Center City 161 kV Substation | KACY | 0 | 0
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Center City 161 kV Substation GEN-2023-023 Interconnection (Non-Shared NU) (KACY) | 158715 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-023 (200MW/Battery/Storage), into Center City 161 kV Substation | KACY | 40 | 4998381
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Odessa and Lexington 161 kV Line GEN-2023-032 Interconnection (TOIF) (Evergy) | 158732 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-032 (200MW/Solar), into Odessa and Lexington 161 kV Line | Evergy | 36 | 940803
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Odessa and Lexington 161 kV Line GEN-2023-032 Interconnection (Non-Shared NU) (Evergy) | 158733 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-032 (200MW/Solar), into Odessa and Lexington 161 kV Line | Evergy | 36 | 17300479
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Liberty South 161 kV Substation GEN-2023-033 Interconnection (TOIF) (Evergy) | 158734 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-033 (200MW/Battery/Storage), into Liberty South 161 kV Substation | Evergy | 36 | 940803
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Liberty South 161 kV Substation GEN-2023-033 Interconnection (Non-Shared NU) (Evergy) | 158735 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-033 (200MW/Battery/Storage), into Liberty South 161 kV Substation | Evergy | 36 | 1265759
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Clear Water - Waco 138 kV line GEN-2023-034 Interconnection (TOIF) (Evergy) | 158736 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-034 (130MW/Solar), into Clear Water - Waco 138 kV line | Evergy | 36 | 928794
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Clear Water - Waco 138 kV line GEN-2023-034 Interconnection (Non-Shared NU) (Evergy) | 158737 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-034 (130MW/Solar), into Clear Water - Waco 138 kV line | Evergy | 36 | 15091408
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Eckles Road 161 kV Substation GEN-2023-036 Interconnection (TOIF) (INDN) | 158740 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-036 (165MW/Battery/Storage), into Eckles Road 161 kV Substation. | INDN | 42 | 500000
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Eckles Road 161 kV Substation GEN-2023-036 Interconnection (Non-Shared NU) (INDN) | 158741 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-036 (165MW/Battery/Storage), into Eckles Road 161 kV Substation | INDN | 42 | 2800000
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Nearman 161 kV Substation GEN-2023-037 Interconnection (TOIF) (KACY) | 158742 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-037 (200MW/Battery/Storage), into Nearman161 kV Substation | KACY | 0 | 0
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Nearman 161 kV Substation GEN-2023-037 Interconnection (Non-Shared NU) (KACY) | 158743 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-037 (200MW/Battery/Storage), into Nearman 161 kV Substation | KACY | 40 | 3357305
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Neosho 345 kV Substation GEN-2023-050 Interconnection (TOIF) (Evergy) | 158759 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-050 (400MW/Hybrid), into Neosho 345 kV Substation | Evergy | 56 | 1873996
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Neosho 345 kV Substation GEN-2023-050 Interconnection (Non-Shared NU) (Evergy) | 158760 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-050 (400MW/Hybrid), into Neosho 345 kV Substation | Evergy | 56 | 14476634
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carthage 161 kV Substation GEN-2023-061 Interconnection (TOIF) (SWPA) | 158777 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-061 (100MW/Battery/Storage), into Carthage 161 kV Substation | SWPA | 48 | 700000
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Carthage 161 kV Substation GEN-2023-061 Interconnection (Non-Shared NU) (SWPA) | 158778 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-061 (100MW/Battery/Storage), into Carthage 161 kV Substation | SWPA | 48 | 4200000
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Halstead 69 kV Substation GEN-2023-065 Interconnection (TOIF) (Evergy) | 158785 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-065 (140MW/Battery/Storage), into Halstead 69 kV Substation | Evergy | 36 | 897140
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Halstead 69 kV Substation GEN-2023-065 Interconnection (Non-Shared NU) (Evergy) | 158786 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-065 (140MW/Battery/Storage), into Halstead 69 kV Substation | Evergy | 36 | 949941
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Rose Hill 345 kV Substation GEN-2023-073 Interconnection (TOIF) (Evergy) | 158800 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-073 250MW/Battery/Storage), into Rose Hill 345 kV Substation | Evergy | 56 | 1958090
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Mansfield - Logan 161 kV Line GEN-2023-085 Interconnection (TOIF) (SWPA) | 158816 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-085 (150MW/Wind), into Mansfield - Logan 161 kV Line | SWPA | 48 | 800000
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Mansfield - Logan 161 kV Line GEN-2023-085 Interconnection (Non-Shared NU) (SWPA) | 158817 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-085 (150MW/Wind), into Mansfield - Logan 161 kV Line | SWPA | 48 | 8600000
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Archie 161 kV Substation GEN-2023-087 Interconnection (TOIF) (Evergy) | 158820 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-087 (200MW/Solar), into Archie 161 kV Substation | Evergy | 36 | 1085685
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Archie 161 kV Substation GEN-2023-087 Interconnection (Non-Shared NU) (Evergy) | 158821 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-087 (200MW/Solar), into Archie 161 kV Substation | Evergy | 36 | 26353701
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Jeffery Energy Center 345 kV Substation GEN-2023-099 Interconnection (TOIF) (Evergy) | 158837 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-099 (300MW/Solar), into Jeffery Energy Center 345 kV Substation | Evergy | 60 | 112910
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Jeffery Energy Center 345 kV Substation GEN-2023-099 Interconnection (Non-Shared NU) (Evergy) | 158838 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-099 (300MW/Solar), into Jeffery Energy Center 345 kV Substation | Evergy | 36 | 0
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Setab 345 kV Substation GEN-2023-107 Interconnection (TOIF) (SUNC) | 158849 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-107 (300MW/Wind), into Setab 345 kV | SUNC | 48 | 2206495
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | LaCygne - Stilwell 345 kV Line GEN-2023-149 Interconnection (TOIF) (Evergy) | 158900 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-149 (300MW/Battery/Storage), into LaCygne - Stilwell 345 kV Line | Evergy | 56 | 1958092
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | LaCygne - Stilwell 345 kV Line GEN-2023-149 Interconnection (Non-Shared NU) (Evergy) | 158901 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-149 (300MW/Battery/Storage), into LaCygne - Stilwell 345 kV Line | Evergy | 56 | 33114559
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Missouri City - Liberty South 161 kV Line GEN-2023-169 Interconnection (TOIF) (Evergy) | 158936 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-169 (125MW/Battery/Storage), into Missouri City - Liberty South 161 kV Line | Evergy | 36 | 1085688
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Missouri City - Liberty South 161 kV Line GEN-2023-169 Interconnection (Non-Shared NU) (Evergy) | 158937 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-169 (125MW/Battery/Storage), into Missouri City - Liberty South 161 kV Line | Evergy | 36 | 17089522
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Salisbury 161 kV Substation GEN-2023-170 Interconnection (TOIF) (Evergy) | 158938 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-170 (150MW/Battery/Storage), into Salisbury 161 kV Substation | Evergy | 36 | 1085688
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Salisbury 161 kV Substation GEN-2023-170 Interconnection (Non-Shared NU) (Evergy) | 158939 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-170 (150MW/Battery/Storage), into Salisbury 161 kV Substation | Evergy | 36 | 6267996
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Sub M 161 kV Substation GEN-2023-171 Interconnection (TOIF) (INDN) | 158940 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-171 (150MW/Battery/Storage), into Sub M 161 kV Substation. | INDN | 42 | 500000
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Sub M 161 kV Substation GEN-2023-171 Interconnection (Non-Shared NU) (INDN) | 158941 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-171 (150MW/Battery/Storage), into Sub M 161 kV Substation | INDN | 42 | 3280000
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Holcomb 345 kV GEN-2023-172 Interconnection (TOIF) (SUNC) | 158942 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-172 (200MW/Wind), into Holcomb 345 kV | SUNC | 48 | 2718247
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Holcomb 345 kV GEN-2023-173 Interconnection (TOIF) (SUNC) | 158943 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-173 (100MW/Wind), into Holcomb 345 kV | SUNC | 48 | 2718247
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Riverton - Neosho 161 kV Line Tap GEN-2023-194 Interconnection (TOIF) (EDE) | 158973 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-194 (225MW/Solar), into Riverton - Neosho 161 kV Line Tap (sharing the gen-tie with GEN-2020-079) | EMDE | 0 | 0
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Riverton - Neosho 161 kV Line Tap GEN-2023-194 Interconnection (Non-Shared NU) (EDE) | 158974 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-194 (225MW/Solar), into Riverton - Neosho 161 kV Line Tap (sharing the gen-tie with GEN-2020-079) | EMDE | 30 | 2368711.8
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Reading - Osage Jct 115 kV Line GEN-2023-219 Interconnection (TOIF) (Evergy) | 159016 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-219 (125MW/Solar), into Reading - Osage Jct 115 kV Line | Evergy | 36 | 927366
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Reading - Osage Jct 115 kV Line GEN-2023-219 Interconnection (Non-Shared NU) (Evergy) | 159017 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-219 (125MW/Solar), into Reading - Osage Jct 115 kV Line | Evergy | 36 | 14414502
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-220 Interconnection (TOIF) (Evergy) | 159018 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-220 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | Evergy | 56 | 1958092
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-220 Interconnection (Non-Shared NU) (Evergy) | 159019 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-220 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | Evergy | 56 | 32882571
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-221 Interconnection (TOIF) (Evergy) | 159020 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-221 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | Evergy | 56 | 1958092
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Emporia Energy Center - Swissvale 345 kV Line GEN-2023-221 Interconnection (Non-Shared NU) (Evergy) | 159021 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-221 (250MW/Solar), into Emporia Energy Center - Swissvale 345 kV Line | Evergy | 56 | 33237331
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Neosho - LaCynge 345 kV Line GEN-2023-231 Interconnection (TOIF) (Evergy) | 159036 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-231 (310MW/Hybrid), into Neosho - LaCynge 345 kV Line | Evergy | 56 | 1958090
Interconnection | DISIS-2023-001 | Steady State | 03 CENTRAL | DISIS-2023-001 | ERIS | Neosho - LaCynge 345 kV Line GEN-2023-231 Interconnection (Non-Shared NU) (Evergy) | 159037 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-231 (310MW/Hybrid), into Neosho - LaCynge 345 kV Line | Evergy | 56 | 80302305
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Degrasse 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | 158662 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100/102 (300/475MW/Hybrid), into Degrasse 345 kV Substation | OKGE | 36 | 7460545
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Delaware - Neosho 345 kV Interconnection (DISIS-2023-001) (Evergy) | 158663 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-075/076 (200/100MW/Wind), into Delaware - Neosho 345 kV | Evergy | 56 | 31404400
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Gracemont 345 kV Substation Interconnection (DISIS-2023-001) (OGE) | 158664 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-164/165 (210MW/Battery/Storage), into Gracemont 345 kV Substation | OKGE | 48 | 4584856
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Hugo 138 kV Substation GEN-2023-009 Interconnection (TOIF) (WFEC) | 158690 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-009 (250MW/Battery/Storage), into Hugo 138 kV Substation | WFEC | 60 | 517000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Hugo 138 kV Substation GEN-2023-009 Interconnection (Non-Shared NU) (WFEC) | 158691 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-009 (250MW/Battery/Storage), into Hugo 138 kV Substation | WFEC | 60 | 1200000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Candian River 345 kV Substation GEN-2023-022 Interconnection (TOIF) (OGE) | 158712 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-022 (250MW/Wind), into CaN/Adian River 345 kV Substation | OKGE | 48 | 1591654
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Candian River 345 kV Substation GEN-2023-022 Interconnection (Non-Shared NU) (OGE) | 158713 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-022 (250MW/Wind), into Candian River 345 kV Substation | OKGE | 48 | 1790488
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Bird Hollow (Langley) - Pryor Junction 138 kV Line GEN-2023-027 Interconnection (TOIF) (AEP) | 158722 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-027 (150MW/Hybrid), into Bird Hollow (Langley) - Pryor Junction 138 kV Line | AEP | 36 | 2125000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Bird Hollow (Langley) - Pryor Junction 138 kV Line GEN-2023-027 Intercon (Non-Shared NU) (AEP) | 158723 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-027 (150MW/Hybrid), into Bird Hollow (Langley) - Pryor Junction 138 kV Line | AEP | 36 | 11850000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-028 Interconnection (TOIF) (GRDA) | 158724 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-028 (230MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | GRDA | 24 | 1057500
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-028 Interconnection (Non-Shared NU) (GRDA) | 158725 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-028 (230MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | GRDA | 24 | 6545735
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap between 345 kV SW Shreveport-Dolet Hills Subs GEN-2023-030 Interconnection (TOIF) (AEP) | 158728 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-030 (25MW/Solar), into Tap between 345 kV SW Shreveport-Dolet Hills Subs | AEP | 18 | 206941
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap between 345 kV SW Shreveport-Dolet Hills SubsGEN-2023-030 Interconnection (Non-Shared NU) (AEP) | 158729 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-030 (25MW/Solar), into Tap between 345 kV SW Shreveport-Dolet Hills Subs | AEP | 18 | 171180
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Cleveland - Amber Tap 138 kV Line GEN-2023-035 Interconnection (TOIF) (WFEC) | 158738 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-035 (200MW/Solar), into Cleveland - Amber Tap 138 kV Line | WFEC | 60 | 517000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Cleveland - Amber Tap 138 kV Line GEN-2023-035 Interconnection (Non-Shared NU) (WFEC) | 158739 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-035 (200MW/Solar), into Cleveland - Amber Tap 138 kV Line | WFEC | 60 | 6050000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lula 138 kV Substation GEN-2023-038 Interconnection (TOIF) (OGE) | 158744 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-038 (200MW/Solar), into Lula 138 kV Substation | OKGE | 36 | 3711456
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lula 138 kV Substation GEN-2023-038 Interconnection (Non-Shared NU) (OGE) | 158745 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-038 (200MW/Solar), into Lula 138 kV Substation | OKGE | 36 | 2513699
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-049 Interconnection (TOIF) (GRDA) | 158757 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-049 (150MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | GRDA | 24 | 852499
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Dry Gulch - Pensacola 161 kV Line GEN-2023-049 Interconnection (Non-Shared NU) (GRDA) | 158758 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-049 (150MW/Hybrid), into Dry Gulch - Pensacola 161 kV Line | GRDA | 24 | 5801735
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Kerr Grove 161 kV GEN-2023-055 Interconnection (TOIF) (GRDA) | 158768 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-055 (100MW/Battery/Storage), into Kerr Grove 161 kV | GRDA | 24 | 2619247
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Kerr Grove 161 kV GEN-2023-055 Interconnection (Non-Shared NU) (GRDA) | 158769 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-055 (100MW/Battery/Storage), into Kerr Grove 161 kV | GRDA | 24 | 1750000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Van Buren 161 kV GEN-2023-056 Interconnection (TOIF) (SWPA) | 158770 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-056 (150MW/Battery/Storage), into Van Buren 161 kV | SWPA | 48 | 775000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Van Buren 161 kV GEN-2023-056 Interconnection (Non-Shared NU) (SWPA) | 158771 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-056 (150MW/Battery/Storage), into Van Buren 161 kV | SWPA | 48 | 4400000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pawnee Switch 138 kV GEN-2023-057 Interconnection (TOIF) (GRDA) | 158772 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-057 (150MW/Battery/Storage), into Pawnee Switch 138 kV | GRDA | 18 | 990399
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pawnee Switch 138 kV GEN-2023-057 Interconnection (Non-Shared NU) (GRDA) | 158773 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-057 (150MW/Battery/Storage), into Pawnee Switch 138 kV | GRDA | 18 | 0
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap Rockhill to South Shreveport 138 kV line GEN-2023-059 Interconnection (TOIF) (AEP) | 158774 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-059 (200MW/Hybrid), into Tap Rockhill to South Shreveport 138 kV line | AEP | 36 | 2125000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap Rockhill to South Shreveport 138 kV line GEN-2023-059 Interconnection (Non-Shared NU) (AEP) | 158775 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-059 (200MW/Hybrid), into Tap Rockhill to South Shreveport 138 kV line | AEP | 36 | 11850000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Catoosa - Owasso 88th 138 kV line GEN-2023-063 Interconnection (TOIF) (AEP) | 158781 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-063 (135MW/Hybrid), into Catoosa - Owasso 88th 138 kV line | AEP | 36 | 2125000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Catoosa - Owasso 88th 138 kV line GEN-2023-063 Interconnection (Non-Shared NU) (AEP) | 158782 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-063 (135MW/Hybrid), into Catoosa - Owasso 88th 138 kV line | AEP | 36 | 11850000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | RS Kerr-Stigler 161 kV line GEN-2023-064 Interconnection (TOIF) (SWPA) | 158783 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-064 (200MW/Hybrid), into RS Kerr-Stigler 161 kV line | SWPA | 48 | 800000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | RS Kerr-Stigler 161 kV line GEN-2023-064 Interconnection (Non-Shared NU) (SWPA) | 158784 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-064 (200MW/Hybrid), into RS Kerr-Stigler 161 kV line | SWPA | 48 | 8600000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tupelo - Atoka 138 kV Line GEN-2023-069 Interconnection (TOIF) (WFEC) | 158792 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-069 (100MW/Hybrid), into Tupelo - Atoka 138 kV Line | WFEC | 60 | 517000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tupelo - Atoka 138 kV Line GEN-2023-069 Interconnection (Non-Shared NU) (WFEC) | 158793 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-069 (100MW/Hybrid), into Tupelo - Atoka 138 kV Line | WFEC | 60 | 6050000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Delaware - Neosho 345 kV GEN-2023-075 Interconnection (TOIF) (Evergy) | 158801 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-075 (200MW/Wind), into Delaware - Neosho 345 kV | Evergy | 56 | 1958090
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Delaware - Neosho 345 kV GEN-2023-076 Interconnection (TOIF) (Evergy) | 158802 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-076 (100MW/Wind), into Delaware - Neosho 345 kV | Evergy | 56 | 112909
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pharaoh 138 kV Substation GEN-2023-088 Interconnection (TOIF) (WFEC) | 158822 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-088 (117MW/Wind), into Pharaoh 138 kV Substation | WFEC | 60 | 517000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pharaoh 138 kV Substation GEN-2023-088 Interconnection (Non-Shared NU) (WFEC) | 158823 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-088 (117MW/Wind), into Pharaoh 138 kV Substation | WFEC | 60 | 1200000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Unger - Frogville 138 kV line GEN-2023-092 Interconnection (TOIF) (WFEC) | 158827 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-092 (125MW/Hybrid), into Unger - Frogville 138 kV line | WFEC | 60 | 517000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Unger - Frogville 138 kV line GEN-2023-092 Interconnection (Non-Shared NU) (WFEC) | 158828 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-092 (125MW/Hybrid), into Unger - Frogville 138 kV line | WFEC | 60 | 6050000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Degrasse 345 kV Substation GEN-2023-100 Interconnection (TOIF) (OGE) | 158839 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-100 (300MW/Hybrid), into Degrasse 345 kV Substation | OKGE | 36 | 2986797
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap Stateline Demarc - Wheeler 230 kV Line GEN-2023-101 Interconnection (TOIF) (SPS) | 158840 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-101 (150MW/Hybrid), into Tap Stateline Demarc - Wheeler 230 kV Line | SPS | TBD (42-month lead time) | 2989552
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Tap Stateline Demarc - Wheeler 230 kV Line GEN-2023-101 Interconnection (Non-Shared NU) (SPS) | 158841 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-101 (150MW/Hybrid), into Tap Stateline Demarc - Wheeler 230 kV Line | SPS | TBD (42-month lead time) | 25538381
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Degrasse 345 kV Substation GEN-2023-102 Interconnection (TOIF) (OGE) | 158842 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-102 (475MW/Hybrid), into Degrasse 345 kV Substation | OKGE | 48 | 2986797
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Mooreland - Noel 138 kV Line GEN-2023-104 Interconnection (TOIF) (WFEC) | 158845 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-104 (100MW/Hybrid), into Mooreland - Noel 138 kV Line | WFEC | 60 | 517000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Mooreland - Noel 138 kV Line GEN-2023-104 Interconnection (Non-Shared NU) (WFEC) | 158846 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-104 (100MW/Hybrid), into Mooreland - Noel 138 kV Line | WFEC | 60 | 6050000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Jonesboro - Independence 161 kV GEN-2023-132 Interconnection (TOIF) (SWPA) | 158874 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-132 (150MW/Solar), into Jonesboro - Independence 161 kV | SWPA | 48 | 800000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Jonesboro - Independence 161 kV GEN-2023-132 Interconnection (Non-Shared NU) (SWPA) | 158875 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-132 (150MW/Solar), into Jonesboro - Independence 161 kV | SWPA | 48 | 8600000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Fixico Tap to Weleetka 138 kV Line GEN-2023-134 Interconnection (TOIF) (AEP) | 158878 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-134 (252MW/Wind), into Fixico Tap to Weleetka 138 kV Line | AEP | 36 | 1925000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Fixico Tap to Weleetka 138 kV Line GEN-2023-134 Interconnection (Non-Shared NU) (AEP) | 158879 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-134 (252MW/Wind), into Fixico Tap to Weleetka 138 kV Line | AEP | 36 | 11850000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lydia 345kV substation GEN-2023-135 Interconnection (TOIF) (AEP) | 158880 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-135 (52MW/Solar), into Lydia 345kV substation | AEP | 18 | 206941
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Lydia 345kV substation GEN-2023-135 Interconnection (Non-Shared NU) (AEP) | 158881 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-135 (52MW/Solar), into Lydia 345kV substation | AEP | 18 | 171180
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | GRDA1 - Tonece7 345 kV Line GEN-2023-138 Interconnection (TOIF) (GRDA) | 158886 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-138 (250MW/Wind), into GRDA1 - Tonece7 345 kV Line | GRDA | 28 | 1809871
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | GRDA1 - Tonece7 345 kV Line GEN-2023-138 Interconnection (Non-Shared NU) (GRDA) | 158887 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-138 (250MW/Wind), into GRDA1 - Tonece7 345 kV Line | GRDA | 28 | 12220783.75
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Gracemont 138 kV Substation GEN-2023-150 Interconnection (TOIF) (OGE) | 158902 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-150 (150MW/Solar), into Gracemont 138 kV Substation | OKGE | 36 | 3163387
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Gracemont 138 kV Substation GEN-2023-150 Interconnection (Non-Shared NU) (OGE) | 158903 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-150 (150MW/Solar), into Gracemont 138 kV Substation | OKGE | 36 | 2762110
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | South N/Ashville - South Murfreesboro 138kV GEN-2023-151 Interconnection (TOIF) (AEP) | 158904 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-151 (100MW/Hybrid), into South N/Ashville - South Murfreesboro 138kV | AEP | 36 | 2125000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | South N/Ashville - South Murfreesboro 138kV GEN-2023-151 Interconnection (Non-Shared NU) (AEP) | 158905 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-151 (100MW/Hybrid), into South N/Ashville - South Murfreesboro 138kV | AEP | 36 | 11850000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Roman Nose 138 kV Substation GEN-2023-161 Interconnection (TOIF) (OGE) | 158922 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-161 (74.9MW/Battery/Storage), into Roman Nose 138 kV Substation | OKGE | 36 | 1764041
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Roman Nose 138 kV Substation GEN-2023-161 Interconnection (Non-Shared NU) (OGE) | 158923 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-161 (74.9MW/Battery/Storage), into Roman Nose 138 kV Substation | OKGE | 36 | 1502516
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Gracemont 345 kV Substation GEN-2023-164 Interconnection (TOIF) (OGE) | 158928 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-164 (210MW/Battery/Storage), into Gracemont 345 kV Substation | OKGE | 48 | 1960313
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Gracemont 345 kV Substation GEN-2023-165 Interconnection (TOIF) (OGE) | 158929 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-165 (210MW/Battery/Storage), into Gracemont 345 kV Substation | OKGE | 48 | 1960313
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | 84th Street - Tennessee Tap 138 kV Line GEN-2023-166 Interconnection (TOIF) (OGE) | 158930 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-166 (150MW/Battery/Storage), into 84th Street - Tennessee Tap 138 kV Line | OKGE | 36 | 3759390
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | 84th Street - Tennessee Tap 138 kV Line GEN-2023-166 Interconnection (Non-Shared NU) (OGE) | 158931 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-166 (150MW/Battery/Storage), into 84th Street - Tennessee Tap 138 kV Line | OKGE | 36 | 7079843
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Washington Park 138 kV Substation GEN-2023-167 Interconnection (TOIF) (OGE) | 158932 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-167 (250MW/Battery/Storage), into Washington Park 138 kV Substation | OKGE | 36 | 1458153
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Washington Park 138 kV Substation GEN-2023-167 Interconnection (Non-Shared NU) (OGE) | 158933 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-167 (250MW/Battery/Storage), into Washington Park 138 kV Substation | OKGE | 36 | 1069049
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Classen 138 kV Substation GEN-2023-168 Interconnection (TOIF) (OGE) | 158934 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-168 (175MW/Battery/Storage), into Classen 138 kV Substation | OKGE | 36 | 2000000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Classen 138 kV Substation GEN-2023-168 Interconnection (Non-Shared NU) (OGE) | 158935 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-168 (175MW/Battery/Storage), into Classen 138 kV Substation | OKGE | 36 | 10000000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Paoli West 138 kV Substation GEN-2023-174 Interconnection (TOIF) (WFEC) | 158944 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-174 (150MW/Battery/Storage), into Paoli West 138 kV Substation | WFEC | 60 | 517000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Paoli West 138 kV Substation GEN-2023-174 Interconnection (Non-Shared NU) (WFEC) | 158945 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-174 (150MW/Battery/Storage), into Paoli West 138 kV Substation | WFEC | 60 | 12500000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Paoli - Seminole 138 kV line tap GEN-2023-177 Interconnection (TOIF) (OGE) | 158949 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-177 (200MW/Solar), into Paoli - Seminole 138 kV line tap | OKGE | 36 | 3759390
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Paoli - Seminole 138 kV line tap GEN-2023-177 Interconnection (Non-Shared NU) (OGE) | 158950 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-177 (200MW/Solar), into Paoli - Seminole 138 kV line tap | OKGE | 36 | 7079843
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Hackett - N Huntington 161 kV Line Tap GEN-2023-180 Interconnection (TOIF) (AEP) | 158953 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-180 (150MW/Solar), into Hackett - N Huntington 161 kV Line Tap | AEP | 36 | 1925000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Hackett - N Huntington 161 kV Line Tap GEN-2023-180 Interconnection (Non-Shared NU) (AEP) | 158954 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-180 (150MW/Solar), into Hackett - N Huntington 161 kV Line Tap | AEP | 36 | 11850000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pirkey - Whitney 138 kV Line GEN-2023-193 Interconnection (TOIF) (AEP) | 158971 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-193 (175MW/Hybrid), into Pirkey - Whitney 138 kV Line | AEP | 36 | 2125000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Pirkey - Whitney 138 kV Line GEN-2023-193 Interconnection (Non-Shared NU) (AEP) | 158972 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-193 (175MW/Hybrid), into Pirkey - Whitney 138 kV Line | AEP | 36 | 11850000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Welsh-Lydia 345kV Line GEN-2023-204 Interconnection (TOIF) (AEP) | 158991 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-204 (953MW/Thermal), into Welsh-Lydia 345kV Line | AEP | 42 | 3275000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Welsh-Lydia 345kV Line GEN-2023-204 Interconnection (Non-Shared NU) (AEP) | 158992 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-204 (953MW/Thermal), into Welsh-Lydia 345kV Line | AEP | 42 | 20000000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | McAlester City - Weleetka 138 kV line GEN-2023-205 Interconnection (TOIF) (AEP) | 158993 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-205 (180MW/Solar), into McAlester City - Weleetka 138 kV line | AEP | 36 | 1925000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | McAlester City - Weleetka 138 kV line GEN-2023-205 Interconnection (Non-Shared NU) (AEP) | 158994 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-205 (180MW/Solar), into McAlester City - Weleetka 138 kV line | AEP | 36 | 11850000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Battlefield BESS 161 kV Substation GEN-2023-206 Interconnection (TOIF) (OGE) | 158995 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-206 (50MW/Battery/Storage), into Battlefield BESS 161 kV Substation | OKGE | 24 | 100000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Battlefield BESS 161 kV Substation GEN-2023-206 Interconnection (Non-Shared NU) (OGE) | 158996 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-206 (50MW/Battery/Storage), into Battlefield BESS 161 kV Substation | OKGE | 24 | 30000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Prague - Chernicky 138 kV Line GEN-2023-210 Interconnection (TOIF) (WFEC) | 159003 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-210 (191MW/Solar), into Prague - Chernicky 138 kV Line | WFEC | 60 | 517000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Prague - Chernicky 138 kV Line GEN-2023-210 Interconnection (Non-Shared NU) (WFEC) | 159004 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-210 (191MW/Solar), into Prague - Chernicky 138 kV Line | WFEC | 60 | 6050000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Ranch Road 345 kV Substation GEN-2023-211 Interconnection (TOIF) (OGE) | 159005 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-211 (250MW/Hybrid), into Ranch Road 345 kV Substation | OKGE | 24 | 100000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Ranch Road 345 kV Substation GEN-2023-211 Interconnection (Non-Shared NU) (OGE) | 159006 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-211 (250MW/Hybrid), into Ranch Road 345 kV Substation | OKGE | 24 | 30000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Northwest TexarkaN/A - Valliant 345 kV Line GEN-2023-212 Interconnection (TOIF) (AEP) | 159007 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-212 (400MW/Hybrid), into Northwest TexarkaN/A - Valliant 345 kV Line | AEP | 42 | 3475000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Northwest TexarkaN/A - Valliant 345 kV Line GEN-2023-212 Interconnection (Non-Shared NU) (AEP) | 159008 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-212 (400MW/Hybrid), into Northwest TexarkaN/A - Valliant 345 kV Line | AEP | 42 | 20000000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Chamber Springs 161 kV Substation GEN-2023-213 Interconnection (TOIF) (AEP) | 159009 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-213 (100MW/Battery/Storage), into Chamber Springs 161 kV Substation | AEP | 30 | 6911274
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Chamber Springs 161 kV Substation GEN-2023-213 Interconnection (Non-Shared NU) (AEP) | 159010 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-213 (100MW/Battery/Storage), into Chamber Springs 161 kV Substation | AEP | 30 | 3160652
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Petty to Chapel 138 kV Line GEN-2023-227 Interconnection (TOIF) (AEP) | 159028 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-227 (200MW/Battery/Storage), into Petty to Chapel 138 kV Line | AEP | 36 | 1925000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Petty to Chapel 138 kV Line GEN-2023-227 Interconnection (Non-Shared NU) (AEP) | 159029 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-227 (200MW/Battery/Storage), into Petty to Chapel 138 kV Line | AEP | 36 | 11850000
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Southwestern Power Station 138 kV Substation (SWS4) GEN-2023-229 Interconnection (TOIF) (AEP) | 159032 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-229 (230MW/Wind), into Southwestern Power Station 138 kV Substation (SWS4) | AEP | 36 | 2164113
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Southwestern Power Station 138 kV Sub (SWS4) GEN-2023-229 Interconnection (Non-Shared NU) (AEP) | 159033 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-229 (230MW/Wind), into Southwestern Power Station 138 kV Substation (SWS4) | AEP | 36 | 3553691
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Red Pointe 138 kV Substation GEN-2023-230 Interconnection (TOIF) (AEP) | 159034 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-230 (150MW/Hybrid), into Red Pointe 138 kV Substation | AEP | 30 | 2575383
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Red Pointe 138 kV Substation GEN-2023-230 Interconnection (Non-Shared NU) (AEP) | 159035 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-230 (150MW/Hybrid), into Red Pointe 138 kV Substation | AEP | 30 | 3338007
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Winnsboro 138 kV Substation GEN-2023-241 Interconnection (TOIF) (AEP) | 159050 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-241 (93MW/Solar), into Winnsboro 138 kV Substation | AEP | 36 | 2327363
Interconnection | DISIS-2023-001 | Steady State | 04 SOUTHEAST | DISIS-2023-001 | ERIS | Winnsboro 138 kV Substation GEN-2023-241 Interconnection (Non-Shared NU) (AEP) | 159051 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-241 (93MW/Solar), into Winnsboro 138 kV Substation | AEP | 36 | 4107515
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Needmore - Yoakum 230 kV Line Interconnection (DISIS-2023-001) (SPS) | 158669 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-158/159 (335/170MW/Solar/Battery/Storage), into Needmore - Yoakum 230 kV Line | SPS | TBD (42-month lead time) | 25538381
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation Interconnection (DISIS-2023-001) (SPS) | 158672 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005/060/142/143/176 (256/256/275/200/300MW/Solar/Wind/Bat), into Plant X 230kV Substation | SPS | TBD (42-month lead time) | 31511051
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Roosevelt - Tolk 230 kV line tap Interconnection (DISIS-2023-001) (SPS) | 158673 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-195 (250/Solar), into Roosevelt - Tolk 230 kV line tap | SPS | TBD (42-month lead time) | 25797424
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | T14 Circuit 115 V Line GEN-2023-001 Interconnection (TOIF) (SPS) | 158679 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-001 (230MW/Solar), into T14 Circuit 115 V Line (sharing the gen-tie with GEN-2018-004) | SPS | 0 | 0
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | T14 Circuit 115 V Line GEN-2023-001 Interconnection (Non-Shared NU) (SPS) | 158680 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-001 (230MW/Solar), into T14 Circuit 115 V Line (sharing the gen-tie with GEN-2018-004) | SPS | 0 | 0
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation GEN-2023-005 Interconnection (TOIF) (SPS) | 158685 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-005 (256MW/Solar), into Plant X 230kV Substation | SPS | TBD (42-month lead time) | 4249032
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco - Carlisle 230 kV line GEN-2023-008 Interconnection (TOIF) (SPS) | 158688 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-008 (75MW/Solar), into Tuco - Carlisle 230 kV line | SPS | TBD (42-month lead time) | 2989552
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco - Carlisle 230 kV line GEN-2023-008 Interconnection (Non-Shared NU) (SPS) | 158689 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-008 (75MW/Solar), into Tuco - Carlisle 230 kV line | SPS | TBD (42-month lead time) | 25538381
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Moore Co 230 kV Substation GEN-2023-010 Interconnection (TOIF) (SPS) | 158692 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-010 (280MW/Wind), into Moore Co 230 kV Substation | SPS | TBD (42-month lead time) | 2429360
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Moore Co 230 kV Substation GEN-2023-010 Interconnection (Non-Shared NU) (SPS) | 158693 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-010 (280MW/Wind), into Moore Co 230 kV Substation | SPS | TBD (42-month lead time) | 4930512
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation GEN-2023-060 Interconnection (TOIF) (SPS) | 158776 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-060 (256MW/Solar), into Plant X 230kV Substation | SPS | TBD (42-month lead time) | 4249032
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-081 Interconnection (TOIF) (NEET) | 158808 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-081 (625MW/Hybrid), into Crossroads - Hobbs 345 kV Line | NEET | 42 | 578564
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-081 Interconnection (Non-Shared NU) (NEET) | 158809 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-081 (625MW/Hybrid), into Crossroads - Hobbs 345 kV Line | NEET | 42 | 41756429
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Potter - Newhart 230 kV line GEN-2023-086 Interconnection (TOIF) (SPS) | 158818 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-086 (300MW/Hybrid), into Potter - Newhart 230 kV line | SPS | TBD (42-month lead time) | 2989552
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Potter - Newhart 230 kV line GEN-2023-086 Interconnection (Non-Shared NU) (SPS) | 158819 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-086 (300MW/Hybrid), into Potter - Newhart 230 kV line | SPS | TBD (42-month lead time) | 25538381
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tap Border to Tuco 345 kV Line GEN-2023-110 Interconnection (TOIF) (SPS) | 158852 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-110 (250MW/Solar), into Tap Border to Tuco 345 kV Line | SPS | TBD (48-month lead time) | 3480128
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tap Border to Tuco 345 kV Line GEN-2023-110 Interconnection (Non-Shared NU) (SPS) | 158853 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-110 (250MW/Solar), into Tap Border to Tuco 345 kV Line | SPS | TBD (48-month lead time) | 47223747
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Kress 115 kV Substation GEN-2023-120 Interconnection (TOIF) (SPS) | 158862 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-120 (130MW/Solar), into Kress 115 kV Substation | SPS | TBD (42-month lead time) | 2840814
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Kress 115 kV Substation GEN-2023-120 Interconnection (Non-Shared NU) (SPS) | 158863 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-120 (130MW/Solar), into Kress 115 kV Substation | SPS | TBD (42-month lead time) | 4967846
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Pringle Interchange 230 kV Substation GEN-2023-123 Interconnection (TOIF) (SPS) | 158868 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-123 (285MW/Wind), into Pringle Interchange 230 kV Substation | SPS | TBD (42-month lead time) | 3656888
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Pringle Interchange 230 kV Substation GEN-2023-123 Interconnection (Non-Shared NU) (SPS) | 158869 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-123 (285MW/Wind), into Pringle Interchange 230 kV Substation | SPS | TBD (42-month lead time) | 7205502
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation GEN-2023-142 Interconnection (TOIF) (SPS) | 158888 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-142 (275MW/Solar), into Plant X 230 kV Substation | SPS | TBD (42-month lead time) | 4249032
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation GEN-2023-143 Interconnection (TOIF) (SPS) | 158889 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-143 (200MW/Battery/Storage), into Plant X 230 kV Substation | SPS | TBD (42-month lead time) | 4249032
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Needmore - Yoakum 230 kV Line GEN-2023-158 Interconnection (TOIF) (SPS) | 158918 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-158 (335MW/Solar), into Needmore - Yoakum 230 kV Line | SPS | TBD (42-month lead time) | 2989552
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Needmore - Yoakum 230 kV Line GEN-2023-159 Interconnection (TOIF) (SPS) | 158919 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-159 (170MW/Battery/Storage), into Needmore - Yoakum 230 kV Line | SPS | TBD (42-month lead time) | 2989552
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Plant X 230 kV Substation GEN-2023-176 Interconnection (TOIF) (SPS) | 158948 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-176 (300MW/Wind), into Plant X 230 kV Substation | SPS | TBD (42-month lead time) | 4249032
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Roosevelt 230kV Substation GEN-2023-178 Interconnection (TOIF) (SPS) | 158951 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-178 (200MW/Solar), into Roosevelt 230kV Substation | SPS |  | 0
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Roosevelt 230kV Substation GEN-2023-178 Interconnection (Non-Shared NU) (SPS) | 158952 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-178 (200MW/Solar), into Roosevelt 230kV Substation | SPS |  | 0
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco 345kV GEN-2023-183 Interconnection (TOIF) (SPS) | 158957 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-183 (217MW/Thermal), into Tuco 345kV | SPS |  | 0
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco 345kV GEN-2023-183 Interconnection (Non-Shared NU) (SPS) | 158958 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-183 (217MW/Thermal), into Tuco 345kV | SPS |  | 0
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Phantom 115 kV Substation GEN-2023-184 Interconnection (TOIF) (SPS) | 158959 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-184 (200MW/Solar), into Phantom 115 kV Substation | SPS | TBD (42-month lead time) | 2683685
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Phantom 115 kV Substation GEN-2023-184 Interconnection (Non-Shared NU) (SPS) | 158960 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-184 (200MW/Solar), into Phantom 115 kV Substation | SPS | TBD (42-month lead time) | 1035860
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Oklaunion - Lawton 345 kV Line GEN-2023-188 Interconnection (TOIF) (AEP) | 158965 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-188 (160MW/Hybrid), into Oklaunion - Lawton 345 kV Line | AEP | 42 | 3475000
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Oklaunion - Lawton 345 kV Line GEN-2023-188 Interconnection (Non-Shared NU) (AEP) | 158966 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-188 (160MW/Hybrid), into Oklaunion - Lawton 345 kV Line | AEP | 42 | 20000000
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Roosevelt - Tolk 230 kV line tap GEN-2023-195 Interconnection (TOIF) (SPS) | 158975 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-195 (250MW/Solar), into Roosevelt - Tolk 230 kV line tap | SPS | TBD (42-month lead time) | 2989552
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-201 Interconnection (TOIF) (NEET) | 158985 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-201 (300MW/Hybrid), into Crossroads - Hobbs 345 kV Line | NEET | 42 | 589025
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crossroads - Hobbs 345 kV Line GEN-2023-201 Interconnection (Non-Shared NU) (NEET) | 158986 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-201 (300MW/Hybrid), into Crossroads - Hobbs 345 kV Line | NEET | 42 | 27334989
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Hobbs - Ink Basin 230 kV Transmission Line GEN-2023-203 Interconnection (TOIF) (SPS) | 158989 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-203 (300MW/Hybrid), into Hobbs - Ink Basin 230 kV Transmission Line | SPS | TBD (42-month lead time) | 2989552
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Hobbs - Ink Basin 230 kV Transmission Line GEN-2023-203 Interconnection (Non-Shared NU) (SPS) | 158990 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-203 (300MW/Hybrid), into Hobbs - Ink Basin 230 kV Transmission Line | SPS | TBD (42-month lead time) | 25538381
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rolling Hills 115 kV GEN-2023-208 Interconnection (TOIF) (SPS) | 158999 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-208 (200MW/Battery/Storage), into Rolling Hills 115 kV | SPS | TBD (42-month lead time) | 2165031
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Rolling Hills 115 kV GEN-2023-208 Interconnection (Non-Shared NU) (SPS) | 159000 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-208 (200MW/Battery/Storage), into Rolling Hills 115 kV | SPS | TBD (42-month lead time) | 1743672
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Amarillo South 115 kV GEN-2023-209 Interconnection (TOIF) (SPS) | 159001 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-209 (125MW/Battery/Storage), into Amarillo South 115 kV | SPS | TBD (42-month lead time) | 2948304
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Amarillo South 115 kV GEN-2023-209 Interconnection (Non-Shared NU) (SPS) | 159002 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-209 (125MW/Battery/Storage), into Amarillo South 115 kV | SPS | TBD (42-month lead time) | 15402434
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco-Okalunion 345 kV line GEN-2023-228 Interconnection (TOIF) (SPS) | 159030 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-228 (250MW/Battery/Storage), into Tuco-Okalunion 345 kV line | SPS |  | 0
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Tuco-Okalunion 345 kV line GEN-2023-228 Interconnection (Non-Shared NU) (SPS) | 159031 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-228 (250MW/Battery/Storage), into Tuco-Okalunion 345 kV line | SPS |  | 0
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Hobbs - Yoakum 345 kV GEN-2023-236 Interconnection (TOIF) (SPS) | 159040 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-236 (400MW/Solar), into Hobbs - Yoakum 345 Kv | SPS | TBD (48-month lead time) | 3480128
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Hobbs - Yoakum 345 kV GEN-2023-236 Interconnection (Non-Shared NU) (SPS) | 159041 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-236 (400MW/Solar), into Hobbs - Yoakum 345 kV | SPS | TBD (48-month lead time) | 42358867
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crawfish Draw 345 kV Substation GEN-2023-237 Interconnection (TOIF) (SPS) | 159042 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-237 (500MW/Wind), into Crawfish Draw 345 kV Substation | SPS | TBD (48-month lead time) | 3433613
Interconnection | DISIS-2023-001 | Steady State | 05 SOUTHWEST | DISIS-2023-001 | ERIS | Crawfish Draw 345 kV Substation GEN-2023-237 Interconnection (Non-Shared NU) (SPS) | 159043 | Interconnection upgrades and cost estimates needed to interconnect GEN-2023-237 (500MW/Wind), into Crawfish Draw 345 kV Substation | SPS | TBD (48-month lead time) | 56159206
24386695758.65

## Contingent Upgrades - Screening
Gen Number | Group | Service Type | NTC ID | Upgrade ID | Project Name | Upgrade Name | Upgrade Description | Study Identified | Inclusion in 27L and 27SP Base Models | Inclusion in NRIS base models | PTDF | Estimated In-Service Date | Total Upgrade Cost | Financial Risk on Total Upgrade Cost
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.04378 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.03618 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.0413 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.0413 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.03109 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.03109 | TBD (36 month lead time) | 428620878 | 428620878
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05554 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.04972 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05447 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.12424 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05447 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.06513 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.11353 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.06341 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05385 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.12471 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05447 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05447 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.04947 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.04947 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.10931 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05447 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05536 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05338 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.0583 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.04545 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.11556 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.11054 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05298 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05514 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.04273 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Beckham to Potter 345 kV Line Ckt 2 | Build New Beckham to Potter 345 kV Line Ckt 2 | Build a second Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.03039 | TBD (36 month lead time) | 428620878 | 428620878
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03014 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03375 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03745 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03745 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-174 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03088 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03027 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.08219 | TBD (36 month lead time) | 44046000 | 44046000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03644 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03804 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.06607 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.0325 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.07503 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.14515 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.25734 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03654 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03556 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03963 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.21383 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03812 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.23631 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.05723 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.06541 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03216 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.03216 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.07852 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.26343 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build New Crawfish Draw to G17-151 TAP 345 kV Line Ckt 2 | Build a new 24.47 miles Crawfish Draw to G17-151 TAP 345 kV Line CKT 2 | DISIS-2020-001 | Yes | Yes | 0.05888 | TBD (36 month lead time) | 44046000 | 44046000
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.03598 | TBD (36 month lead time) | 261000000 | 261000000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.19661 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.17526 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.09072 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.03811 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.09072 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.23234 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.05088 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.03119 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.09072 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.09072 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.11571 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.11571 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.09123 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.11203 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.09776 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.19616 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.1115 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.20821 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.15996 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.06731 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.05927 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.19005 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.05806 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.04632 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.04548 | TBD (36 month lead time) | 261000000 | 261000000
ASGI-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.03721 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.04247 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-081 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.07353 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-086 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.03558 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-201 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.05867 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-203 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.03786 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-209 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.04008 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Crossroads to Potter County 345 kV Line | Build New Crossroads to Potter County 345 kV Line | Build a new Crossroads to Potter County 345 kV line (145 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.04878 | TBD (36 month lead time) | 261000000 | 261000000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New G17-151-Tap to Border 345 kV Line | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.04204 | TBD (36 month lead time) | 335411258 | 335411258
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New G17-151-Tap to Border 345 kV Line | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.06552 | TBD (36 month lead time) | 335411258 | 335411258
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New G17-151-Tap to Border 345 kV Line | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.08675 | TBD (36 month lead time) | 335411258 | 335411258
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New G17-151-Tap to Border 345 kV Line | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.18027 | TBD (36 month lead time) | 335411258 | 335411258
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New G17-151-Tap to Border 345 kV Line | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.08241 | TBD (36 month lead time) | 335411258 | 335411258
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New G17-151-Tap to Border 345 kV Line | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.16573 | TBD (36 month lead time) | 335411258 | 335411258
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build New G17-151-Tap to Border 345 kV Line | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.03756 | TBD (36 month lead time) | 335411258 | 335411258
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New G17-151-Tap to Border 345 kV Line | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.07176 | TBD (36 month lead time) | 335411258 | 335411258
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New G17-151-Tap to Border 345 kV Line | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.0676 | TBD (36 month lead time) | 335411258 | 335411258
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New G17-151-Tap to Border 345 kV Line | Build New G17-151-Tap to Border 345 kV Line | Build a new G17-151-Tap to Border 345 kV line (126 miles) to a minimum rating of 1195 MVA | DISIS-2020-001 | Yes | Yes | 0.06298 | TBD (36 month lead time) | 335411258 | 335411258
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.03061 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.06449 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.04494 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.05034 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.05034 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.051 | TBD (36 month lead time) | 184680000 | 184680000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.06527 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.06113 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.05999 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.04171 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.05999 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.07194 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.09197 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.05588 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.07809 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.05999 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.05999 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.05814 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.05814 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.11994 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.06081 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.08184 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.06515 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.06011 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.06726 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.05816 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.08728 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.08545 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.06365 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.07496 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.14176 | TBD (36 month lead time) | 184680000 | 184680000
ASGI-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build New Hitchland to Potter 345 kV Line Ckt 2 | Build a second Hitchland to Potter 345 kV line (102.6 miles) to a minimum rating of 1037 MVA | DISIS-2020-001 | Yes | Yes | 0.03278 | TBD (36 month lead time) | 184680000 | 184680000
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.08778 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-022 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05074 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-030 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05159 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.04634 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.0563 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05576 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.0534 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.08904 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.03667 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-135 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.07014 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.0416 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-151 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05655 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05278 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05278 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.04023 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.07408 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-193 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.0584 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.06605 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.06972 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-227 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05936 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-229 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.03565 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-230 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05602 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-241 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05933 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.03432 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.03038 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.04772 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05429 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.03719 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.07421 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-035 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.03197 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-038 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.04562 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-069 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.0394 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.07548 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-135 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.04322 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-150 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.03628 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.04651 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.04651 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-177 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.03879 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.09275 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-193 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.03113 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-212 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.04274 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-227 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.03317 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-022 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05002 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05387 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-229 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build New Lawton Eastside to G17-171-TAP 345 kV Second Circuit | Build a new Lawton Eastside to G17-171-TAP 345 kV line (14.4 miles) Ckt 2 | DISIS-2020-001 | Yes | Yes | 0.05179 | TBD (36 month lead time) | 56160000 | 56160000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.04074 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.03201 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.03655 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.03655 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.09617 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.05525 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.03412 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.06126 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.10177 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.1672 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.24497 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.15344 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.03846 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.03269 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.03269 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.09015 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build New Oklaunion to G18-015-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G18-015-TAP 345 kV line (59.065 miles) to a minimum rating of 997.3 MVA | DISIS-2020-001 | Yes | Yes | 0.20277 | TBD (36 month lead time) | 230353500 | 230353500
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | DISIS-2020-001 | Yes | Yes | 0.03276 | TBD (36 month lead time) | 168086100 | 168086100
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | DISIS-2020-001 | Yes | Yes | 0.19842 | TBD (36 month lead time) | 168086100 | 168086100
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | DISIS-2020-001 | Yes | Yes | 0.04269 | TBD (36 month lead time) | 168086100 | 168086100
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | DISIS-2020-001 | Yes | Yes | 0.04724 | TBD (36 month lead time) | 168086100 | 168086100
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | DISIS-2020-001 | Yes | Yes | 0.07773 | TBD (36 month lead time) | 168086100 | 168086100
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | DISIS-2020-001 | Yes | Yes | 0.1273 | TBD (36 month lead time) | 168086100 | 168086100
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | DISIS-2020-001 | Yes | Yes | 0.18529 | TBD (36 month lead time) | 168086100 | 168086100
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | DISIS-2020-001 | Yes | Yes | 0.11655 | TBD (36 month lead time) | 168086100 | 168086100
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | DISIS-2020-001 | Yes | Yes | 0.1931 | TBD (36 month lead time) | 168086100 | 168086100
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build New Oklaunion to G20-009-TAP 345kV Line Ckt 2 | Build a second Oklaunion to G20-009-TAP 345 kV line (43.099 miles) to a minimum rating of 1176 MVA | DISIS-2020-001 | Yes | Yes | 0.15195 | TBD (36 month lead time) | 168086100 | 168086100
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03367 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03542 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03414 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03392 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03405 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-135 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03154 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03871 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.04223 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.04223 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-166 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03187 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-167 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03249 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-168 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03244 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-174 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03572 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03497 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.08152 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-193 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03002 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-205 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03095 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-210 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03194 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03151 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-227 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03016 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-241 | 04 SOUTHEAST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03015 | TBD (36 month lead time) | 18427752 | 18427752
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.04735 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.04986 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03152 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03871 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.08097 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03152 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.04144 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.20468 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.09298 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03152 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03152 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03823 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03823 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.19159 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03371 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.34893 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.0475 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03371 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.04599 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.05228 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.20873 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.04978 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.20104 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.12476 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.10887 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-086 | 05 SOUTHWEST | NRIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.03538 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-209 | 05 SOUTHWEST | NRIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.04565 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.19483 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build the Crawfish Draw 345 kV Substation | Build the Crawfish Draw 345 kV Substation | Tap the existing Tuco to Border 345 kV line and Tuco to Oklaunion 345 kV line (G17-171 Tap) and build a 345 kV substation (Crawfish Draw) | DISIS-2020-001 | Yes | Yes | 0.23075 | TBD (36 month lead time) | 18427752 | 18427752
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.03022 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.03022 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.06696 | TBD (36 month lead time) | 8302968 | 8302968
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.09366 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.09551 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.03407 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.06266 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.03407 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.08293 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.18664 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.07423 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.03407 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.03407 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.05085 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.05085 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.14516 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.04138 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.12911 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.09403 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.03931 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.09193 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.09929 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.0319 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.18571 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 1 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.09993 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.05835 | TBD (36 month lead time) | 8302968 | 8302968
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.08162 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.08324 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.0546 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.07227 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.16265 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.06469 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.04432 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.04432 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.12651 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.03606 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.11252 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.08195 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.03426 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.08011 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.08653 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.16184 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 | Replace the TUCO_INT 7 to TUCO_INT 6 345-230 kV transformer 2 to achieve minimum ratings of 675 MVA | DISIS-2020-001 | Yes | Yes | 0.08708 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.03383 | TBD (36 month lead time) | 35352000 | 35352000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.26965 | TBD (36 month lead time) | 35352000 | 35352000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.08191 | TBD (36 month lead time) | 35352000 | 35352000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.16733 | TBD (36 month lead time) | 35352000 | 35352000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05491 | TBD (36 month lead time) | 35352000 | 35352000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.15381 | TBD (36 month lead time) | 35352000 | 35352000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.0351 | TBD (36 month lead time) | 35352000 | 35352000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.0642 | TBD (36 month lead time) | 35352000 | 35352000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.03932 | TBD (36 month lead time) | 35352000 | 35352000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Border to Beckham 345 kV New Line | Border to Beckham 345 kV New Line | Build a second Border to Beckham 345 kV line (19.64 miles) to a minimum rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05644 | TBD (36 month lead time) | 35352000 | 35352000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Hobbs to Andrews Voltage Conversion | Hobbs to Andrews Voltage Conversion | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | DISIS-2020-001 | Yes | Yes | 0.10301 | TBD (36 month lead time) | 53295780 | 53295780
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Hobbs to Andrews Voltage Conversion | Hobbs to Andrews Voltage Conversion | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | DISIS-2020-001 | Yes | Yes | 0.07535 | TBD (36 month lead time) | 53295780 | 53295780
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Hobbs to Andrews Voltage Conversion | Hobbs to Andrews Voltage Conversion | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | DISIS-2020-001 | Yes | Yes | 0.11642 | TBD (36 month lead time) | 53295780 | 53295780
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Hobbs to Andrews Voltage Conversion | Hobbs to Andrews Voltage Conversion | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | DISIS-2020-001 | Yes | Yes | 0.03183 | TBD (36 month lead time) | 53295780 | 53295780
ASGI-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Hobbs to Andrews Voltage Conversion | Hobbs to Andrews Voltage Conversion | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | DISIS-2020-001 | Yes | Yes | 0.04177 | TBD (36 month lead time) | 53295780 | 53295780
GEN-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Hobbs to Andrews Voltage Conversion | Hobbs to Andrews Voltage Conversion | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | DISIS-2020-001 | Yes | Yes | 0.04659 | TBD (36 month lead time) | 53295780 | 53295780
GEN-2023-081 | 05 SOUTHWEST | NRIS | TBD | TBD | Hobbs to Andrews Voltage Conversion | Hobbs to Andrews Voltage Conversion | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | DISIS-2020-001 | Yes | Yes | 0.03098 | TBD (36 month lead time) | 53295780 | 53295780
GEN-2023-201 | 05 SOUTHWEST | NRIS | TBD | TBD | Hobbs to Andrews Voltage Conversion | Hobbs to Andrews Voltage Conversion | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | DISIS-2020-001 | Yes | Yes | 0.05204 | TBD (36 month lead time) | 53295780 | 53295780
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Hobbs to Andrews Voltage Conversion | Hobbs to Andrews Voltage Conversion | Convert the existing Hobbs to Andrews 230 kV line to 345 kV. Transmission line is built for 345 kV operation. Terminate the Hobbs end at the Hobbs 345 kV substation and replace the Andrews 230/115 kV transformers with a single 345/115 kV transformer. | DISIS-2020-001 | Yes | Yes | 0.06051 | TBD (36 month lead time) | 53295780 | 53295780
GEN-2023-149 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the MARTCIT5 to REDEL 5 161kV line 1 | Rebuild the MARTCIT5 to REDEL 5 161kV line 1 | Rebuild the existing MARTCIT5 to REDEL 5 161 kV line(3.86 miles) to a minimum ratings of 400 MVA | DISIS-2020-001 | Yes | Yes | 0.09694 | TBD (36 month lead time) | 11000000 | 11000000
GEN-2023-149 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the STILWEL5 to REDEL 5 161kV line 1 | Rebuild the STILWEL5 to REDEL 5 161kV line 1 | Rebuild the STILWEL5 to REDEL 5 161 kV line 1 (4.22 miles) to a minimum rating of 400 MVA | DISIS-2020-001 | Yes | Yes | 0.09694 | TBD (36 month lead time) | 13088846 | 13088846
GEN-2023-056 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild BRANCH 5 to GRNDPRT5 161kV line 1 | Rebuild BRANCH 5 to GRNDPRT5 161kV line 1 | Rebuild the BRANCH5 to GRANDPRT5 161kV line CKT1 (3.99 miles) to a minimum rating of 191 MVA | DISIS-2021-001 | Yes | Yes | 0.08316 | TBD (36 month lead time) | 5594111.463 | 5594111.463
GEN-2023-064 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild BRANCH 5 to GRNDPRT5 161kV line 1 | Rebuild BRANCH 5 to GRNDPRT5 161kV line 1 | Rebuild the BRANCH5 to GRANDPRT5 161kV line CKT1 (3.99 miles) to a minimum rating of 191 MVA | DISIS-2021-001 | Yes | Yes | 0.03844 | TBD (36 month lead time) | 5594111.463 | 5594111.463
GEN-2023-056 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild BRANCH 5 to GRNDPRT5 161kV line 1 | Rebuild BRANCH 5 to GRNDPRT5 161kV line 1 | Rebuild the BRANCH5 to GRANDPRT5 161kV line CKT1 (3.99 miles) to a minimum rating of 191 MVA | DISIS-2021-001 | Yes | Yes | 0.09623 | TBD (36 month lead time) | 5594111.463 | 5594111.463
GEN-2023-064 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild BRANCH 5 to GRNDPRT5 161kV line 1 | Rebuild BRANCH 5 to GRNDPRT5 161kV line 1 | Rebuild the BRANCH5 to GRANDPRT5 161kV line CKT1 (3.99 miles) to a minimum rating of 191 MVA | DISIS-2021-001 | Yes | Yes | 0.05125 | TBD (36 month lead time) | 5594111.463 | 5594111.463
GEN-2023-062 | 01 NORTH | ERIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.04519 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.04646 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.03906 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.03906 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.04438 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.04383 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.03911 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.37765 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.37765 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.37765 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-105 | 01 NORTH | NRIS | TBD | TBD | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the RAUN 3 to HOSKINS3 345kV line 1 | Rebuild the existing RAUN 3 to HOSKINS3 345 kV line 1 (65.2 miles) to a minimum rating of 1135 MVA | DISIS-2021-001 | Yes | Yes | 0.0405 | TBD (36 month lead time) | 74617748.8 | 74617748.8
GEN-2023-062 | 01 NORTH | ERIS | TBD | TBD | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line(4.2 miles) to a minimum ratings of 635 MVA | DISIS-2021-001 | Yes | Yes | 0.04139 | TBD (36 month lead time) | 0 | 0
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line(4.2 miles) to a minimum ratings of 635 MVA | DISIS-2021-001 | Yes | Yes | 0.04297 | TBD (36 month lead time) | 0 | 0
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Rebuild the SHEYNNE4 to FARGO 4 230kV line 1 | Rebuild the existing SHEYNNE4 to FARGO 4 230 kV line(4.2 miles) to a minimum ratings of 635 MVA | DISIS-2021-001 | Yes | Yes | 0.0339 | TBD (36 month lead time) | 0 | 0
GEN-2023-166 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the SW5TH4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line CKT1 (3.43 miles) to a minimum rating of 295 MVA | DISIS-2021-001 | Yes | Yes | 0.07921 | TBD (36 month lead time) | 3440000 | 3440000
GEN-2023-167 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the SW5TH4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line CKT1 (3.43 miles) to a minimum rating of 295 MVA | DISIS-2021-001 | Yes | Yes | 0.10353 | TBD (36 month lead time) | 3440000 | 3440000
GEN-2023-168 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the SW5TH4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line CKT1 (3.43 miles) to a minimum rating of 295 MVA | DISIS-2021-001 | Yes | Yes | 0.28769 | TBD (36 month lead time) | 3440000 | 3440000
GEN-2023-167 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the SW5TH4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line CKT1 (3.43 miles) to a minimum rating of 295 MVA | DISIS-2021-001 | Yes | Yes | 0.10071 | TBD (36 month lead time) | 3440000 | 3440000
GEN-2023-168 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the SW5TH4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line 1 | Rebuild the SW5TH4 to CLASSEN4 138 kV line CKT1 (3.43 miles) to a minimum rating of 295 MVA | DISIS-2021-001 | Yes | Yes | 0.2849 | TBD (36 month lead time) | 3440000 | 3440000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | DISIS-2021-001 | Yes | Yes | 0.03053 | TBD (36 month lead time) | 20859647.5 | 20859647.5
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | DISIS-2021-001 | Yes | Yes | 0.03252 | TBD (36 month lead time) | 20859647.5 | 20859647.5
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | DISIS-2021-001 | Yes | Yes | 0.6649 | TBD (36 month lead time) | 20859647.5 | 20859647.5
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | DISIS-2021-001 | Yes | Yes | 0.10483 | TBD (36 month lead time) | 20859647.5 | 20859647.5
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | DISIS-2021-001 | Yes | Yes | 0.10483 | TBD (36 month lead time) | 20859647.5 | 20859647.5
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1 | Rebuild the existing TWIN CH4 to SIOUXCY4 230 kV line 1 (23.61 miles) to a minimum rating of 425 MVA | DISIS-2021-001 | Yes | Yes | 0.10483 | TBD (36 month lead time) | 20859647.5 | 20859647.5
GEN-2023-056 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild VBI 5 to GRANDPRT5 161kV line 1 | Rebuild VBI 5 to GRANDPRT5 161kV line 1 | Rebuild the VBI5 to GRANDPRT5 161kV line CKT1 (24.54 miles) to a minimum rating of 191 MVA | DISIS-2021-001 | Yes | Yes | 0.08316 | TBD (36 month lead time) | 34405888.54 | 34405888.54
GEN-2023-064 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild VBI 5 to GRANDPRT5 161kV line 1 | Rebuild VBI 5 to GRANDPRT5 161kV line 1 | Rebuild the VBI5 to GRANDPRT5 161kV line CKT1 (24.54 miles) to a minimum rating of 191 MVA | DISIS-2021-001 | Yes | Yes | 0.03844 | TBD (36 month lead time) | 34405888.54 | 34405888.54
GEN-2023-056 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild VBI 5 to GRANDPRT5 161kV line 1 | Rebuild VBI 5 to GRANDPRT5 161kV line 1 | Rebuild the VBI5 to GRANDPRT5 161kV line CKT1 (24.54 miles) to a minimum rating of 191 MVA | DISIS-2021-001 | Yes | Yes | 0.09623 | TBD (36 month lead time) | 34405888.54 | 34405888.54
GEN-2023-064 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild VBI 5 to GRANDPRT5 161kV line 1 | Rebuild VBI 5 to GRANDPRT5 161kV line 1 | Rebuild the VBI5 to GRANDPRT5 161kV line CKT1 (24.54 miles) to a minimum rating of 191 MVA | DISIS-2021-001 | Yes | Yes | 0.05125 | TBD (36 month lead time) | 34405888.54 | 34405888.54
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild the WOODWRD4 to WINDFRM4 138kV line CKT1 (12.07 miles) to a minimum rating of 181 MVA | DISIS-2021-001 | Yes | Yes | 0.10522 | TBD (36 month lead time) | 11637399.13 | 11637399.13
GEN-2023-035 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild the WOODWRD4 to WINDFRM4 138kV line CKT1 (12.07 miles) to a minimum rating of 181 MVA | DISIS-2021-001 | Yes | Yes | 0.09738 | TBD (36 month lead time) | 11637399.13 | 11637399.13
GEN-2023-069 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild the WOODWRD4 to WINDFRM4 138kV line CKT1 (12.07 miles) to a minimum rating of 181 MVA | DISIS-2021-001 | Yes | Yes | 0.10462 | TBD (36 month lead time) | 11637399.13 | 11637399.13
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild the WOODWRD4 to WINDFRM4 138kV line CKT1 (12.07 miles) to a minimum rating of 181 MVA | DISIS-2021-001 | Yes | Yes | 0.10517 | TBD (36 month lead time) | 11637399.13 | 11637399.13
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild the WOODWRD4 to WINDFRM4 138kV line CKT1 (12.07 miles) to a minimum rating of 181 MVA | DISIS-2021-001 | Yes | Yes | 0.07605 | TBD (36 month lead time) | 11637399.13 | 11637399.13
GEN-2023-210 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild the WOODWRD4 to WINDFRM4 138kV line CKT1 (12.07 miles) to a minimum rating of 181 MVA | DISIS-2021-001 | Yes | Yes | 0.10297 | TBD (36 month lead time) | 11637399.13 | 11637399.13
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild WOODWRD4 to WINDFRM4 138kV line 1 | Rebuild the WOODWRD4 to WINDFRM4 138kV line CKT1 (12.07 miles) to a minimum rating of 181 MVA | DISIS-2021-001 | Yes | Yes | 0.06652 | TBD (36 month lead time) | 11637399.13 | 11637399.13
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the existing Shell Creek 345/230 kV transformer ckt 1 with a rating of 360 MVA | DISIS-2021-001 | Yes | Yes | 0.04457 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the existing Shell Creek 345/230 kV transformer ckt 1 with a rating of 360 MVA | DISIS-2021-001 | Yes | Yes | 0.03589 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the existing Shell Creek 345/230 kV transformer ckt 1 with a rating of 360 MVA | DISIS-2021-001 | Yes | Yes | 0.03589 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03128 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03357 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03105 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.05627 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03565 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03565 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03824 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03883 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03883 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03883 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-222 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03303 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-223 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03303 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-006 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.10932 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-023 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.05626 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03869 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04831 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-034 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.06958 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04415 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-037 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.05731 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.05653 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03906 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-065 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.05401 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-073 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.07349 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-085 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04155 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.05447 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-099 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.14902 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-149 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.07208 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04531 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-170 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04035 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04822 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04417 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-219 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.23354 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-220 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.27359 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-221 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.27762 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04424 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-027 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03833 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-028 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03991 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-049 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03988 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-055 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03971 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-057 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03199 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-063 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03637 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-075 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04358 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-076 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04358 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-100 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03324 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-102 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03324 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03292 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-138 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03458 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03182 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-211 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.0399 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-213 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03642 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03656 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03443 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-034 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.07982 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-050 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.10363 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03283 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-065 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.05918 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-073 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.27593 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-149 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.04248 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-219 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.17681 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-220 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.21546 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-221 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.21957 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-100 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.08034 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-102 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.08034 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.05836 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03019 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-022 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03101 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.03637 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-211 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new 50MVAR Capacitor Bank at G21-096-TAP 345kV | Build a new switched cap at G21-096-TAP 345 kV with a capacity of 50 MVAR | DISIS-2022-001 | Yes | Yes | 0.14539 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-100 | 04 SOUTHEAST | ERIS | TBD | TBD | Build DGRASSE7 Transformer CKT 2 | Build DGRASSE7 Transformer CKT 2 | Duplicate DGRASSE7 345kV Transformer | DISIS-2022-001 | Yes | Yes | 0.04603 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-100 | 04 SOUTHEAST | ERIS | TBD | TBD | Build DGRASSE7 Transformer CKT 2 | Build DGRASSE7 Transformer CKT 2 | Duplicate DGRASSE7 345kV Transformer | DISIS-2022-001 | Yes | Yes | 0.04603 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-102 | 04 SOUTHEAST | ERIS | TBD | TBD | Build DGRASSE7 Transformer CKT 2 | Build DGRASSE7 Transformer CKT 2 | Duplicate DGRASSE7 345kV Transformer | DISIS-2022-001 | Yes | Yes | 0.04603 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-102 | 04 SOUTHEAST | ERIS | TBD | TBD | Build DGRASSE7 Transformer CKT 2 | Build DGRASSE7 Transformer CKT 2 | Duplicate DGRASSE7 345kV Transformer | DISIS-2022-001 | Yes | Yes | 0.04603 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Build DGRASSE7 Transformer CKT 2 | Build DGRASSE7 Transformer CKT 2 | Duplicate DGRASSE7 345kV Transformer | DISIS-2022-001 | Yes | Yes | 0.37581 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Build DGRASSE7 Transformer CKT 2 | Build DGRASSE7 Transformer CKT 2 | Duplicate DGRASSE7 345kV Transformer | DISIS-2022-001 | Yes | Yes | 0.37581 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-100 | 04 SOUTHEAST | NRIS | TBD | TBD | Build DGRASSE7 Transformer CKT 2 | Build DGRASSE7 Transformer CKT 2 | Duplicate DGRASSE7 345kV Transformer | DISIS-2022-001 | Yes | Yes | 0.05075 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-102 | 04 SOUTHEAST | NRIS | TBD | TBD | Build DGRASSE7 Transformer CKT 2 | Build DGRASSE7 Transformer CKT 2 | Duplicate DGRASSE7 345kV Transformer | DISIS-2022-001 | Yes | Yes | 0.05075 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Build DGRASSE7 Transformer CKT 2 | Build DGRASSE7 Transformer CKT 2 | Duplicate DGRASSE7 345kV Transformer | DISIS-2022-001 | Yes | Yes | 0.34647 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-062 | 01 NORTH | ERIS | TBD | TBD | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07705 | TBD (36 month lead time) | 250000000 | 250000000
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07288 | TBD (36 month lead time) | 250000000 | 250000000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.4231 | TBD (36 month lead time) | 250000000 | 250000000
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05428 | TBD (36 month lead time) | 250000000 | 250000000
GEN-2023-097 | 01 NORTH | NRIS | TBD | TBD | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04466 | TBD (36 month lead time) | 250000000 | 250000000
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03862 | TBD (36 month lead time) | 250000000 | 250000000
GEN-2023-012 | 01 NORTH | NRIS | TBD | TBD | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04012 | TBD (36 month lead time) | 250000000 | 250000000
GEN-2023-105 | 01 NORTH | NRIS | TBD | TBD | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build new FTTHOM1-LNX3 to CHAPELLE-BE3 345kV Line 1 | Build a new FTTHOM1-LNX3 to CHAPELLE-BE3 345 kV line 1 (21.97 miles) to a standard rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.38951 | TBD (36 month lead time) | 250000000 | 250000000
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03812 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03277 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03277 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03741 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03181 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03103 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0305 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-100 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04178 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.11316 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-102 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04178 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03689 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05219 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.08113 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.08113 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-174 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03723 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03431 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05287 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03056 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-229 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04365 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06099 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03593 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07564 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06386 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05925 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0535 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04304 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04049 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04971 | TBD (36 month lead time) | 88218000 | 88218000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05589 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05589 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.1479 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04615 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07812 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.12137 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07326 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.03016 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.03016 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.0388 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.09128 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.13482 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.22677 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.22677 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-166 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.04543 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-167 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.04238 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-168 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.04448 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.14599 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-229 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.13647 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.03928 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.06348 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.04106 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.06941 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.08533 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.1103 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.08357 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.10417 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.05499 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-022 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04147 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-030 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03021 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03401 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03344 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.0364 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03743 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.05643 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-135 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04291 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03442 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-151 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03371 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.14117 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.14117 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.0301 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.17622 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-193 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03488 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04344 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04264 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-227 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03554 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-230 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03324 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-241 | 04 SOUTHEAST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03552 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.0366 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.07737 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03865 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.03015 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.0308 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.03616 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.32988 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.04413 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.03141 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.04865 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.0787 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.12814 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.18429 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.11681 | TBD (36 month lead time) | 184860000 | 184860000
GEN-2023-219 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1 | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1 | Rebuild the existing EAST ST3 to WEMPORI3 115 kV line 1 (5.1 miles) to a minimum rating of 120 MVA | DISIS-2022-001 | Yes | Yes | 0.08209 | TBD (36 month lead time) | 3625284 | 3625284
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.03542 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.0936 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.16188 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.03313 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-027 | 04 SOUTHEAST | ERIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.05911 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-028 | 04 SOUTHEAST | ERIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.13352 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-049 | 04 SOUTHEAST | ERIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.16081 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-055 | 04 SOUTHEAST | ERIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.06935 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-063 | 04 SOUTHEAST | ERIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.03884 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04175 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0444 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0418 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05906 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05268 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05268 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05454 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04833 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04401 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0496 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0496 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0496 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-006 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04299 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04197 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-023 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0638 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0572 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.06055 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-034 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.19122 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05916 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-037 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.06403 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.03528 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-065 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.13884 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-073 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.09436 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05657 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-099 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.08641 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04768 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-149 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.06377 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0591 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-170 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04421 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.06087 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04514 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04514 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-219 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.08909 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-220 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.08875 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-221 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.08909 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.03962 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04916 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.03757 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-057 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04558 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0347 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0456 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-161 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04764 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04506 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04506 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-166 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05642 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-167 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05434 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-168 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05524 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-174 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04567 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04409 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05264 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-205 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.03178 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-210 | 04 SOUTHEAST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04373 | TBD (36 month lead time) | 13035217.16 | 13035217.16
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04946 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05031 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04969 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.06169 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04969 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04819 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.03825 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04552 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04932 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04969 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04969 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05056 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05056 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04976 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04948 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04999 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04908 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.0509 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.03536 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.03665 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.05388 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04977 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-151 | 04 SOUTHEAST | ERIS | TBD | TBD | ANDRSNC4 to RIFFIN REC4 138kV Line Rebuild | ANDRSNC4 to RIFFIN REC4 138kV Line Rebuild | Rebuild the existing ANDRSNC4 to RIFFIN REC4 138 kV line 1 (8.4 miles) to a minimum rating of 215 MVA | DISIS-2022-001 | Yes | Yes | 0.04718 | TBD (36 month lead time) | 19320000 | 19320000
GEN-2023-151 | 04 SOUTHEAST | NRIS | TBD | TBD | ANDRSNC4 to RIFFIN REC4 138kV Line Rebuild | ANDRSNC4 to RIFFIN REC4 138kV Line Rebuild | Rebuild the existing ANDRSNC4 to RIFFIN REC4 138 kV line 1 (8.4 miles) to a minimum rating of 215 MVA | DISIS-2022-001 | Yes | Yes | 0.05345 | TBD (36 month lead time) | 19320000 | 19320000
GEN-2023-212 | 04 SOUTHEAST | NRIS | TBD | TBD | ANDRSNC4 to RIFFIN REC4 138kV Line Rebuild | ANDRSNC4 to RIFFIN REC4 138kV Line Rebuild | Rebuild the existing ANDRSNC4 to RIFFIN REC4 138 kV line 1 (8.4 miles) to a minimum rating of 215 MVA | DISIS-2022-001 | Yes | Yes | 0.03258 | TBD (36 month lead time) | 19320000 | 19320000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Clinton City Terminal Upgrade | Clinton City Terminal Upgrade | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1198 MVA | DISIS-2022-001 | Yes | Yes | 0.04142 | TBD (36 month lead time) | 566485 | 566485
GEN-2023-038 | 04 SOUTHEAST | NRIS | TBD | TBD | Clinton City Terminal Upgrade | Clinton City Terminal Upgrade | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1198 MVA | DISIS-2022-001 | Yes | Yes | 0.04256 | TBD (36 month lead time) | 566485 | 566485
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Clinton City Terminal Upgrade | Clinton City Terminal Upgrade | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1198 MVA | DISIS-2022-001 | Yes | Yes | 0.04279 | TBD (36 month lead time) | 566485 | 566485
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Clinton City Terminal Upgrade | Clinton City Terminal Upgrade | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1198 MVA | DISIS-2022-001 | Yes | Yes | 0.12387 | TBD (36 month lead time) | 566485 | 566485
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Clinton City Terminal Upgrade | Clinton City Terminal Upgrade | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1198 MVA | DISIS-2022-001 | Yes | Yes | 0.12387 | TBD (36 month lead time) | 566485 | 566485
GEN-2023-177 | 04 SOUTHEAST | NRIS | TBD | TBD | Clinton City Terminal Upgrade | Clinton City Terminal Upgrade | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1198 MVA | DISIS-2022-001 | Yes | Yes | 0.03917 | TBD (36 month lead time) | 566485 | 566485
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Clinton City Terminal Upgrade | Clinton City Terminal Upgrade | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1198 MVA | DISIS-2022-001 | Yes | Yes | 0.15463 | TBD (36 month lead time) | 566485 | 566485
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Clinton City Terminal Upgrade | Clinton City Terminal Upgrade | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1198 MVA | DISIS-2022-001 | Yes | Yes | 0.08685 | TBD (36 month lead time) | 566485 | 566485
GEN-2023-022 | 04 SOUTHEAST | NRIS | TBD | TBD | Clinton City Terminal Upgrade | Clinton City Terminal Upgrade | Rebuild 6.9 miles of 345 kV from Lawton Eastside to G20-075-TAP to a minimum of 1198 MVA | DISIS-2022-001 | Yes | Yes | 0.03882 | TBD (36 month lead time) | 566485 | 566485
GEN-2023-075 | 04 SOUTHEAST | ERIS | TBD | TBD | DELWARE4 to G18-079-TAP 138kV Line Rebuild | DELWARE4 to G18-079-TAP 138kV Line Rebuild | Rebuild 12.23 miles DELWARE4 to G18-079-TAP 138kV line ckt 1 to a minimum of 340 MVA | DISIS-2022-001 | Yes | Yes | 0.03391 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-076 | 04 SOUTHEAST | ERIS | TBD | TBD | DELWARE4 to G18-079-TAP 138kV Line Rebuild | DELWARE4 to G18-079-TAP 138kV Line Rebuild | Rebuild 12.23 miles DELWARE4 to G18-079-TAP 138kV line ckt 1 to a minimum of 340 MVA | DISIS-2022-001 | Yes | Yes | 0.03391 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-028 | 04 SOUTHEAST | NRIS | TBD | TBD | DELWARE4 to G18-079-TAP 138kV Line Rebuild | DELWARE4 to G18-079-TAP 138kV Line Rebuild | Rebuild 12.23 miles DELWARE4 to G18-079-TAP 138kV line ckt 1 to a minimum of 340 MVA | DISIS-2022-001 | Yes | Yes | 0.05718 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-049 | 04 SOUTHEAST | NRIS | TBD | TBD | DELWARE4 to G18-079-TAP 138kV Line Rebuild | DELWARE4 to G18-079-TAP 138kV Line Rebuild | Rebuild 12.23 miles DELWARE4 to G18-079-TAP 138kV line ckt 1 to a minimum of 340 MVA | DISIS-2022-001 | Yes | Yes | 0.05704 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-055 | 04 SOUTHEAST | NRIS | TBD | TBD | DELWARE4 to G18-079-TAP 138kV Line Rebuild | DELWARE4 to G18-079-TAP 138kV Line Rebuild | Rebuild 12.23 miles DELWARE4 to G18-079-TAP 138kV line ckt 1 to a minimum of 340 MVA | DISIS-2022-001 | Yes | Yes | 0.05761 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-057 | 04 SOUTHEAST | NRIS | TBD | TBD | DELWARE4 to G18-079-TAP 138kV Line Rebuild | DELWARE4 to G18-079-TAP 138kV Line Rebuild | Rebuild 12.23 miles DELWARE4 to G18-079-TAP 138kV line ckt 1 to a minimum of 340 MVA | DISIS-2022-001 | Yes | Yes | 0.05323 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-035 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0318 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-100 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04406 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03773 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-102 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04406 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0348 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-150 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04544 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07668 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07668 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04027 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Gracemont to G16-037-Tap 345 kV New Line | Gracemont to G16-037-Tap 345 kV New Line | Build a new Gracemont to G16-037-Tap 345 kV line (49.01 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06979 | TBD (36 month lead time) | 28129000 | 28129000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05129 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05129 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.14653 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Gracemont to G22-114-Tap 345 kV New Line | Gracemont to G22-114-Tap 345 kV New Line | Build a new Gracemont to G22-114-Tap 345 kV line (78 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.10851 | TBD (36 month lead time) | 140400000 | 140400000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.03572 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-038 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.04164 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-069 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.0313 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-100 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.0354 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-102 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.0354 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.04249 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-150 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.15889 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.24847 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.24847 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-177 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.03317 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.14245 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-210 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.06573 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.05312 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.10688 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-134 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.04618 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-229 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Minco 345 kV New Line | Gracemont to Minco 345 kV New Line | Build a new Gracemont to Minco 345 kV line (20.67 miles) to a minimum rating of 1775 MVA | DISIS-2022-001 | Yes | Yes | 0.08646 | TBD (36 month lead time) | 37206000 | 37206000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03638 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04371 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-038 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03738 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-038 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04491 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03758 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04515 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.0314 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.10879 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.13071 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.10879 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.13071 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-177 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.0344 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-177 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04134 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.13581 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.16318 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.07628 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.09165 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-022 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03517 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-022 | 04 SOUTHEAST | NRIS | TBD | TBD | Gracemont to Treasure Island 345 kV New Line | Gracemont to Treasure Island 345 kV New Line | Build a new Gracemont to Treasure Island 345 kV line (9.69 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04225 | TBD (36 month lead time) | 17442000 | 17442000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.33659 | TBD (36 month lead time) | 99540000 | 99540000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Lawton Eastside to G20-009-TAP 345kV New Line | Lawton Eastside to G20-009-TAP 345kV New Line | Build a second Lawton Eastside to G20-009 TAP 345 kV line (23.7 miles) | DISIS-2022-001 | Yes | Yes | 0.14852 | TBD (36 month lead time) | 99540000 | 99540000
GEN-2023-227 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild JEFFRSN4 to WILKES 4 138kV line 1 | Rebuild JEFFRSN4 to WILKES 4 138kV line 1 | Rebuild the JEFFRSN4 to WILKES4 138kV line CKT1 (11.11 miles) to a minimum rating of 258 MVA | DISIS-2022-001 | Yes | Yes | 0.10266 | TBD (36 month lead time) | 25530000 | 25530000
GEN-2023-227 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the LSSOUTH4 to DIANA 4 138kV Line 1 | Rebuild the LSSOUTH4 to DIANA 4 138kV Line 1 | Rebuild the existing LSSOUTH4 to DIANA 4 138 kV line 1 (12.63 miles) to a minimum rating of 324 MVA | DISIS-2022-001 | Yes | Yes | 0.20121 | TBD (36 month lead time) | 29049000 | 29049000
GEN-2023-241 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the LSSOUTH4 to DIANA 4 138kV Line 1 | Rebuild the LSSOUTH4 to DIANA 4 138kV Line 1 | Rebuild the existing LSSOUTH4 to DIANA 4 138 kV line 1 (12.63 miles) to a minimum rating of 324 MVA | DISIS-2022-001 | Yes | Yes | 0.15642 | TBD (36 month lead time) | 29049000 | 29049000
GEN-2023-227 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the LSSOUTH4 to DIANA 4 138kV Line 1 | Rebuild the LSSOUTH4 to DIANA 4 138kV Line 1 | Rebuild the existing LSSOUTH4 to DIANA 4 138 kV line 1 (12.63 miles) to a minimum rating of 324 MVA | DISIS-2022-001 | Yes | Yes | 0.21025 | TBD (36 month lead time) | 29049000 | 29049000
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the NEO SPA5 to TIP292 5 161kV Line 1 (EMDE) | Rebuild the NEO SPA5 to TIP292 5 161kV Line 1 (EMDE) | Rebuild the existing NEO SPA5 to TIP292 5 161 kV line 1 (10.6 miles) to a minimum rating of 270/315 MVA | DISIS-2022-001 | Yes | Yes | 0.09498 | TBD (36 month lead time) | 10369174.4 | 10369174.4
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the PHILL 5 to HSNVL 5 161kV Line 1 | Rebuild the PHILL 5 to HSNVL 5 161kV Line 1 | Rebuild the existing PHILL 5 to HSNVL 5 161 kV line 1 (12.47 miles) to a minimum rating of 350 MVA | DISIS-2022-001 | Yes | Yes | 0.31131 | TBD (36 month lead time) | 21000000 | 21000000
GEN-2023-032 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the PHILL 5 to HSNVL 5 161kV Line 1 | Rebuild the PHILL 5 to HSNVL 5 161kV Line 1 | Rebuild the existing PHILL 5 to HSNVL 5 161 kV line 1 (12.47 miles) to a minimum rating of 350 MVA | DISIS-2022-001 | Yes | Yes | 0.10487 | TBD (36 month lead time) | 21000000 | 21000000
GEN-2023-033 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the PHILL 5 to HSNVL 5 161kV Line 1 | Rebuild the PHILL 5 to HSNVL 5 161kV Line 1 | Rebuild the existing PHILL 5 to HSNVL 5 161 kV line 1 (12.47 miles) to a minimum rating of 350 MVA | DISIS-2022-001 | Yes | Yes | 0.11747 | TBD (36 month lead time) | 21000000 | 21000000
GEN-2023-149 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the PHILL 5 to HSNVL 5 161kV Line 1 | Rebuild the PHILL 5 to HSNVL 5 161kV Line 1 | Rebuild the existing PHILL 5 to HSNVL 5 161 kV line 1 (12.47 miles) to a minimum rating of 350 MVA | DISIS-2022-001 | Yes | Yes | 0.13466 | TBD (36 month lead time) | 21000000 | 21000000
GEN-2023-169 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the PHILL 5 to HSNVL 5 161kV Line 1 | Rebuild the PHILL 5 to HSNVL 5 161kV Line 1 | Rebuild the existing PHILL 5 to HSNVL 5 161 kV line 1 (12.47 miles) to a minimum rating of 350 MVA | DISIS-2022-001 | Yes | Yes | 0.11908 | TBD (36 month lead time) | 21000000 | 21000000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.10058 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.10567 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.10567 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.08063 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-172 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.09021 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-173 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.09021 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 1 (23.69 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.04653 | TBD (36 month lead time) | 92391000 | 92391000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 1 (23.69 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.04286 | TBD (36 month lead time) | 92391000 | 92391000
GEN-2023-135 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 1 (23.69 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.08067 | TBD (36 month lead time) | 92391000 | 92391000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 1 (23.69 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.09942 | TBD (36 month lead time) | 92391000 | 92391000
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 1 (23.69 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.06289 | TBD (36 month lead time) | 92391000 | 92391000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 1 (23.69 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.03035 | TBD (36 month lead time) | 92391000 | 92391000
GEN-2023-135 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 1 (23.69 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.11459 | TBD (36 month lead time) | 92391000 | 92391000
GEN-2023-151 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 1 (23.69 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.04187 | TBD (36 month lead time) | 92391000 | 92391000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 1 (23.69 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.0315 | TBD (36 month lead time) | 92391000 | 92391000
GEN-2023-212 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the WELSH 7 to DIANA 7 345kV Line 1 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 1 (23.69 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.09568 | TBD (36 month lead time) | 92391000 | 92391000
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 2 (23.6 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.0467 | TBD (36 month lead time) | 92040000 | 92040000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 2 (23.6 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.04303 | TBD (36 month lead time) | 92040000 | 92040000
GEN-2023-135 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 2 (23.6 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.08098 | TBD (36 month lead time) | 92040000 | 92040000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 2 (23.6 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.0998 | TBD (36 month lead time) | 92040000 | 92040000
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 2 (23.6 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.06313 | TBD (36 month lead time) | 92040000 | 92040000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 2 (23.6 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.03046 | TBD (36 month lead time) | 92040000 | 92040000
GEN-2023-135 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 2 (23.6 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.11503 | TBD (36 month lead time) | 92040000 | 92040000
GEN-2023-151 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 2 (23.6 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.04203 | TBD (36 month lead time) | 92040000 | 92040000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 2 (23.6 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.03162 | TBD (36 month lead time) | 92040000 | 92040000
GEN-2023-212 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the WELSH 7 to DIANA 7 345kV Line 2 | Rebuild the existing WELSH 7 to DIANA 7 345 kV line 2 (23.6 miles) to a minimum rating of 1195 MVA | DISIS-2022-001 | Yes | Yes | 0.09605 | TBD (36 month lead time) | 92040000 | 92040000
GEN-2023-050 | 03 CENTRAL | NRIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.06884 | TBD (36 month lead time) | 23884546.28 | 23884546.28
GEN-2023-057 | 04 SOUTHEAST | NRIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04793 | TBD (36 month lead time) | 23884546.28 | 23884546.28
GEN-2023-064 | 04 SOUTHEAST | NRIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.03253 | TBD (36 month lead time) | 23884546.28 | 23884546.28
GEN-2023-075 | 04 SOUTHEAST | NRIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.12537 | TBD (36 month lead time) | 23884546.28 | 23884546.28
GEN-2023-076 | 04 SOUTHEAST | NRIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.12537 | TBD (36 month lead time) | 23884546.28 | 23884546.28
GEN-2023-027 | 04 SOUTHEAST | NRIS | TBD | TBD | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | DISIS-2022-001 | Yes | Yes | 0.03577 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-063 | 04 SOUTHEAST | NRIS | TBD | TBD | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | DISIS-2022-001 | Yes | Yes | 0.03514 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-180 | 04 SOUTHEAST | NRIS | TBD | TBD | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | DISIS-2022-001 | Yes | Yes | 0.04048 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | DISIS-2022-001 | Yes | Yes | 0.03196 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-205 | 04 SOUTHEAST | NRIS | TBD | TBD | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | DISIS-2022-001 | Yes | Yes | 0.03275 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-213 | 04 SOUTHEAST | NRIS | TBD | TBD | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the LONGWD 4 to LONGWD 7 345kV Transformer 1 | Replace the existing LONGWD 4 to LONGWD 7 345-138 kV transformer 1 with a rating of 595 MVA | DISIS-2022-001 | Yes | Yes | 0.036 | TBD (36 month lead time) | 8302968 | 8302968
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.09651 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-194 | 03 CENTRAL | NRIS | TBD | TBD | RIV4525 to BAX488 5 161kV Line Rebuild | RIV4525 to BAX488 5 161kV Line Rebuild | Rebuild 5.19 miles RIV4525 to BAX488 5 161kV line ckt 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.03365 | TBD (36 month lead time) | 5076982.56 | 5076982.56
GEN-2023-050 | 03 CENTRAL | NRIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.06884 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-057 | 04 SOUTHEAST | NRIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.04793 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-064 | 04 SOUTHEAST | NRIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.03253 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-075 | 04 SOUTHEAST | NRIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.12537 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-076 | 04 SOUTHEAST | NRIS | TBD | TBD | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | VIOLA 7 to G18-128-TAP 345kV Line Rebuild | Rebuild 11.39 miles VIOLA 7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1572 MVA | DISIS-2022-001 | Yes | Yes | 0.12537 | TBD (36 month lead time) | 13035217.16 | 13035217.16
GEN-2023-219 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1 | Rebuild the EAST ST3 to WEMPORI3 115kV Line 1 | Rebuild the existing EAST ST3 to WEMPORI3 115 kV line 1 (5.1 miles) to a minimum rating of 120 MVA | DISIS-2022-001 | Yes | Yes | 0.08102 | TBD (48 month lead time) | 35000000 | 35000000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | 122546 | Crossroads - Tolk 345 kV Ckt 1 Rebuild | Crossroads - Tolk 345 kV Ckt 1 Rebuild | Replace approximately four structures on the Crossroads - Tolk 345 kV line to achieve a minimum rating of 956 MVA. Network Upgrade shared among four requests: GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.05579 | 2020-12-01 | 184651 | 184651
GEN-2023-005 | 05 SOUTHWEST | NRIS | TBD | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.09327 | 2020-12-15 | 968567 | 968567
GEN-2023-060 | 05 SOUTHWEST | NRIS | TBD | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.09327 | 2020-12-15 | 968567 | 968567
GEN-2023-142 | 05 SOUTHWEST | NRIS | TBD | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.09327 | 2020-12-15 | 968567 | 968567
GEN-2023-143 | 05 SOUTHWEST | NRIS | TBD | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.09327 | 2020-12-15 | 968567 | 968567
GEN-2023-158 | 05 SOUTHWEST | NRIS | TBD | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.1116 | 2020-12-15 | 968567 | 968567
GEN-2023-159 | 05 SOUTHWEST | NRIS | TBD | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.1116 | 2020-12-15 | 968567 | 968567
GEN-2023-178 | 05 SOUTHWEST | NRIS | TBD | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.10782 | 2020-12-15 | 968567 | 968567
GEN-2023-195 | 05 SOUTHWEST | NRIS | TBD | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.11678 | 2020-12-15 | 968567 | 968567
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | 122646 | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 478 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.07629 | 2020-12-15 | 968567 | 968567
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210556 | 112187 | Henessey 138 kV Ckt 1 Terminal Upgrades | Henessey 138 kV Ckt 1 Terminal Upgrades | Rebuild Hennessey - Bull Foot Tap 138kV to rating 268/287 MVA | DISIS-2016-002 | Yes | Yes | 0.03027 | 2020-12-31 | 142965 | 142965
GEN-2023-161 | 04 SOUTHEAST | NRIS | 210556 | 112187 | Henessey 138 kV Ckt 1 Terminal Upgrades | Henessey 138 kV Ckt 1 Terminal Upgrades | Rebuild Hennessey - Bull Foot Tap 138kV to rating 268/287 MVA | DISIS-2016-002 | Yes | Yes | 0.03113 | 2020-12-31 | 142965 | 142965
GEN-2023-005 | 05 SOUTHWEST | NRIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild | Newhart - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.13556 | 2020-12-31 | 697513 | 697513
GEN-2023-060 | 05 SOUTHWEST | NRIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild | Newhart - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.13556 | 2020-12-31 | 697513 | 697513
GEN-2023-142 | 05 SOUTHWEST | NRIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild | Newhart - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.13556 | 2020-12-31 | 697513 | 697513
GEN-2023-143 | 05 SOUTHWEST | NRIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild | Newhart - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.13556 | 2020-12-31 | 697513 | 697513
GEN-2023-158 | 05 SOUTHWEST | NRIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild | Newhart - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.0791 | 2020-12-31 | 697513 | 697513
GEN-2023-159 | 05 SOUTHWEST | NRIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild | Newhart - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.0791 | 2020-12-31 | 697513 | 697513
GEN-2023-178 | 05 SOUTHWEST | NRIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild | Newhart - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.07159 | 2020-12-31 | 697513 | 697513
GEN-2023-195 | 05 SOUTHWEST | NRIS | TBD | 122641 | Newhart - Plant X 230 kV Ckt 1 Rebuild | Newhart - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum emergency rating of 456 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.07889 | 2020-12-31 | 697513 | 697513
GEN-2023-086 | 05 SOUTHWEST | NRIS | TBD | 122647 | Tuco 230 kV Capacitive Reactive Power Support | Tuco 230 kV Capacitive Reactive Power Support | Build 100 MVAR at Tuco 230 kV Substation. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.08632 | 2020-12-31 | 5943138 | 5943138
GEN-2023-209 | 05 SOUTHWEST | NRIS | TBD | 122647 | Tuco 230 kV Capacitive Reactive Power Support | Tuco 230 kV Capacitive Reactive Power Support | Build 100 MVAR at Tuco 230 kV Substation. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.07951 | 2020-12-31 | 5943138 | 5943138
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | 122647 | Tuco 230 kV Capacitive Reactive Power Support | Tuco 230 kV Capacitive Reactive Power Support | Build 100 MVAR at Tuco 230 kV Substation. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.05067 | 2020-12-31 | 5943138 | 5943138
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | 122647 | Tuco 230 kV Capacitive Reactive Power Support | Tuco 230 kV Capacitive Reactive Power Support | Build 100 MVAR at Tuco 230 kV Substation. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.05784 | 2020-12-31 | 5943138 | 5943138
GEN-2023-209 | 05 SOUTHWEST | NRIS | TBD | 122648 | Deafsmith 115 kV Capacitive Reactive Power Support | Deafsmith 115 kV Capacitive Reactive Power Support | Build 100 MVAR at Deaf Smith 115 kV substation. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.04221 | 2021-10-28 | 3318135 | 3318135
GEN-2023-178 | 05 SOUTHWEST | NRIS | TBD | 122645 | Curry - Deafsmith 115 kV Ckt 1 Rebuild | Curry - Deafsmith 115 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 90/90 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.05593 | 2021-12-15 | 4852215 | 4852215
GEN-2023-195 | 05 SOUTHWEST | NRIS | TBD | 122645 | Curry - Deafsmith 115 kV Ckt 1 Rebuild | Curry - Deafsmith 115 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 90/90 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.03244 | 2021-12-15 | 4852215 | 4852215
GEN-2023-005 | 05 SOUTHWEST | NRIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.11391 | 2021-12-17 | 4578401 | 4578401
GEN-2023-060 | 05 SOUTHWEST | NRIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.11391 | 2021-12-17 | 4578401 | 4578401
GEN-2023-142 | 05 SOUTHWEST | NRIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.11391 | 2021-12-17 | 4578401 | 4578401
GEN-2023-143 | 05 SOUTHWEST | NRIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.11391 | 2021-12-17 | 4578401 | 4578401
GEN-2023-158 | 05 SOUTHWEST | NRIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.07336 | 2021-12-17 | 4578401 | 4578401
GEN-2023-159 | 05 SOUTHWEST | NRIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.07336 | 2021-12-17 | 4578401 | 4578401
GEN-2023-178 | 05 SOUTHWEST | NRIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.04769 | 2021-12-17 | 4578401 | 4578401
GEN-2023-195 | 05 SOUTHWEST | NRIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.06278 | 2021-12-17 | 4578401 | 4578401
GEN-2023-203 | 05 SOUTHWEST | NRIS | TBD | 122640 | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Deaf Smith - Plant X 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum system emergency rating of 430 MVA. Network Upgrade shared among four requests: GEN-2016-121, GEN-2016-123, GEN-2016-124, and GEN-2016-125 | DISIS-2016-002 | Yes | Yes | 0.03077 | 2021-12-17 | 4578401 | 4578401
GEN-2023-009 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04692 | 2025-01-23 | 16516041 | 0
GEN-2023-022 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.07636 | 2025-01-23 | 16516041 | 0
GEN-2023-030 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03167 | 2025-01-23 | 16516041 | 0
GEN-2023-038 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05617 | 2025-01-23 | 16516041 | 0
GEN-2023-059 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03419 | 2025-01-23 | 16516041 | 0
GEN-2023-059 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04214 | 2025-01-23 | 16516041 | 0
GEN-2023-069 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04999 | 2025-01-23 | 16516041 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04995 | 2025-01-23 | 16516041 | 0
GEN-2023-092 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04712 | 2025-01-23 | 16516041 | 0
GEN-2023-100 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0326 | 2025-01-23 | 16516041 | 0
GEN-2023-101 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03479 | 2025-01-23 | 16516041 | 0
GEN-2023-102 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0326 | 2025-01-23 | 16516041 | 0
GEN-2023-104 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03219 | 2025-01-23 | 16516041 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06542 | 2025-01-23 | 16516041 | 0
GEN-2023-135 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04155 | 2025-01-23 | 16516041 | 0
GEN-2023-151 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0349 | 2025-01-23 | 16516041 | 0
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03884 | 2025-01-23 | 16516041 | 0
GEN-2023-164 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04544 | 2025-01-23 | 16516041 | 0
GEN-2023-165 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04544 | 2025-01-23 | 16516041 | 0
GEN-2023-177 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0685 | 2025-01-23 | 16516041 | 0
GEN-2023-193 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03532 | 2025-01-23 | 16516041 | 0
GEN-2023-204 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04763 | 2025-01-23 | 16516041 | 0
GEN-2023-205 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03741 | 2025-01-23 | 16516041 | 0
GEN-2023-212 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0414 | 2025-01-23 | 16516041 | 0
GEN-2023-227 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03588 | 2025-01-23 | 16516041 | 0
GEN-2023-230 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03407 | 2025-01-23 | 16516041 | 0
GEN-2023-241 | 04 SOUTHEAST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03585 | 2025-01-23 | 16516041 | 0
ASGI-2023-001 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05793 | 2025-01-23 | 16516041 | 0
GEN-2023-001 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05842 | 2025-01-23 | 16516041 | 0
GEN-2023-005 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05897 | 2025-01-23 | 16516041 | 0
GEN-2023-008 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06774 | 2025-01-23 | 16516041 | 0
GEN-2023-060 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05897 | 2025-01-23 | 16516041 | 0
GEN-2023-081 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05733 | 2025-01-23 | 16516041 | 0
GEN-2023-086 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05193 | 2025-01-23 | 16516041 | 0
GEN-2023-110 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04961 | 2025-01-23 | 16516041 | 0
GEN-2023-120 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05912 | 2025-01-23 | 16516041 | 0
GEN-2023-142 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05897 | 2025-01-23 | 16516041 | 0
GEN-2023-143 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05897 | 2025-01-23 | 16516041 | 0
GEN-2023-158 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05926 | 2025-01-23 | 16516041 | 0
GEN-2023-159 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05926 | 2025-01-23 | 16516041 | 0
GEN-2023-178 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05891 | 2025-01-23 | 16516041 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05794 | 2025-01-23 | 16516041 | 0
GEN-2023-195 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05909 | 2025-01-23 | 16516041 | 0
GEN-2023-201 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05773 | 2025-01-23 | 16516041 | 0
GEN-2023-203 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05871 | 2025-01-23 | 16516041 | 0
GEN-2023-208 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04962 | 2025-01-23 | 16516041 | 0
GEN-2023-209 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05051 | 2025-01-23 | 16516041 | 0
GEN-2023-228 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03469 | 2025-01-23 | 16516041 | 0
GEN-2023-236 | 05 SOUTHWEST | ERIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05802 | 2025-01-23 | 16516041 | 0
GEN-2023-009 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03841 | 2025-01-23 | 16516041 | 0
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0558 | 2025-01-23 | 16516041 | 0
GEN-2023-069 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03971 | 2025-01-23 | 16516041 | 0
GEN-2023-092 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03856 | 2025-01-23 | 16516041 | 0
GEN-2023-177 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0654 | 2025-01-23 | 16516041 | 0
GEN-2023-022 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.07374 | 2025-01-23 | 16516041 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05653 | 2025-01-23 | 16516041 | 0
GEN-2023-134 | 04 SOUTHEAST | NRIS | 210670 | 133106 | Multi - Minco - Pleasant Valley - Draper 345 kV | Draper - Pleasant Valley 345 kV Ckt 2 | Build a second 13.2-mile 345 kV line from Draper 345 kV substation to Pleasant Valley 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04098 | 2025-01-23 | 16516041 | 0
GEN-2023-178 | 05 SOUTHWEST | ERIS | 210574 | 143167 | Line - Cargill - Friona 115 kV | Cargill - Friona 115 kV Ckt 1 Rebuild | Rebuild 1.15 miles of existing 115 kV line from Cargill to Friona and upgrade any necessary terminal equipment to achieve a summer emergency rating of 240 MVA | 2020 ITP | Yes | Yes | 0.06338 | 2025-02-18 | 1217890 | 0
GEN-2023-195 | 05 SOUTHWEST | ERIS | 210574 | 143167 | Line - Cargill - Friona 115 kV | Cargill - Friona 115 kV Ckt 1 Rebuild | Rebuild 1.15 miles of existing 115 kV line from Cargill to Friona and upgrade any necessary terminal equipment to achieve a summer emergency rating of 240 MVA | 2020 ITP | Yes | Yes | 0.04029 | 2025-02-18 | 1217890 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 210574 | 143167 | Line - Cargill - Friona 115 kV | Cargill - Friona 115 kV Ckt 1 Rebuild | Rebuild 1.15 miles of existing 115 kV line from Cargill to Friona and upgrade any necessary terminal equipment to achieve a summer emergency rating of 240 MVA | 2020 ITP | Yes | Yes | 0.05593 | 2025-02-18 | 1217890 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 210574 | 143167 | Line - Cargill - Friona 115 kV | Cargill - Friona 115 kV Ckt 1 Rebuild | Rebuild 1.15 miles of existing 115 kV line from Cargill to Friona and upgrade any necessary terminal equipment to achieve a summer emergency rating of 240 MVA | 2020 ITP | Yes | Yes | 0.03244 | 2025-02-18 | 1217890 | 0
GEN-2023-012 | 01 NORTH | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04503 | 2025-04-02 | 28123307 | 0
GEN-2023-062 | 01 NORTH | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.0304 | 2025-04-02 | 28123307 | 0
GEN-2023-082 | 01 NORTH | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04164 | 2025-04-02 | 28123307 | 0
GEN-2023-097 | 01 NORTH | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04014 | 2025-04-02 | 28123307 | 0
GEN-2023-105 | 01 NORTH | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04518 | 2025-04-02 | 28123307 | 0
GEN-2023-154 | 01 NORTH | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04171 | 2025-04-02 | 28123307 | 0
GEN-2023-182 | 01 NORTH | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04422 | 2025-04-02 | 28123307 | 0
GEN-2023-011 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05707 | 2025-04-02 | 28123307 | 0
GEN-2023-077 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04829 | 2025-04-02 | 28123307 | 0
GEN-2023-078 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04829 | 2025-04-02 | 28123307 | 0
GEN-2023-079 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04829 | 2025-04-02 | 28123307 | 0
GEN-2023-116 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03758 | 2025-04-02 | 28123307 | 0
GEN-2023-117 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03758 | 2025-04-02 | 28123307 | 0
GEN-2023-133 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04116 | 2025-04-02 | 28123307 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03156 | 2025-04-02 | 28123307 | 0
GEN-2023-199 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04836 | 2025-04-02 | 28123307 | 0
GEN-2023-216 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.0542 | 2025-04-02 | 28123307 | 0
GEN-2023-217 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.0542 | 2025-04-02 | 28123307 | 0
GEN-2023-218 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.0542 | 2025-04-02 | 28123307 | 0
GEN-2023-222 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04453 | 2025-04-02 | 28123307 | 0
GEN-2023-223 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04453 | 2025-04-02 | 28123307 | 0
GEN-2023-224 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04498 | 2025-04-02 | 28123307 | 0
GEN-2023-225 | 02 NEBRASKA | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04498 | 2025-04-02 | 28123307 | 0
GEN-2023-006 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03504 | 2025-04-02 | 28123307 | 0
GEN-2023-023 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.13707 | 2025-04-02 | 28123307 | 0
GEN-2023-032 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.0441 | 2025-04-02 | 28123307 | 0
GEN-2023-033 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.07993 | 2025-04-02 | 28123307 | 0
GEN-2023-036 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.06169 | 2025-04-02 | 28123307 | 0
GEN-2023-037 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.14285 | 2025-04-02 | 28123307 | 0
GEN-2023-050 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04713 | 2025-04-02 | 28123307 | 0
GEN-2023-073 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03415 | 2025-04-02 | 28123307 | 0
GEN-2023-099 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04276 | 2025-04-02 | 28123307 | 0
GEN-2023-149 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.11758 | 2025-04-02 | 28123307 | 0
GEN-2023-169 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.06942 | 2025-04-02 | 28123307 | 0
GEN-2023-170 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03333 | 2025-04-02 | 28123307 | 0
GEN-2023-171 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.07815 | 2025-04-02 | 28123307 | 0
GEN-2023-194 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03425 | 2025-04-02 | 28123307 | 0
GEN-2023-220 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05614 | 2025-04-02 | 28123307 | 0
GEN-2023-221 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05505 | 2025-04-02 | 28123307 | 0
GEN-2023-231 | 03 CENTRAL | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05271 | 2025-04-02 | 28123307 | 0
GEN-2023-183 | 05 SOUTHWEST | ERIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03023 | 2025-04-02 | 28123307 | 0
GEN-2023-033 | 03 CENTRAL | NRIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.06561 | 2025-04-02 | 28123307 | 0
GEN-2023-034 | 03 CENTRAL | NRIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.04323 | 2025-04-02 | 28123307 | 0
GEN-2023-050 | 03 CENTRAL | NRIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.06244 | 2025-04-02 | 28123307 | 0
GEN-2023-061 | 03 CENTRAL | NRIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03285 | 2025-04-02 | 28123307 | 0
GEN-2023-065 | 03 CENTRAL | NRIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.03654 | 2025-04-02 | 28123307 | 0
GEN-2023-073 | 03 CENTRAL | NRIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.05039 | 2025-04-02 | 28123307 | 0
GEN-2023-149 | 03 CENTRAL | NRIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.12583 | 2025-04-02 | 28123307 | 0
GEN-2023-169 | 03 CENTRAL | NRIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.0543 | 2025-04-02 | 28123307 | 0
GEN-2023-220 | 03 CENTRAL | NRIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.07391 | 2025-04-02 | 28123307 | 0
GEN-2023-221 | 03 CENTRAL | NRIS | 220791 | 158641 | Multi - Atlantic- Craig - West Gardener 345/115 kV | Atlantic Substation 345 kV | Build a new 345 kV substation at the new intersection of West Gardner-Craig and Atlantic -Eudora Township. | 2023 ITP | Yes | Yes | 0.07277 | 2025-04-02 | 28123307 | 0
GEN-2023-101 | 04 SOUTHEAST | ERIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.04204 | 2025-04-20 | 3996000 | 3996000
GEN-2023-110 | 05 SOUTHWEST | ERIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.06552 | 2025-04-20 | 3996000 | 3996000
GEN-2023-176 | 05 SOUTHWEST | ERIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.08675 | 2025-04-20 | 3996000 | 3996000
GEN-2023-183 | 05 SOUTHWEST | ERIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1-345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.18027 | 2025-04-20 | 3996000 | 3996000
GEN-2023-228 | 05 SOUTHWEST | ERIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.08241 | 2025-04-20 | 3996000 | 3996000
GEN-2023-237 | 05 SOUTHWEST | ERIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.16573 | 2025-04-20 | 3996000 | 3996000
GEN-2023-015 | 03 CENTRAL | NRIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.0351 | 2025-04-20 | 3996000 | 3996000
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.0642 | 2025-04-20 | 3996000 | 3996000
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.03932 | 2025-04-20 | 3996000 | 3996000
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220790 | 122537 | Device - Border 345kV Capacitive Reactive Support | Border 345kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker, and associated switches, relaying, and control equipment at Border substation | DISIS-2016-002 | Yes | Yes | 0.05644 | 2025-04-20 | 3996000 | 3996000
GEN-2023-153 | 02 NEBRASKA | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03143 | 2025-04-20 | 6000000 | 6000000
GEN-2023-015 | 03 CENTRAL | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.08071 | 2025-04-20 | 6000000 | 6000000
GEN-2023-107 | 03 CENTRAL | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.0608 | 2025-04-20 | 6000000 | 6000000
GEN-2023-172 | 03 CENTRAL | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.06807 | 2025-04-20 | 6000000 | 6000000
GEN-2023-173 | 03 CENTRAL | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.06807 | 2025-04-20 | 6000000 | 6000000
GEN-2023-009 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.05527 | 2025-04-20 | 6000000 | 6000000
GEN-2023-022 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.05394 | 2025-04-20 | 6000000 | 6000000
GEN-2023-030 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03413 | 2025-04-20 | 6000000 | 6000000
GEN-2023-035 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.09112 | 2025-04-20 | 6000000 | 6000000
GEN-2023-038 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.06215 | 2025-04-20 | 6000000 | 6000000
GEN-2023-059 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03699 | 2025-04-20 | 6000000 | 6000000
GEN-2023-069 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.06033 | 2025-04-20 | 6000000 | 6000000
GEN-2023-088 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.04736 | 2025-04-20 | 6000000 | 6000000
GEN-2023-092 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.05745 | 2025-04-20 | 6000000 | 6000000
GEN-2023-100 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.10192 | 2025-04-20 | 6000000 | 6000000
GEN-2023-101 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.38346 | 2025-04-20 | 6000000 | 6000000
GEN-2023-102 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.10192 | 2025-04-20 | 6000000 | 6000000
GEN-2023-104 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.0858 | 2025-04-20 | 6000000 | 6000000
GEN-2023-134 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.0533 | 2025-04-20 | 6000000 | 6000000
GEN-2023-135 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.04531 | 2025-04-20 | 6000000 | 6000000
GEN-2023-150 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.12838 | 2025-04-20 | 6000000 | 6000000
GEN-2023-151 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03805 | 2025-04-20 | 6000000 | 6000000
GEN-2023-161 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.04328 | 2025-04-20 | 6000000 | 6000000
GEN-2023-164 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.14916 | 2025-04-20 | 6000000 | 6000000
GEN-2023-165 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.14916 | 2025-04-20 | 6000000 | 6000000
GEN-2023-166 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.05138 | 2025-04-20 | 6000000 | 6000000
GEN-2023-167 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.05547 | 2025-04-20 | 6000000 | 6000000
GEN-2023-168 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.05572 | 2025-04-20 | 6000000 | 6000000
GEN-2023-174 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.08301 | 2025-04-20 | 6000000 | 6000000
GEN-2023-177 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.06649 | 2025-04-20 | 6000000 | 6000000
GEN-2023-188 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.09529 | 2025-04-20 | 6000000 | 6000000
GEN-2023-193 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03827 | 2025-04-20 | 6000000 | 6000000
GEN-2023-204 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1-345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.05968 | 2025-04-20 | 6000000 | 6000000
GEN-2023-205 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.04431 | 2025-04-20 | 6000000 | 6000000
GEN-2023-210 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.05213 | 2025-04-20 | 6000000 | 6000000
GEN-2023-212 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.04518 | 2025-04-20 | 6000000 | 6000000
GEN-2023-227 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03892 | 2025-04-20 | 6000000 | 6000000
GEN-2023-229 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.13033 | 2025-04-20 | 6000000 | 6000000
GEN-2023-230 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03685 | 2025-04-20 | 6000000 | 6000000
GEN-2023-241 | 04 SOUTHEAST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03888 | 2025-04-20 | 6000000 | 6000000
GEN-2023-010 | 05 SOUTHWEST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.07893 | 2025-04-20 | 6000000 | 6000000
GEN-2023-110 | 05 SOUTHWEST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.21742 | 2025-04-20 | 6000000 | 6000000
GEN-2023-123 | 05 SOUTHWEST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.05831 | 2025-04-20 | 6000000 | 6000000
GEN-2023-176 | 05 SOUTHWEST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.1021 | 2025-04-20 | 6000000 | 6000000
GEN-2023-183 | 05 SOUTHWEST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1-345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.11917 | 2025-04-20 | 6000000 | 6000000
GEN-2023-237 | 05 SOUTHWEST | ERIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.11724 | 2025-04-20 | 6000000 | 6000000
GEN-2023-015 | 03 CENTRAL | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.0714 | 2025-04-20 | 6000000 | 6000000
GEN-2023-038 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03225 | 2025-04-20 | 6000000 | 6000000
GEN-2023-100 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.1048 | 2025-04-20 | 6000000 | 6000000
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.33453 | 2025-04-20 | 6000000 | 6000000
GEN-2023-102 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.1048 | 2025-04-20 | 6000000 | 6000000
GEN-2023-104 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.14062 | 2025-04-20 | 6000000 | 6000000
GEN-2023-150 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.10463 | 2025-04-20 | 6000000 | 6000000
GEN-2023-164 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.12352 | 2025-04-20 | 6000000 | 6000000
GEN-2023-165 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.12352 | 2025-04-20 | 6000000 | 6000000
GEN-2023-177 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03372 | 2025-04-20 | 6000000 | 6000000
GEN-2023-188 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.06025 | 2025-04-20 | 6000000 | 6000000
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.04122 | 2025-04-20 | 6000000 | 6000000
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03932 | 2025-04-20 | 6000000 | 6000000
GEN-2023-022 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.04075 | 2025-04-20 | 6000000 | 6000000
GEN-2023-088 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.08312 | 2025-04-20 | 6000000 | 6000000
GEN-2023-134 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.04515 | 2025-04-20 | 6000000 | 6000000
GEN-2023-229 | 04 SOUTHEAST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.03328 | 2025-04-20 | 6000000 | 6000000
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220790 | 170374 | Beckham 345 kV Capacitive Reactive Support | Beckham 345 kV Capacitive Reactive Support | Install 1-345 kV 39 Mvar Capacitor Bank, 1- 345 kV Capacitor Breaker and associated switches relaying, and control equipment at Beckham substation. | DISIS-2016-002 | Yes | Yes | 0.06023 | 2025-04-20 | 6000000 | 6000000
GEN-2023-101 | 04 SOUTHEAST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.03383 | 2025-04-30 | 23820158 | 0
GEN-2023-110 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.26965 | 2025-04-30 | 23820158 | 0
GEN-2023-176 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.08191 | 2025-04-30 | 23820158 | 0
GEN-2023-183 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.16733 | 2025-04-30 | 23820158 | 0
GEN-2023-228 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.05491 | 2025-04-30 | 23820158 | 0
GEN-2023-237 | 05 SOUTHWEST | ERIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.15381 | 2025-04-30 | 23820158 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.0351 | 2025-04-30 | 23820158 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.0642 | 2025-04-30 | 23820158 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.03932 | 2025-04-30 | 23820158 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 210628 | 122823 | Multi - Border - Woodward 345 kV Tap | Border - Woodward Tap 345 kV Substation | Tap the existing Border to Woodward 345 kV line 19 miles from the Border station and build a new 345 kV substation or switching station | 2020 ITP | Yes | Yes | 0.05644 | 2025-04-30 | 23820158 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 220758 | 157382 | Sub - Anadarko 138 kV - Southwestern 138 kV | Anadarko 138 kV Terminal Upgrade Ckt 1 | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation | 2023 ITP | Yes | Yes | 0.08198 | 2025-05-30 | 24000 | 0
GEN-2023-150 | 04 SOUTHEAST | ERIS | 220758 | 157382 | Sub - Anadarko 138 kV - Southwestern 138 kV | Anadarko 138 kV Terminal Upgrade Ckt 1 | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation | 2023 ITP | Yes | Yes | 0.03202 | 2025-05-30 | 24000 | 0
GEN-2023-229 | 04 SOUTHEAST | ERIS | 220758 | 157382 | Sub - Anadarko 138 kV - Southwestern 138 kV | Anadarko 138 kV Terminal Upgrade Ckt 1 | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation | 2023 ITP | Yes | Yes | 0.23478 | 2025-05-30 | 24000 | 0
GEN-2023-035 | 04 SOUTHEAST | NRIS | 220758 | 157382 | Sub - Anadarko 138 kV - Southwestern 138 kV | Anadarko 138 kV Terminal Upgrade Ckt 1 | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation | 2023 ITP | Yes | Yes | 0.09517 | 2025-05-30 | 24000 | 0
GEN-2023-150 | 04 SOUTHEAST | NRIS | 220758 | 157382 | Sub - Anadarko 138 kV - Southwestern 138 kV | Anadarko 138 kV Terminal Upgrade Ckt 1 | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation | 2023 ITP | Yes | Yes | 0.03053 | 2025-05-30 | 24000 | 0
GEN-2023-229 | 04 SOUTHEAST | NRIS | 220758 | 157382 | Sub - Anadarko 138 kV - Southwestern 138 kV | Anadarko 138 kV Terminal Upgrade Ckt 1 | Upgrade terminal equipment at Anadarko 138 kV substation for the line to Southwestern 138 kV substation | 2023 ITP | Yes | Yes | 0.20556 | 2025-05-30 | 24000 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 210681 | 156410 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Roadrunner 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.07408 | 2025-05-30 | 12100819 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 210681 | 156410 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Roadrunner 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.03032 | 2025-05-30 | 12100819 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 210681 | 156410 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Roadrunner 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.05907 | 2025-05-30 | 12100819 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 210681 | 156410 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Roadrunner 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.07158 | 2025-05-30 | 12100819 | 0
ASGI-2023-001 | 05 SOUTHWEST | ERIS | 210681 | 156410 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Roadrunner 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.16403 | 2025-05-30 | 12100819 | 0
GEN-2023-001 | 05 SOUTHWEST | ERIS | 210681 | 156410 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Roadrunner 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.03599 | 2025-05-30 | 12100819 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 210681 | 156410 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Roadrunner 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.18143 | 2025-05-30 | 12100819 | 0
GEN-2023-236 | 05 SOUTHWEST | ERIS | 210681 | 156410 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Roadrunner 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Roadrunner 345 kV to support a new double-circuit line from Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.03197 | 2025-05-30 | 12100819 | 0
ASGI-2023-001 | 05 SOUTHWEST | ERIS | 210681 | 156409 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #2 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV | 2021 ITP | Yes | Yes | 0.16403 | 2025-05-30 | 15760331 | 0
GEN-2023-001 | 05 SOUTHWEST | ERIS | 210681 | 156409 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #2 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV | 2021 ITP | Yes | Yes | 0.03599 | 2025-05-30 | 15760331 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 210681 | 156409 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #2 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV | 2021 ITP | Yes | Yes | 0.18143 | 2025-05-30 | 15760331 | 0
GEN-2023-236 | 05 SOUTHWEST | ERIS | 210681 | 156409 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #2 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV | 2021 ITP | Yes | Yes | 0.03197 | 2025-05-30 | 15760331 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 210681 | 156409 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #2 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV | 2021 ITP | Yes | Yes | 0.07408 | 2025-05-30 | 15760331 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 210681 | 156409 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #2 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV | 2021 ITP | Yes | Yes | 0.03032 | 2025-05-30 | 15760331 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 210681 | 156409 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #2 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV | 2021 ITP | Yes | Yes | 0.05907 | 2025-05-30 | 15760331 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 210681 | 156409 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #2 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Roadrunner 345 kV | 2021 ITP | Yes | Yes | 0.07158 | 2025-05-30 | 15760331 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 210681 | 156407 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.03462 | 2025-05-30 | 18722925 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 210681 | 156407 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.08713 | 2025-05-30 | 18722925 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 210681 | 156407 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.28152 | 2025-05-30 | 18722925 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 210681 | 156407 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.18555 | 2025-05-30 | 18722925 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 210681 | 156407 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.07962 | 2025-05-30 | 18722925 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 210681 | 156407 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads 345 kV ckts 1 & 2 Terminal Equipment | Install any necessary terminal equipment at Crossroads 345 kV to support a new double-circuit line to Hobbs 345 kV | 2021 ITP | Yes | Yes | 0.12772 | 2025-05-30 | 18722925 | 0
ASGI-2023-001 | 05 SOUTHWEST | ERIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.13167 | 2025-05-30 | 21266504 | 0
GEN-2023-001 | 05 SOUTHWEST | ERIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.12262 | 2025-05-30 | 21266504 | 0
GEN-2023-081 | 05 SOUTHWEST | ERIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.22543 | 2025-05-30 | 21266504 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.13535 | 2025-05-30 | 21266504 | 0
GEN-2023-201 | 05 SOUTHWEST | ERIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.29547 | 2025-05-30 | 21266504 | 0
GEN-2023-203 | 05 SOUTHWEST | ERIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.10941 | 2025-05-30 | 21266504 | 0
GEN-2023-236 | 05 SOUTHWEST | ERIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.16031 | 2025-05-30 | 21266504 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.03462 | 2025-05-30 | 21266504 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.08713 | 2025-05-30 | 21266504 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.21848 | 2025-05-30 | 21266504 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.31445 | 2025-05-30 | 21266504 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.07962 | 2025-05-30 | 21266504 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 210681 | 156408 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs 345 kV ckts 1 & 2 Terminal Equipment #1 | Install any necessary terminal equipment at Hobbs 345 kV to support a new double-circuit line from Crossroads 345 kV | 2021 ITP | Yes | Yes | 0.12772 | 2025-05-30 | 21266504 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210483 | 72019 | Multi - Park Community - Sunshine 138 kV | Calumet - Concho 138 kV Ckt 1 Voltage Conversion | Convert 9.0 mile 69 kV line from Calumet - Concho to 138 kV. Complete necessary terminal upgrades at Concho. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03423 | 2025-07-30 | 2150000 | 2150000
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210483 | 72018 | Multi - Park Community - Sunshine 138 kV | Calumet - Watonga SW 138 kV Ckt 1 Voltage Conversion | Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03114 | 2025-07-30 | 8400000 | 8400000
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210483 | 72018 | Multi - Park Community - Sunshine 138 kV | Calumet - Watonga SW 138 kV Ckt 1 Voltage Conversion | Convert 16.8 mile 69 kV line from Calumet - Watonga SW to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03683 | 2025-07-30 | 8400000 | 8400000
GEN-2023-097 | 01 NORTH | ERIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.0502 | 2025-09-01 | 66041 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.03119 | 2025-09-01 | 66041 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 210648 | 143613 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Sully Buttes - Whitlock 230 kV Line Clearance Increase | Increase ground clearance of the Sully Buttes to Whitlock 230 kV line. | 2021 ITP | Yes | Yes | 0.03875 | 2025-09-01 | 66041 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.0502 | 2025-09-01 | 323364 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.03119 | 2025-09-01 | 323364 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 210648 | 143614 | Line - Oahe - Sully Buttes - Whitlock - Glenham 230 kV | Whitlock - Glenham 230 kV Clearance Increase | Increase ground clearance of the Whitlock - Glenham 230 kV. | 2021 ITP | Yes | Yes | 0.03875 | 2025-09-01 | 323364 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220828 | 169979 | Multi - Madison, SD Area 115 kV System Voltage Conversion | Lake County 115/69 kV Transformer Ckt 1 (69 kV) | Install new 115/69 transformer at Lake County 69 kV substation | 2024 ITP | Yes | Yes | 0.03375 | 2025-09-14 | 3344000 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210483 | 72021 | Multi - Park Community - Sunshine 138 kV | Calumet 138 kV Substation | New Calumet 138 kV substation with 4-terminal ring bus. | DPA-2017-August-767-774-776 | Yes | Yes | 0.06538 | 2025-09-30 | 6580002 | 6580002
GEN-2023-150 | 04 SOUTHEAST | ERIS | 210483 | 72021 | Multi - Park Community - Sunshine 138 kV | Calumet 138 kV Substation | New Calumet 138 kV substation with 4-terminal ring bus. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03178 | 2025-09-30 | 6580002 | 6580002
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210483 | 72021 | Multi - Park Community - Sunshine 138 kV | Calumet 138 kV Substation | New Calumet 138 kV substation with 4-terminal ring bus. | DPA-2017-August-767-774-776 | Yes | Yes | 0.04769 | 2025-09-30 | 6580002 | 6580002
GEN-2023-229 | 04 SOUTHEAST | ERIS | 210483 | 72021 | Multi - Park Community - Sunshine 138 kV | Calumet 138 kV Substation | New Calumet 138 kV substation with 4-terminal ring bus. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03219 | 2025-09-30 | 6580002 | 6580002
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210483 | 72021 | Multi - Park Community - Sunshine 138 kV | Calumet 138 kV Substation | New Calumet 138 kV substation with 4-terminal ring bus. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03683 | 2025-09-30 | 6580002 | 6580002
GEN-2023-006 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04757 | 2025-10-01 | 3909824 | 0
GEN-2023-034 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04134 | 2025-10-01 | 3909824 | 0
GEN-2023-061 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03968 | 2025-10-01 | 3909824 | 0
GEN-2023-065 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03266 | 2025-10-01 | 3909824 | 0
GEN-2023-073 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04154 | 2025-10-01 | 3909824 | 0
GEN-2023-085 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05812 | 2025-10-01 | 3909824 | 0
GEN-2023-194 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03876 | 2025-10-01 | 3909824 | 0
GEN-2023-231 | 03 CENTRAL | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05038 | 2025-10-01 | 3909824 | 0
GEN-2022-130 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0498 | 2025-10-01 | 3909824 | 0
GEN-2023-022 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06074 | 2025-10-01 | 3909824 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07002 | 2025-10-01 | 3909824 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06622 | 2025-10-01 | 3909824 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06496 | 2025-10-01 | 3909824 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06878 | 2025-10-01 | 3909824 | 0
GEN-2023-056 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05126 | 2025-10-01 | 3909824 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.08843 | 2025-10-01 | 3909824 | 0
GEN-2023-064 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05223 | 2025-10-01 | 3909824 | 0
GEN-2023-075 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07147 | 2025-10-01 | 3909824 | 0
GEN-2023-076 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07147 | 2025-10-01 | 3909824 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07311 | 2025-10-01 | 3909824 | 0
GEN-2023-100 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03272 | 2025-10-01 | 3909824 | 0
GEN-2023-102 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03272 | 2025-10-01 | 3909824 | 0
GEN-2023-104 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0358 | 2025-10-01 | 3909824 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0594 | 2025-10-01 | 3909824 | 0
GEN-2023-138 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.09248 | 2025-10-01 | 3909824 | 0
GEN-2023-180 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04909 | 2025-10-01 | 3909824 | 0
GEN-2023-205 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04619 | 2025-10-01 | 3909824 | 0
GEN-2023-211 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.09535 | 2025-10-01 | 3909824 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06581 | 2025-10-01 | 3909824 | 0
ASGI-2023-001 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03305 | 2025-10-01 | 3909824 | 0
GEN-2023-001 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03309 | 2025-10-01 | 3909824 | 0
GEN-2023-005 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-01 | 3909824 | 0
GEN-2023-008 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03428 | 2025-10-01 | 3909824 | 0
GEN-2023-060 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-01 | 3909824 | 0
GEN-2023-081 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03302 | 2025-10-01 | 3909824 | 0
GEN-2023-086 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0326 | 2025-10-01 | 3909824 | 0
GEN-2023-110 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03172 | 2025-10-01 | 3909824 | 0
GEN-2023-120 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03334 | 2025-10-01 | 3909824 | 0
GEN-2023-142 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-01 | 3909824 | 0
GEN-2023-143 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-01 | 3909824 | 0
GEN-2023-158 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03326 | 2025-10-01 | 3909824 | 0
GEN-2023-159 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03326 | 2025-10-01 | 3909824 | 0
GEN-2023-178 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03325 | 2025-10-01 | 3909824 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03305 | 2025-10-01 | 3909824 | 0
GEN-2023-195 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-01 | 3909824 | 0
GEN-2023-201 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03303 | 2025-10-01 | 3909824 | 0
GEN-2023-203 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03311 | 2025-10-01 | 3909824 | 0
GEN-2023-208 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03233 | 2025-10-01 | 3909824 | 0
GEN-2023-209 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03242 | 2025-10-01 | 3909824 | 0
GEN-2023-236 | 05 SOUTHWEST | ERIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03304 | 2025-10-01 | 3909824 | 0
GEN-2023-050 | 03 CENTRAL | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03568 | 2025-10-01 | 3909824 | 0
GEN-2023-030 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03262 | 2025-10-01 | 3909824 | 0
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03129 | 2025-10-01 | 3909824 | 0
GEN-2023-057 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05551 | 2025-10-01 | 3909824 | 0
GEN-2023-059 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03398 | 2025-10-01 | 3909824 | 0
GEN-2023-135 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03776 | 2025-10-01 | 3909824 | 0
GEN-2023-151 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03342 | 2025-10-01 | 3909824 | 0
GEN-2023-188 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07189 | 2025-10-01 | 3909824 | 0
GEN-2023-193 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03472 | 2025-10-01 | 3909824 | 0
GEN-2023-212 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03758 | 2025-10-01 | 3909824 | 0
GEN-2023-227 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03518 | 2025-10-01 | 3909824 | 0
GEN-2023-230 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03364 | 2025-10-01 | 3909824 | 0
GEN-2023-022 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06154 | 2025-10-01 | 3909824 | 0
GEN-2023-075 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05718 | 2025-10-01 | 3909824 | 0
GEN-2023-076 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05718 | 2025-10-01 | 3909824 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06766 | 2025-10-01 | 3909824 | 0
GEN-2023-211 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.09176 | 2025-10-01 | 3909824 | 0
GEN-2023-229 | 04 SOUTHEAST | NRIS | 210540 | 112504 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345kV Terminal Upgrades (OGE) | Install terminal equipment to support a 345kV line from Wekiwa to Sooner rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03013 | 2025-10-01 | 3909824 | 0
GEN-2023-011 | 02 NEBRASKA | ERIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.12155 | 2025-10-01 | 5468352 | 5468352
GEN-2023-222 | 02 NEBRASKA | ERIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.17888 | 2025-10-01 | 5468352 | 5468352
GEN-2023-223 | 02 NEBRASKA | ERIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.17888 | 2025-10-01 | 5468352 | 5468352
GEN-2023-224 | 02 NEBRASKA | ERIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.03472 | 2025-10-01 | 5468352 | 5468352
GEN-2023-225 | 02 NEBRASKA | ERIS | 200477 | 71964 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #1 | Add a new 345/115 kV ckt 1 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.03472 | 2025-10-01 | 5468352 | 5468352
GEN-2023-006 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04757 | 2025-10-08 | 5915803 | 0
GEN-2023-034 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04134 | 2025-10-08 | 5915803 | 0
GEN-2023-061 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03968 | 2025-10-08 | 5915803 | 0
GEN-2023-065 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03266 | 2025-10-08 | 5915803 | 0
GEN-2023-073 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04154 | 2025-10-08 | 5915803 | 0
GEN-2023-085 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05812 | 2025-10-08 | 5915803 | 0
GEN-2023-194 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03876 | 2025-10-08 | 5915803 | 0
GEN-2023-231 | 03 CENTRAL | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05038 | 2025-10-08 | 5915803 | 0
GEN-2022-130 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0498 | 2025-10-08 | 5915803 | 0
GEN-2023-022 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06074 | 2025-10-08 | 5915803 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07002 | 2025-10-08 | 5915803 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06622 | 2025-10-08 | 5915803 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06496 | 2025-10-08 | 5915803 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06878 | 2025-10-08 | 5915803 | 0
GEN-2023-056 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05126 | 2025-10-08 | 5915803 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.08843 | 2025-10-08 | 5915803 | 0
GEN-2023-064 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05223 | 2025-10-08 | 5915803 | 0
GEN-2023-075 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07147 | 2025-10-08 | 5915803 | 0
GEN-2023-076 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07147 | 2025-10-08 | 5915803 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07311 | 2025-10-08 | 5915803 | 0
GEN-2023-100 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03272 | 2025-10-08 | 5915803 | 0
GEN-2023-102 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03272 | 2025-10-08 | 5915803 | 0
GEN-2023-104 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0358 | 2025-10-08 | 5915803 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0594 | 2025-10-08 | 5915803 | 0
GEN-2023-138 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.09248 | 2025-10-08 | 5915803 | 0
GEN-2023-180 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04909 | 2025-10-08 | 5915803 | 0
GEN-2023-205 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.04619 | 2025-10-08 | 5915803 | 0
GEN-2023-211 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.09535 | 2025-10-08 | 5915803 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06581 | 2025-10-08 | 5915803 | 0
ASGI-2023-001 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03305 | 2025-10-08 | 5915803 | 0
GEN-2023-001 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03309 | 2025-10-08 | 5915803 | 0
GEN-2023-005 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-08 | 5915803 | 0
GEN-2023-008 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03428 | 2025-10-08 | 5915803 | 0
GEN-2023-060 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-08 | 5915803 | 0
GEN-2023-081 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03302 | 2025-10-08 | 5915803 | 0
GEN-2023-086 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.0326 | 2025-10-08 | 5915803 | 0
GEN-2023-110 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03172 | 2025-10-08 | 5915803 | 0
GEN-2023-120 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03334 | 2025-10-08 | 5915803 | 0
GEN-2023-142 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-08 | 5915803 | 0
GEN-2023-143 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-08 | 5915803 | 0
GEN-2023-158 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03326 | 2025-10-08 | 5915803 | 0
GEN-2023-159 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03326 | 2025-10-08 | 5915803 | 0
GEN-2023-178 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03325 | 2025-10-08 | 5915803 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03305 | 2025-10-08 | 5915803 | 0
GEN-2023-195 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-08 | 5915803 | 0
GEN-2023-201 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03303 | 2025-10-08 | 5915803 | 0
GEN-2023-203 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03311 | 2025-10-08 | 5915803 | 0
GEN-2023-208 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03233 | 2025-10-08 | 5915803 | 0
GEN-2023-209 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03242 | 2025-10-08 | 5915803 | 0
GEN-2023-236 | 05 SOUTHWEST | ERIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03304 | 2025-10-08 | 5915803 | 0
GEN-2023-050 | 03 CENTRAL | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03568 | 2025-10-08 | 5915803 | 0
GEN-2023-030 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03262 | 2025-10-08 | 5915803 | 0
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03129 | 2025-10-08 | 5915803 | 0
GEN-2023-057 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05551 | 2025-10-08 | 5915803 | 0
GEN-2023-059 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03398 | 2025-10-08 | 5915803 | 0
GEN-2023-135 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03776 | 2025-10-08 | 5915803 | 0
GEN-2023-151 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03342 | 2025-10-08 | 5915803 | 0
GEN-2023-188 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.07189 | 2025-10-08 | 5915803 | 0
GEN-2023-193 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03472 | 2025-10-08 | 5915803 | 0
GEN-2023-212 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03758 | 2025-10-08 | 5915803 | 0
GEN-2023-227 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03518 | 2025-10-08 | 5915803 | 0
GEN-2023-230 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03364 | 2025-10-08 | 5915803 | 0
GEN-2023-022 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06154 | 2025-10-08 | 5915803 | 0
GEN-2023-075 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05718 | 2025-10-08 | 5915803 | 0
GEN-2023-076 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.05718 | 2025-10-08 | 5915803 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.06766 | 2025-10-08 | 5915803 | 0
GEN-2023-211 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.09176 | 2025-10-08 | 5915803 | 0
GEN-2023-229 | 04 SOUTHEAST | NRIS | 210544 | 112502 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV Terminal Upgrades (AEP) | Install terminal equipment at Wekiwa to support a 345 kV line from Sooner to Wekiwa rated at summer emergency of 1792 MVA | 2019 ITP | Yes | Yes | 0.03013 | 2025-10-08 | 5915803 | 0
GEN-2023-006 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.04757 | 2025-10-08 | 129129933 | 0
GEN-2023-034 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.04134 | 2025-10-08 | 129129933 | 0
GEN-2023-061 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03968 | 2025-10-08 | 129129933 | 0
GEN-2023-065 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03266 | 2025-10-08 | 129129933 | 0
GEN-2023-073 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.04154 | 2025-10-08 | 129129933 | 0
GEN-2023-085 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.05812 | 2025-10-08 | 129129933 | 0
GEN-2023-194 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03876 | 2025-10-08 | 129129933 | 0
GEN-2023-231 | 03 CENTRAL | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.05038 | 2025-10-08 | 129129933 | 0
GEN-2022-130 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0498 | 2025-10-08 | 129129933 | 0
GEN-2023-022 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.06074 | 2025-10-08 | 129129933 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07002 | 2025-10-08 | 129129933 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.06622 | 2025-10-08 | 129129933 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.06496 | 2025-10-08 | 129129933 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.06878 | 2025-10-08 | 129129933 | 0
GEN-2023-056 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.05126 | 2025-10-08 | 129129933 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.08843 | 2025-10-08 | 129129933 | 0
GEN-2023-064 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.05223 | 2025-10-08 | 129129933 | 0
GEN-2023-075 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07147 | 2025-10-08 | 129129933 | 0
GEN-2023-076 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07147 | 2025-10-08 | 129129933 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07311 | 2025-10-08 | 129129933 | 0
GEN-2023-100 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03272 | 2025-10-08 | 129129933 | 0
GEN-2023-102 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03272 | 2025-10-08 | 129129933 | 0
GEN-2023-104 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0358 | 2025-10-08 | 129129933 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0594 | 2025-10-08 | 129129933 | 0
GEN-2023-138 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.09248 | 2025-10-08 | 129129933 | 0
GEN-2023-180 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.04909 | 2025-10-08 | 129129933 | 0
GEN-2023-205 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.04619 | 2025-10-08 | 129129933 | 0
GEN-2023-211 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.09535 | 2025-10-08 | 129129933 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.06581 | 2025-10-08 | 129129933 | 0
ASGI-2023-001 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03305 | 2025-10-08 | 129129933 | 0
GEN-2023-001 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03309 | 2025-10-08 | 129129933 | 0
GEN-2023-005 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-08 | 129129933 | 0
GEN-2023-008 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03428 | 2025-10-08 | 129129933 | 0
GEN-2023-060 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-08 | 129129933 | 0
GEN-2023-081 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03302 | 2025-10-08 | 129129933 | 0
GEN-2023-086 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.0326 | 2025-10-08 | 129129933 | 0
GEN-2023-110 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03172 | 2025-10-08 | 129129933 | 0
GEN-2023-120 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03334 | 2025-10-08 | 129129933 | 0
GEN-2023-142 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-08 | 129129933 | 0
GEN-2023-143 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-08 | 129129933 | 0
GEN-2023-158 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03326 | 2025-10-08 | 129129933 | 0
GEN-2023-159 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03326 | 2025-10-08 | 129129933 | 0
GEN-2023-178 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03325 | 2025-10-08 | 129129933 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03305 | 2025-10-08 | 129129933 | 0
GEN-2023-195 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03327 | 2025-10-08 | 129129933 | 0
GEN-2023-201 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03303 | 2025-10-08 | 129129933 | 0
GEN-2023-203 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03311 | 2025-10-08 | 129129933 | 0
GEN-2023-208 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03233 | 2025-10-08 | 129129933 | 0
GEN-2023-209 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03242 | 2025-10-08 | 129129933 | 0
GEN-2023-236 | 05 SOUTHWEST | ERIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03304 | 2025-10-08 | 129129933 | 0
GEN-2023-050 | 03 CENTRAL | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03568 | 2025-10-08 | 129129933 | 0
GEN-2023-030 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03262 | 2025-10-08 | 129129933 | 0
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03129 | 2025-10-08 | 129129933 | 0
GEN-2023-057 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.05551 | 2025-10-08 | 129129933 | 0
GEN-2023-059 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03398 | 2025-10-08 | 129129933 | 0
GEN-2023-135 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03776 | 2025-10-08 | 129129933 | 0
GEN-2023-151 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03342 | 2025-10-08 | 129129933 | 0
GEN-2023-188 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.07189 | 2025-10-08 | 129129933 | 0
GEN-2023-193 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03472 | 2025-10-08 | 129129933 | 0
GEN-2023-212 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03758 | 2025-10-08 | 129129933 | 0
GEN-2023-227 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03518 | 2025-10-08 | 129129933 | 0
GEN-2023-230 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03364 | 2025-10-08 | 129129933 | 0
GEN-2023-022 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.06154 | 2025-10-08 | 129129933 | 0
GEN-2023-075 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.05718 | 2025-10-08 | 129129933 | 0
GEN-2023-076 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.05718 | 2025-10-08 | 129129933 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.06766 | 2025-10-08 | 129129933 | 0
GEN-2023-211 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.09176 | 2025-10-08 | 129129933 | 0
GEN-2023-229 | 04 SOUTHEAST | NRIS | 210593 | 112458 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sooner - Wekiwa 345 kV New Line | Build a new 345kV line from Sooner to Wekiwa with a summer emergency rating of 1792 MVA | 2019 ITP | Yes | Yes | 0.03013 | 2025-10-08 | 129129933 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03143 | 2025-10-09 | 12238460 | 0
GEN-2023-015 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.08071 | 2025-10-09 | 12238460 | 0
GEN-2023-107 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.0608 | 2025-10-09 | 12238460 | 0
GEN-2023-172 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.06807 | 2025-10-09 | 12238460 | 0
GEN-2023-173 | 03 CENTRAL | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.06807 | 2025-10-09 | 12238460 | 0
GEN-2023-009 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05527 | 2025-10-09 | 12238460 | 0
GEN-2023-022 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05394 | 2025-10-09 | 12238460 | 0
GEN-2023-030 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03413 | 2025-10-09 | 12238460 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.09112 | 2025-10-09 | 12238460 | 0
GEN-2023-038 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.06215 | 2025-10-09 | 12238460 | 0
GEN-2023-059 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03699 | 2025-10-09 | 12238460 | 0
GEN-2023-059 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05347 | 2025-10-09 | 12238460 | 0
GEN-2023-069 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.06033 | 2025-10-09 | 12238460 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04736 | 2025-10-09 | 12238460 | 0
GEN-2023-092 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05745 | 2025-10-09 | 12238460 | 0
GEN-2023-100 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.10192 | 2025-10-09 | 12238460 | 0
GEN-2023-101 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.38346 | 2025-10-09 | 12238460 | 0
GEN-2023-102 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.10192 | 2025-10-09 | 12238460 | 0
GEN-2023-104 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.0858 | 2025-10-09 | 12238460 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.0533 | 2025-10-09 | 12238460 | 0
GEN-2023-135 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04531 | 2025-10-09 | 12238460 | 0
GEN-2023-150 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.12838 | 2025-10-09 | 12238460 | 0
GEN-2023-151 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03805 | 2025-10-09 | 12238460 | 0
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04328 | 2025-10-09 | 12238460 | 0
GEN-2023-164 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.14916 | 2025-10-09 | 12238460 | 0
GEN-2023-165 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.14916 | 2025-10-09 | 12238460 | 0
GEN-2023-166 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05138 | 2025-10-09 | 12238460 | 0
GEN-2023-167 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05547 | 2025-10-09 | 12238460 | 0
GEN-2023-168 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05572 | 2025-10-09 | 12238460 | 0
GEN-2023-174 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.08301 | 2025-10-09 | 12238460 | 0
GEN-2023-177 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.06649 | 2025-10-09 | 12238460 | 0
GEN-2023-188 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.09529 | 2025-10-09 | 12238460 | 0
GEN-2023-193 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03827 | 2025-10-09 | 12238460 | 0
GEN-2023-204 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05968 | 2025-10-09 | 12238460 | 0
GEN-2023-205 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04431 | 2025-10-09 | 12238460 | 0
GEN-2023-210 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05213 | 2025-10-09 | 12238460 | 0
GEN-2023-212 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04518 | 2025-10-09 | 12238460 | 0
GEN-2023-227 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03892 | 2025-10-09 | 12238460 | 0
GEN-2023-229 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.13033 | 2025-10-09 | 12238460 | 0
GEN-2023-230 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03685 | 2025-10-09 | 12238460 | 0
GEN-2023-241 | 04 SOUTHEAST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03888 | 2025-10-09 | 12238460 | 0
GEN-2023-010 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.07893 | 2025-10-09 | 12238460 | 0
GEN-2023-110 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.21742 | 2025-10-09 | 12238460 | 0
GEN-2023-123 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.05831 | 2025-10-09 | 12238460 | 0
GEN-2023-176 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.1021 | 2025-10-09 | 12238460 | 0
GEN-2023-183 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.11917 | 2025-10-09 | 12238460 | 0
GEN-2023-237 | 05 SOUTHWEST | ERIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.11724 | 2025-10-09 | 12238460 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.0714 | 2025-10-09 | 12238460 | 0
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03225 | 2025-10-09 | 12238460 | 0
GEN-2023-100 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.1048 | 2025-10-09 | 12238460 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.33453 | 2025-10-09 | 12238460 | 0
GEN-2023-102 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.1048 | 2025-10-09 | 12238460 | 0
GEN-2023-104 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.14062 | 2025-10-09 | 12238460 | 0
GEN-2023-150 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.10463 | 2025-10-09 | 12238460 | 0
GEN-2023-164 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.12352 | 2025-10-09 | 12238460 | 0
GEN-2023-165 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.12352 | 2025-10-09 | 12238460 | 0
GEN-2023-177 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03372 | 2025-10-09 | 12238460 | 0
GEN-2023-188 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.06025 | 2025-10-09 | 12238460 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04122 | 2025-10-09 | 12238460 | 0
GEN-2023-022 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04075 | 2025-10-09 | 12238460 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.08312 | 2025-10-09 | 12238460 | 0
GEN-2023-134 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.04515 | 2025-10-09 | 12238460 | 0
GEN-2023-229 | 04 SOUTHEAST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.03328 | 2025-10-09 | 12238460 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 210627 | 143182 | Multi - Border - Woodward 345 kV Tap | Chisholm - Woodward - Border 345 kV Ckt 1 (AEP) | Build 0.84-miles of new 345 kV line from a new tap on the Woodward to Border 345 kV line to Chisholm with a summer emergency rating of 1792 MVA. Oklahoma Gas and Electric Co. and American Electric Power shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC | 2020 ITP | Yes | Yes | 0.06023 | 2025-10-09 | 12238460 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.06538 | 2025-10-30 | 2195001 | 2195001
GEN-2023-150 | 04 SOUTHEAST | ERIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03178 | 2025-10-30 | 2195001 | 2195001
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.04769 | 2025-10-30 | 2195001 | 2195001
GEN-2023-229 | 04 SOUTHEAST | ERIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03219 | 2025-10-30 | 2195001 | 2195001
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.06584 | 2025-10-30 | 2195001 | 2195001
GEN-2023-150 | 04 SOUTHEAST | NRIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03257 | 2025-10-30 | 2195001 | 2195001
GEN-2023-161 | 04 SOUTHEAST | NRIS | 210483 | 72022 | Multi - Park Community - Sunshine 138 kV | Cana - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 3.3 mile 69 kV line from Cana - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno Jct. | DPA-2017-August-767-774-776 | Yes | Yes | 0.04852 | 2025-10-30 | 2195001 | 2195001
GEN-2023-038 | 04 SOUTHEAST | ERIS | 210617 | 143253 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli - Lexington kV 138 kV | Rebuild 14.3 miles of 69 kV line from Paoli to Lexington to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04334 | 2025-10-31 | 10608616 | 10608616
GEN-2023-069 | 04 SOUTHEAST | ERIS | 210617 | 143253 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli - Lexington kV 138 kV | Rebuild 14.3 miles of 69 kV line from Paoli to Lexington to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04217 | 2025-10-31 | 10608616 | 10608616
GEN-2023-174 | 04 SOUTHEAST | ERIS | 210617 | 143253 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli - Lexington kV 138 kV | Rebuild 14.3 miles of 69 kV line from Paoli to Lexington to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.26776 | 2025-10-31 | 10608616 | 10608616
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210617 | 143253 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli - Lexington kV 138 kV | Rebuild 14.3 miles of 69 kV line from Paoli to Lexington to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04592 | 2025-10-31 | 10608616 | 10608616
GEN-2023-069 | 04 SOUTHEAST | NRIS | 210617 | 143253 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli - Lexington kV 138 kV | Rebuild 14.3 miles of 69 kV line from Paoli to Lexington to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.03452 | 2025-10-31 | 10608616 | 10608616
GEN-2023-166 | 04 SOUTHEAST | ERIS | 210664 | 144279 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Classen substation. | DPA-2021-March-1296 | Yes | Yes | 0.14993 | 2025-11-28 | 600000 | 600000
GEN-2023-167 | 04 SOUTHEAST | ERIS | 210664 | 144279 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Classen substation. | DPA-2021-March-1296 | Yes | Yes | 0.03775 | 2025-11-28 | 600000 | 600000
GEN-2023-168 | 04 SOUTHEAST | ERIS | 210664 | 144279 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Classen substation. | DPA-2021-March-1296 | Yes | Yes | 0.46441 | 2025-11-28 | 600000 | 600000
GEN-2023-167 | 04 SOUTHEAST | NRIS | 210664 | 144279 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Classen substation. | DPA-2021-March-1296 | Yes | Yes | 0.03694 | 2025-11-28 | 600000 | 600000
GEN-2023-168 | 04 SOUTHEAST | NRIS | 210664 | 144279 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Classen substation. | DPA-2021-March-1296 | Yes | Yes | 0.46525 | 2025-11-28 | 600000 | 600000
GEN-2023-168 | 04 SOUTHEAST | ERIS | 210664 | 144281 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen - Douglas Tap 138 kV Reconductor | Reconductor of Douglas Tap to Classen 138 kV transmission line. | DPA-2021-March-1296 | Yes | Yes | 0.46441 | 2025-11-28 | 790000 | 790000
GEN-2023-168 | 04 SOUTHEAST | NRIS | 210664 | 144281 | Multi - West Oaks - Council - Classen 138 kV Reconductor | Classen - Douglas Tap 138 kV Reconductor | Reconductor of Douglas Tap to Classen 138 kV transmission line. | DPA-2021-March-1296 | Yes | Yes | 0.46525 | 2025-11-28 | 790000 | 790000
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210617 | 143255 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Paoli Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04432 | 2025-11-30 | 2225000 | 2225000
GEN-2023-038 | 04 SOUTHEAST | ERIS | 210617 | 143255 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Paoli Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.06688 | 2025-11-30 | 2225000 | 2225000
GEN-2023-069 | 04 SOUTHEAST | ERIS | 210617 | 143255 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Paoli Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.0645 | 2025-11-30 | 2225000 | 2225000
GEN-2023-174 | 04 SOUTHEAST | ERIS | 210617 | 143255 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Paoli Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.38303 | 2025-11-30 | 2225000 | 2225000
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210617 | 143255 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Paoli Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04271 | 2025-11-30 | 2225000 | 2225000
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210617 | 143255 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Paoli Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.06696 | 2025-11-30 | 2225000 | 2225000
GEN-2023-069 | 04 SOUTHEAST | NRIS | 210617 | 143255 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Paoli 138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Paoli Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.06561 | 2025-11-30 | 2225000 | 2225000
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.06538 | 2025-11-30 | 6741332 | 6741332
GEN-2023-150 | 04 SOUTHEAST | ERIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03178 | 2025-11-30 | 6741332 | 6741332
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.04769 | 2025-11-30 | 6741332 | 6741332
GEN-2023-229 | 04 SOUTHEAST | ERIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03219 | 2025-11-30 | 6741332 | 6741332
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.06584 | 2025-11-30 | 6741332 | 6741332
GEN-2023-150 | 04 SOUTHEAST | NRIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03257 | 2025-11-30 | 6741332 | 6741332
GEN-2023-161 | 04 SOUTHEAST | NRIS | 210483 | 72020 | Multi - Park Community - Sunshine 138 kV | Calumet - Cana 138 kV Ckt 1 Voltage Conversion | Convert 9.1 mile 69 kV line from Calumet - Cana to 138 kV. Complete necessary terminal upgrades at Cana. | DPA-2017-August-767-774-776 | Yes | Yes | 0.04852 | 2025-11-30 | 6741332 | 6741332
GEN-2023-161 | 04 SOUTHEAST | ERIS | 220739 | 122761 | Line - Cimarron - Czech Hall 138 kV Ckt 1 | Czech Hall 138 kV Terminal Upgrade | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 2023 ITP | Yes | Yes | 0.07386 | 2025-12-01 | 154916 | 0
GEN-2023-166 | 04 SOUTHEAST | ERIS | 220739 | 122761 | Line - Cimarron - Czech Hall 138 kV Ckt 1 | Czech Hall 138 kV Terminal Upgrade | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 2023 ITP | Yes | Yes | 0.08336 | 2025-12-01 | 154916 | 0
GEN-2023-167 | 04 SOUTHEAST | ERIS | 220739 | 122761 | Line - Cimarron - Czech Hall 138 kV Ckt 1 | Czech Hall 138 kV Terminal Upgrade | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 2023 ITP | Yes | Yes | 0.08947 | 2025-12-01 | 154916 | 0
GEN-2023-168 | 04 SOUTHEAST | ERIS | 220739 | 122761 | Line - Cimarron - Czech Hall 138 kV Ckt 1 | Czech Hall 138 kV Terminal Upgrade | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 2023 ITP | Yes | Yes | 0.15221 | 2025-12-01 | 154916 | 0
GEN-2023-161 | 04 SOUTHEAST | NRIS | 220739 | 122761 | Line - Cimarron - Czech Hall 138 kV Ckt 1 | Czech Hall 138 kV Terminal Upgrade | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 2023 ITP | Yes | Yes | 0.06869 | 2025-12-01 | 154916 | 0
GEN-2023-167 | 04 SOUTHEAST | NRIS | 220739 | 122761 | Line - Cimarron - Czech Hall 138 kV Ckt 1 | Czech Hall 138 kV Terminal Upgrade | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 2023 ITP | Yes | Yes | 0.09344 | 2025-12-01 | 154916 | 0
GEN-2023-168 | 04 SOUTHEAST | NRIS | 220739 | 122761 | Line - Cimarron - Czech Hall 138 kV Ckt 1 | Czech Hall 138 kV Terminal Upgrade | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 2023 ITP | Yes | Yes | 0.15629 | 2025-12-01 | 154916 | 0
GEN-2023-210 | 04 SOUTHEAST | NRIS | 220739 | 122761 | Line - Cimarron - Czech Hall 138 kV Ckt 1 | Czech Hall 138 kV Terminal Upgrade | Upgrade the switch at Czech Hall 138 kV on the Cimarron to Czech Hall line to achieve a 388/444/478/478 (SN/SE/WN/WE) MVA rating. | 2023 ITP | Yes | Yes | 0.03263 | 2025-12-01 | 154916 | 0
GEN-2023-167 | 04 SOUTHEAST | NRIS | 220739 | 157392 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Westmoore 138 kV Terminal Upgrade #2 | Install any necessary terminal equipment at Westmoore 138 kV substation to support a new line from Westmoore substation to Southgate 138 kV substation with a summer emergency rating of 308 MVA. | 2023 ITP | Yes | Yes | 0.09252 | 2025-12-01 | 3308294 | 0
GEN-2023-168 | 04 SOUTHEAST | NRIS | 220739 | 157392 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Westmoore 138 kV Terminal Upgrade #2 | Install any necessary terminal equipment at Westmoore 138 kV substation to support a new line from Westmoore substation to Southgate 138 kV substation with a summer emergency rating of 308 MVA. | 2023 ITP | Yes | Yes | 0.12253 | 2025-12-01 | 3308294 | 0
GEN-2023-038 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.11618 | 2025-12-01 | 5613374 | 0
GEN-2023-069 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.07949 | 2025-12-01 | 5613374 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.03085 | 2025-12-01 | 5613374 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.09542 | 2025-12-01 | 5613374 | 0
GEN-2023-177 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.18514 | 2025-12-01 | 5613374 | 0
GEN-2023-205 | 04 SOUTHEAST | ERIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.04198 | 2025-12-01 | 5613374 | 0
GEN-2023-038 | 04 SOUTHEAST | NRIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.12912 | 2025-12-01 | 5613374 | 0
GEN-2023-069 | 04 SOUTHEAST | NRIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.07939 | 2025-12-01 | 5613374 | 0
GEN-2023-177 | 04 SOUTHEAST | NRIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.19941 | 2025-12-01 | 5613374 | 0
GEN-2023-205 | 04 SOUTHEAST | NRIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.04273 | 2025-12-01 | 5613374 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.03933 | 2025-12-01 | 5613374 | 0
GEN-2023-134 | 04 SOUTHEAST | NRIS | 220739 | 157242 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (345 kV) | Install a new 345/138 kV transformer at Seminole 345 kV substation to achieve a summer emergency rating of 675 MVA. | 2023 ITP | Yes | Yes | 0.09931 | 2025-12-01 | 5613374 | 0
GEN-2023-167 | 04 SOUTHEAST | NRIS | 220739 | 157390 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Southgate - Westmoore Tap 138 kV Extend Line | Extend Southgate - Westmoore Tap 138 kV 0.76 miles to Westmoore 138 kV substation, including structures suited for double circuit configuration. | 2023 ITP | Yes | Yes | 0.09252 | 2025-12-01 | 6158692 | 0
GEN-2023-168 | 04 SOUTHEAST | NRIS | 220739 | 157390 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | Southgate - Westmoore Tap 138 kV Extend Line | Extend Southgate - Westmoore Tap 138 kV 0.76 miles to Westmoore 138 kV substation, including structures suited for double circuit configuration. | 2023 ITP | Yes | Yes | 0.12253 | 2025-12-01 | 6158692 | 0
GEN-2023-038 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.11618 | 2025-12-01 | 9281667 | 0
GEN-2023-069 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.07949 | 2025-12-01 | 9281667 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.03085 | 2025-12-01 | 9281667 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.09542 | 2025-12-01 | 9281667 | 0
GEN-2023-177 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.18514 | 2025-12-01 | 9281667 | 0
GEN-2023-205 | 04 SOUTHEAST | ERIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.04198 | 2025-12-01 | 9281667 | 0
GEN-2023-038 | 04 SOUTHEAST | NRIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.12912 | 2025-12-01 | 9281667 | 0
GEN-2023-069 | 04 SOUTHEAST | NRIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.07939 | 2025-12-01 | 9281667 | 0
GEN-2023-177 | 04 SOUTHEAST | NRIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.19941 | 2025-12-01 | 9281667 | 0
GEN-2023-205 | 04 SOUTHEAST | NRIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.04273 | 2025-12-01 | 9281667 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.03933 | 2025-12-01 | 9281667 | 0
GEN-2023-134 | 04 SOUTHEAST | NRIS | 220739 | 157241 | XFR - Seminole 345/138 kV Ckt3 | Seminole 345/138 kV Transformer Ckt 3 (138 kV) | Install a new 345/138 kV transformer at Seminole 138 kV substation to achieve a summer emergency rating of 448 MVA. | 2023 ITP | Yes | Yes | 0.09931 | 2025-12-01 | 9281667 | 0
GEN-2023-166 | 04 SOUTHEAST | ERIS | 220739 | 157390 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | PENNSYLVANIA-SOUTHGATE-WESTMOORE 138 KV EXTEND LINE | Remove the Westmoore Tap and creating a McClain-Westmoore 138 kV line and a SouthgateWestmoore 138 kV line. Terminal upgrades at Westmoor and Pennsylvania substation for 478/478 MVA line rating. | 2023 ITP | Yes | Yes | 0.07022 | 2025-12-01 | 6158692 | 0
GEN-2023-167 | 04 SOUTHEAST | ERIS | 220739 | 157390 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | PENNSYLVANIA-SOUTHGATE-WESTMOORE 138 KV EXTEND LINE | Remove the Westmoore Tap and creating a McClain-Westmoore 138 kV line and a SouthgateWestmoore 138 kV line. Terminal upgrades at Westmoor and Pennsylvania substation for 478/478 MVA line rating. | 2023 ITP | Yes | Yes | 0.08584 | 2025-12-01 | 6158692 | 0
GEN-2023-168 | 04 SOUTHEAST | ERIS | 220739 | 157390 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | PENNSYLVANIA-SOUTHGATE-WESTMOORE 138 KV EXTEND LINE | Remove the Westmoore Tap and creating a McClain-Westmoore 138 kV line and a SouthgateWestmoore 138 kV line. Terminal upgrades at Westmoor and Pennsylvania substation for 478/478 MVA line rating. | 2023 ITP | Yes | Yes | 0.11587 | 2025-12-01 | 6158692 | 0
GEN-2023-167 | 04 SOUTHEAST | NRIS | 220739 | 157390 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | PENNSYLVANIA-SOUTHGATE-WESTMOORE 138 KV EXTEND LINE | Remove the Westmoore Tap and creating a McClain-Westmoore 138 kV line and a SouthgateWestmoore 138 kV line. Terminal upgrades at Westmoor and Pennsylvania substation for 478/478 MVA line rating. | 2023 ITP | Yes | Yes | 0.09252 | 2025-12-01 | 6158692 | 0
GEN-2023-168 | 04 SOUTHEAST | NRIS | 220739 | 157390 | Multi - Southgate - Westmoore Tap - Pennsylvania 138 kV | PENNSYLVANIA-SOUTHGATE-WESTMOORE 138 KV EXTEND LINE | Remove the Westmoore Tap and creating a McClain-Westmoore 138 kV line and a SouthgateWestmoore 138 kV line. Terminal upgrades at Westmoor and Pennsylvania substation for 478/478 MVA line rating. | 2023 ITP | Yes | Yes | 0.12253 | 2025-12-01 | 6158692 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.04139 | 2025-12-31 | 243120 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.04297 | 2025-12-31 | 243120 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210715 | 156282 | Sub - Fargo 230 kV Terminal Upgrade | Fargo 230 kV Terminal Upgrade | Upgrade terminal conductor at Fargo 230 kV substation to support the line to Sheyenne | 2022 ITP | Yes | Yes | 0.0339 | 2025-12-31 | 243120 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0315 | 2025-12-31 | 401187 | 0
GEN-2023-006 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.1159 | 2025-12-31 | 401187 | 0
GEN-2023-015 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08005 | 2025-12-31 | 401187 | 0
GEN-2023-023 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03219 | 2025-12-31 | 401187 | 0
GEN-2023-032 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03484 | 2025-12-31 | 401187 | 0
GEN-2023-033 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03144 | 2025-12-31 | 401187 | 0
GEN-2023-036 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03264 | 2025-12-31 | 401187 | 0
GEN-2023-037 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0319 | 2025-12-31 | 401187 | 0
GEN-2023-050 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.097 | 2025-12-31 | 401187 | 0
GEN-2023-061 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06834 | 2025-12-31 | 401187 | 0
GEN-2023-065 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06781 | 2025-12-31 | 401187 | 0
GEN-2023-073 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.27648 | 2025-12-31 | 401187 | 0
GEN-2023-085 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07045 | 2025-12-31 | 401187 | 0
GEN-2023-087 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04207 | 2025-12-31 | 401187 | 0
GEN-2023-107 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05322 | 2025-12-31 | 401187 | 0
GEN-2023-149 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06504 | 2025-12-31 | 401187 | 0
GEN-2023-169 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03144 | 2025-12-31 | 401187 | 0
GEN-2023-170 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03267 | 2025-12-31 | 401187 | 0
GEN-2023-171 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03213 | 2025-12-31 | 401187 | 0
GEN-2023-172 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06066 | 2025-12-31 | 401187 | 0
GEN-2023-173 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06066 | 2025-12-31 | 401187 | 0
GEN-2023-194 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07687 | 2025-12-31 | 401187 | 0
GEN-2023-231 | 03 CENTRAL | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.11266 | 2025-12-31 | 401187 | 0
GEN-2022-130 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03693 | 2025-12-31 | 401187 | 0
GEN-2023-022 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04979 | 2025-12-31 | 401187 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05793 | 2025-12-31 | 401187 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05971 | 2025-12-31 | 401187 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06052 | 2025-12-31 | 401187 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05781 | 2025-12-31 | 401187 | 0
GEN-2023-056 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03795 | 2025-12-31 | 401187 | 0
GEN-2023-057 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03967 | 2025-12-31 | 401187 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05255 | 2025-12-31 | 401187 | 0
GEN-2023-064 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03707 | 2025-12-31 | 401187 | 0
GEN-2023-075 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.116 | 2025-12-31 | 401187 | 0
GEN-2023-076 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.116 | 2025-12-31 | 401187 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0547 | 2025-12-31 | 401187 | 0
GEN-2023-100 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0981 | 2025-12-31 | 401187 | 0
GEN-2023-101 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03832 | 2025-12-31 | 401187 | 0
GEN-2023-102 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0981 | 2025-12-31 | 401187 | 0
GEN-2023-104 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08748 | 2025-12-31 | 401187 | 0
GEN-2023-132 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03593 | 2025-12-31 | 401187 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04874 | 2025-12-31 | 401187 | 0
GEN-2023-138 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0871 | 2025-12-31 | 401187 | 0
GEN-2023-180 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03687 | 2025-12-31 | 401187 | 0
GEN-2023-211 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.15511 | 2025-12-31 | 401187 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05482 | 2025-12-31 | 401187 | 0
GEN-2023-086 | 05 SOUTHWEST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03569 | 2025-12-31 | 401187 | 0
GEN-2023-110 | 05 SOUTHWEST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03024 | 2025-12-31 | 401187 | 0
GEN-2023-183 | 05 SOUTHWEST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03238 | 2025-12-31 | 401187 | 0
GEN-2023-208 | 05 SOUTHWEST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03825 | 2025-12-31 | 401187 | 0
GEN-2023-209 | 05 SOUTHWEST | ERIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03712 | 2025-12-31 | 401187 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03443 | 2025-12-31 | 401187 | 0
GEN-2023-050 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06423 | 2025-12-31 | 401187 | 0
GEN-2023-065 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05918 | 2025-12-31 | 401187 | 0
GEN-2023-073 | 03 CENTRAL | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.27593 | 2025-12-31 | 401187 | 0
GEN-2023-100 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08034 | 2025-12-31 | 401187 | 0
GEN-2023-102 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08034 | 2025-12-31 | 401187 | 0
GEN-2023-104 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05836 | 2025-12-31 | 401187 | 0
GEN-2023-188 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03019 | 2025-12-31 | 401187 | 0
GEN-2023-022 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03101 | 2025-12-31 | 401187 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03637 | 2025-12-31 | 401187 | 0
GEN-2023-211 | 04 SOUTHEAST | NRIS | 220749 | 158453 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Wichita 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Wichita 345 kV substation on the Wichita to Benton 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.14539 | 2025-12-31 | 401187 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0315 | 2025-12-31 | 1221960 | 0
GEN-2023-006 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.1159 | 2025-12-31 | 1221960 | 0
GEN-2023-015 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08005 | 2025-12-31 | 1221960 | 0
GEN-2023-023 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03219 | 2025-12-31 | 1221960 | 0
GEN-2023-032 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03484 | 2025-12-31 | 1221960 | 0
GEN-2023-033 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03144 | 2025-12-31 | 1221960 | 0
GEN-2023-036 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03264 | 2025-12-31 | 1221960 | 0
GEN-2023-037 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0319 | 2025-12-31 | 1221960 | 0
GEN-2023-050 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.097 | 2025-12-31 | 1221960 | 0
GEN-2023-061 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06834 | 2025-12-31 | 1221960 | 0
GEN-2023-065 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06781 | 2025-12-31 | 1221960 | 0
GEN-2023-073 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.27648 | 2025-12-31 | 1221960 | 0
GEN-2023-085 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07045 | 2025-12-31 | 1221960 | 0
GEN-2023-087 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04207 | 2025-12-31 | 1221960 | 0
GEN-2023-107 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05322 | 2025-12-31 | 1221960 | 0
GEN-2023-149 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06504 | 2025-12-31 | 1221960 | 0
GEN-2023-169 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03144 | 2025-12-31 | 1221960 | 0
GEN-2023-170 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03267 | 2025-12-31 | 1221960 | 0
GEN-2023-171 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03213 | 2025-12-31 | 1221960 | 0
GEN-2023-172 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06066 | 2025-12-31 | 1221960 | 0
GEN-2023-173 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06066 | 2025-12-31 | 1221960 | 0
GEN-2023-194 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.07687 | 2025-12-31 | 1221960 | 0
GEN-2023-231 | 03 CENTRAL | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.11266 | 2025-12-31 | 1221960 | 0
GEN-2022-130 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03693 | 2025-12-31 | 1221960 | 0
GEN-2023-022 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04979 | 2025-12-31 | 1221960 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05793 | 2025-12-31 | 1221960 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05971 | 2025-12-31 | 1221960 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06052 | 2025-12-31 | 1221960 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05781 | 2025-12-31 | 1221960 | 0
GEN-2023-056 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03795 | 2025-12-31 | 1221960 | 0
GEN-2023-057 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03967 | 2025-12-31 | 1221960 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05255 | 2025-12-31 | 1221960 | 0
GEN-2023-064 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03707 | 2025-12-31 | 1221960 | 0
GEN-2023-075 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.116 | 2025-12-31 | 1221960 | 0
GEN-2023-076 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.116 | 2025-12-31 | 1221960 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0547 | 2025-12-31 | 1221960 | 0
GEN-2023-100 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0981 | 2025-12-31 | 1221960 | 0
GEN-2023-101 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03832 | 2025-12-31 | 1221960 | 0
GEN-2023-102 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0981 | 2025-12-31 | 1221960 | 0
GEN-2023-104 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08748 | 2025-12-31 | 1221960 | 0
GEN-2023-132 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03593 | 2025-12-31 | 1221960 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.04874 | 2025-12-31 | 1221960 | 0
GEN-2023-138 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.0871 | 2025-12-31 | 1221960 | 0
GEN-2023-180 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03687 | 2025-12-31 | 1221960 | 0
GEN-2023-211 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.15511 | 2025-12-31 | 1221960 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05482 | 2025-12-31 | 1221960 | 0
GEN-2023-086 | 05 SOUTHWEST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03569 | 2025-12-31 | 1221960 | 0
GEN-2023-110 | 05 SOUTHWEST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03024 | 2025-12-31 | 1221960 | 0
GEN-2023-183 | 05 SOUTHWEST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03238 | 2025-12-31 | 1221960 | 0
GEN-2023-208 | 05 SOUTHWEST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03825 | 2025-12-31 | 1221960 | 0
GEN-2023-209 | 05 SOUTHWEST | ERIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03712 | 2025-12-31 | 1221960 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03443 | 2025-12-31 | 1221960 | 0
GEN-2023-050 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.06423 | 2025-12-31 | 1221960 | 0
GEN-2023-065 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05918 | 2025-12-31 | 1221960 | 0
GEN-2023-073 | 03 CENTRAL | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.27593 | 2025-12-31 | 1221960 | 0
GEN-2023-100 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08034 | 2025-12-31 | 1221960 | 0
GEN-2023-102 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.08034 | 2025-12-31 | 1221960 | 0
GEN-2023-104 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.05836 | 2025-12-31 | 1221960 | 0
GEN-2023-188 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03019 | 2025-12-31 | 1221960 | 0
GEN-2023-022 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03101 | 2025-12-31 | 1221960 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.03637 | 2025-12-31 | 1221960 | 0
GEN-2023-211 | 04 SOUTHEAST | NRIS | 220749 | 158452 | Sub - Benton 345 kV - Wichita 345 kV Terminal Upgrades | Benton 345 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Benton 345 kV substation on the Benton to Wichita 345 kV line to achieve a summer emergency rating of 1119 MVA. | 2023 ITP | Yes | Yes | 0.14539 | 2025-12-31 | 1221960 | 0
GEN-2023-006 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.31232 | 2025-12-31 | 1534495 | 0
GEN-2023-050 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.27384 | 2025-12-31 | 1534495 | 0
GEN-2023-073 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.03267 | 2025-12-31 | 1534495 | 0
GEN-2023-085 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.09164 | 2025-12-31 | 1534495 | 0
GEN-2023-149 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.03239 | 2025-12-31 | 1534495 | 0
GEN-2023-170 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.03601 | 2025-12-31 | 1534495 | 0
GEN-2023-194 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.101 | 2025-12-31 | 1534495 | 0
GEN-2023-231 | 03 CENTRAL | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.22181 | 2025-12-31 | 1534495 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.03113 | 2025-12-31 | 1534495 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.04313 | 2025-12-31 | 1534495 | 0
GEN-2023-075 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.20486 | 2025-12-31 | 1534495 | 0
GEN-2023-076 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.20486 | 2025-12-31 | 1534495 | 0
GEN-2023-132 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.0418 | 2025-12-31 | 1534495 | 0
GEN-2023-138 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.07229 | 2025-12-31 | 1534495 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.04125 | 2025-12-31 | 1534495 | 0
GEN-2023-050 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.23867 | 2025-12-31 | 1534495 | 0
GEN-2023-061 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.05648 | 2025-12-31 | 1534495 | 0
GEN-2023-194 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.03299 | 2025-12-31 | 1534495 | 0
GEN-2023-220 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.03227 | 2025-12-31 | 1534495 | 0
GEN-2023-221 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.03252 | 2025-12-31 | 1534495 | 0
GEN-2023-057 | 04 SOUTHEAST | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.06442 | 2025-12-31 | 1534495 | 0
GEN-2023-213 | 04 SOUTHEAST | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.03889 | 2025-12-31 | 1534495 | 0
GEN-2023-085 | 03 CENTRAL | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.04403 | 2025-12-31 | 1534495 | 0
GEN-2023-075 | 04 SOUTHEAST | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.15063 | 2025-12-31 | 1534495 | 0
GEN-2023-076 | 04 SOUTHEAST | NRIS | 220749 | 157403 | Sub - Blackberry - Neosho 345 kV Terminal Equipment | Neosho 345 kV Terminal Upgrade | Install any necessary terminal equipment at Neosho 345 kV substation on the Neosho to Blackberry 345 kV line to achieve a winter emergency rating of 1075 MVA | 2023 ITP | Yes | Yes | 0.15063 | 2025-12-31 | 1534495 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.23846 | 2025-12-31 | 6255443 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.04224 | 2025-12-31 | 6255443 | 0
GEN-2023-097 | 01 NORTH | NRIS | 210675 | 144198 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Transformer | Install a 345/115 kV Transformer at the new East Fork 345/115 kV Substation. | 2021 ITP | Yes | Yes | 0.04378 | 2025-12-31 | 6255443 | 0
GEN-2023-038 | 04 SOUTHEAST | ERIS | 210617 | 143254 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Lexington - Lil Axe 138 kV | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04334 | 2025-12-31 | 7378510 | 7378510
GEN-2023-069 | 04 SOUTHEAST | ERIS | 210617 | 143254 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Lexington - Lil Axe 138 kV | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04217 | 2025-12-31 | 7378510 | 7378510
GEN-2023-174 | 04 SOUTHEAST | ERIS | 210617 | 143254 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Lexington - Lil Axe 138 kV | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.26776 | 2025-12-31 | 7378510 | 7378510
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210617 | 143254 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Lexington - Lil Axe 138 kV | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04592 | 2025-12-31 | 7378510 | 7378510
GEN-2023-069 | 04 SOUTHEAST | NRIS | 210617 | 143254 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Lexington - Lil Axe 138 kV | Rebuild 9.7 miles of 69 kV line from Lexington to Lil Axe to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.03452 | 2025-12-31 | 7378510 | 7378510
GEN-2023-062 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.04932 | 2025-12-31 | 17821363 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.29636 | 2025-12-31 | 17821363 | 0
GEN-2023-097 | 01 NORTH | NRIS | 210675 | 144171 | Multi - NE Williston - Folvag 115 kV - Judson - East Fork - Tande 345 kV | East Fork 345/115 kV Substation | Bisect the Judson to Tande 345 kV line approximately 18 miles from Judson and build a new 345 kV Substation. | 2021 ITP | Yes | Yes | 0.30511 | 2025-12-31 | 17821363 | 0
GEN-2023-116 | 02 NEBRASKA | ERIS | 220743 | 157595 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Ogallala 230 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Ogallala 230 kV substation on the Ogallala to Gerald Gentleman Station 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.08529 | 2026-01-01 | 103000 | 0
GEN-2023-117 | 02 NEBRASKA | ERIS | 220743 | 157595 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Ogallala 230 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Ogallala 230 kV substation on the Ogallala to Gerald Gentleman Station 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.08529 | 2026-01-01 | 103000 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 220743 | 157595 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Ogallala 230 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Ogallala 230 kV substation on the Ogallala to Gerald Gentleman Station 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.27669 | 2026-01-01 | 103000 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 220743 | 157595 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Ogallala 230 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Ogallala 230 kV substation on the Ogallala to Gerald Gentleman Station 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.25153 | 2026-01-01 | 103000 | 0
GEN-2023-199 | 02 NEBRASKA | NRIS | 220743 | 157595 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Ogallala 230 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Ogallala 230 kV substation on the Ogallala to Gerald Gentleman Station 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.0359 | 2026-01-01 | 103000 | 0
GEN-2023-222 | 02 NEBRASKA | NRIS | 220743 | 157595 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Ogallala 230 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Ogallala 230 kV substation on the Ogallala to Gerald Gentleman Station 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.03299 | 2026-01-01 | 103000 | 0
GEN-2023-223 | 02 NEBRASKA | NRIS | 220743 | 157595 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Ogallala 230 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Ogallala 230 kV substation on the Ogallala to Gerald Gentleman Station 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.03299 | 2026-01-01 | 103000 | 0
GEN-2023-011 | 02 NEBRASKA | ERIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.12554 | 2026-01-01 | 1173160 | 1173160
GEN-2023-222 | 02 NEBRASKA | ERIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.18455 | 2026-01-01 | 1173160 | 1173160
GEN-2023-223 | 02 NEBRASKA | ERIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.18455 | 2026-01-01 | 1173160 | 1173160
GEN-2023-224 | 02 NEBRASKA | ERIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.03049 | 2026-01-01 | 1173160 | 1173160
GEN-2023-225 | 02 NEBRASKA | ERIS | 210682 | 71967 | Multi - Sheldon - Monolith 115 kV | Sheldon - Monolith 115 kV Ckt 1 New Line | Re-terminate LES SW 7th & Bennet - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Construct new 115 kV line interconnections into Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.03049 | 2026-01-01 | 1173160 | 1173160
GEN-2023-116 | 02 NEBRASKA | ERIS | 220743 | 157594 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.08529 | 2026-01-01 | 1600000 | 0
GEN-2023-117 | 02 NEBRASKA | ERIS | 220743 | 157594 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.08529 | 2026-01-01 | 1600000 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 220743 | 157594 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.27669 | 2026-01-01 | 1600000 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 220743 | 157594 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.25153 | 2026-01-01 | 1600000 | 0
GEN-2023-199 | 02 NEBRASKA | NRIS | 220743 | 157594 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.0359 | 2026-01-01 | 1600000 | 0
GEN-2023-222 | 02 NEBRASKA | NRIS | 220743 | 157594 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.03299 | 2026-01-01 | 1600000 | 0
GEN-2023-223 | 02 NEBRASKA | NRIS | 220743 | 157594 | Multi- Gerald Gentleman Station - Ogallala 230 kV Terminal Upgrades | Gerald Gentleman Station - Ogallala 230 kV Line & Terminal Upgrades | Upgrade any necessary terminal equipment at Gerald Gentleman Station 230 kV substation on the Gerald Gentleman Station to Ogallala 230 kV line to achieve a summer emergency rating of 435 MVA. | 2023 ITP | Yes | Yes | 0.03299 | 2026-01-01 | 1600000 | 0
GEN-2023-011 | 02 NEBRASKA | ERIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.12155 | 2026-01-01 | 5468352 | 5468352
GEN-2023-222 | 02 NEBRASKA | ERIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.17888 | 2026-01-01 | 5468352 | 5468352
GEN-2023-223 | 02 NEBRASKA | ERIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.17888 | 2026-01-01 | 5468352 | 5468352
GEN-2023-224 | 02 NEBRASKA | ERIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.03472 | 2026-01-01 | 5468352 | 5468352
GEN-2023-225 | 02 NEBRASKA | ERIS | 200477 | 71965 | Multi - Sheldon - Monolith 115 kV | Monolith 345/115 kV Transformer #2 | Add a new 345/115 kV ckt 2 transformer at Monolith substation. | DPA-2016-December-703 | Yes | Yes | 0.03472 | 2026-01-01 | 5468352 | 5468352
GEN-2023-011 | 02 NEBRASKA | ERIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.12554 | 2026-01-01 | 5928037 | 5928037
GEN-2023-222 | 02 NEBRASKA | ERIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.18455 | 2026-01-01 | 5928037 | 5928037
GEN-2023-223 | 02 NEBRASKA | ERIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.18455 | 2026-01-01 | 5928037 | 5928037
GEN-2023-224 | 02 NEBRASKA | ERIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.03049 | 2026-01-01 | 5928037 | 5928037
GEN-2023-225 | 02 NEBRASKA | ERIS | 200477 | 71968 | Multi - Sheldon - Monolith 115 kV | Sheldon 115 kV Terminal Upgrades | Upgrade all terminal equipment in northern half of Sheldon 115 kV substation to achieve Sheldon - Monolith 115 kV line rating of no less than 400/400 MVA | DPA-2016-December-703 | Yes | Yes | 0.03049 | 2026-01-01 | 5928037 | 5928037
GEN-2023-011 | 02 NEBRASKA | ERIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.12554 | 2026-01-01 | 18617823 | 18617823
GEN-2023-222 | 02 NEBRASKA | ERIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.18455 | 2026-01-01 | 18617823 | 18617823
GEN-2023-223 | 02 NEBRASKA | ERIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.18455 | 2026-01-01 | 18617823 | 18617823
GEN-2023-224 | 02 NEBRASKA | ERIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03049 | 2026-01-01 | 18617823 | 18617823
GEN-2023-225 | 02 NEBRASKA | ERIS | 210682 | 71966 | Multi - Sheldon - Monolith 115 kV | Monolith 115 kV Substation Upgrades | Re-terminate Firth - Sheldon 115 kV line at Monolith 115 kV sub rather than Sheldon 115 kV sub. Install any necessary 115 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03049 | 2026-01-01 | 18617823 | 18617823
GEN-2023-012 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03325 | 2026-01-01 | 24319368 | 24319368
GEN-2023-082 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04457 | 2026-01-01 | 24319368 | 24319368
GEN-2023-097 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.0519 | 2026-01-01 | 24319368 | 24319368
GEN-2023-105 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.06224 | 2026-01-01 | 24319368 | 24319368
GEN-2023-154 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.0632 | 2026-01-01 | 24319368 | 24319368
GEN-2023-182 | 01 NORTH | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.0373 | 2026-01-01 | 24319368 | 24319368
GEN-2023-011 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.13152 | 2026-01-01 | 24319368 | 24319368
GEN-2023-116 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.10668 | 2026-01-01 | 24319368 | 24319368
GEN-2023-117 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.10668 | 2026-01-01 | 24319368 | 24319368
GEN-2023-133 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.12707 | 2026-01-01 | 24319368 | 24319368
GEN-2023-153 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.11454 | 2026-01-01 | 24319368 | 24319368
GEN-2023-199 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.05704 | 2026-01-01 | 24319368 | 24319368
GEN-2023-216 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.07317 | 2026-01-01 | 24319368 | 24319368
GEN-2023-217 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.07317 | 2026-01-01 | 24319368 | 24319368
GEN-2023-218 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.07317 | 2026-01-01 | 24319368 | 24319368
GEN-2023-222 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.24809 | 2026-01-01 | 24319368 | 24319368
GEN-2023-223 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.24809 | 2026-01-01 | 24319368 | 24319368
GEN-2023-224 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.74759 | 2026-01-01 | 24319368 | 24319368
GEN-2023-225 | 02 NEBRASKA | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.74759 | 2026-01-01 | 24319368 | 24319368
GEN-2023-015 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.0306 | 2026-01-01 | 24319368 | 24319368
GEN-2023-023 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04626 | 2026-01-01 | 24319368 | 24319368
GEN-2023-032 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04275 | 2026-01-01 | 24319368 | 24319368
GEN-2023-033 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04811 | 2026-01-01 | 24319368 | 24319368
GEN-2023-036 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04656 | 2026-01-01 | 24319368 | 24319368
GEN-2023-037 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04635 | 2026-01-01 | 24319368 | 24319368
GEN-2023-087 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03874 | 2026-01-01 | 24319368 | 24319368
GEN-2023-099 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03346 | 2026-01-01 | 24319368 | 24319368
GEN-2023-107 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04075 | 2026-01-01 | 24319368 | 24319368
GEN-2023-149 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03405 | 2026-01-01 | 24319368 | 24319368
GEN-2023-169 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04786 | 2026-01-01 | 24319368 | 24319368
GEN-2023-171 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04742 | 2026-01-01 | 24319368 | 24319368
GEN-2023-219 | 03 CENTRAL | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.03016 | 2026-01-01 | 24319368 | 24319368
GEN-2023-059 | 04 SOUTHEAST | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.05193 | 2026-01-01 | 24319368 | 24319368
GEN-2023-204 | 04 SOUTHEAST | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.05161 | 2026-01-01 | 24319368 | 24319368
GEN-2023-183 | 05 SOUTHWEST | ERIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.04275 | 2026-01-01 | 24319368 | 24319368
GEN-2023-222 | 02 NEBRASKA | NRIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.44096 | 2026-01-01 | 24319368 | 24319368
GEN-2023-223 | 02 NEBRASKA | NRIS | 200477 | 71963 | Multi - Sheldon - Monolith 115 kV | Monolith 345 kV Substation | Tap the existing 345 kV line from Moore to Cooper to construct the new Monolith substation approximately 1 mile from Moore. Install any necessary 345 kV terminal equipment. | DPA-2016-December-703 | Yes | Yes | 0.44096 | 2026-01-01 | 24319368 | 24319368
GEN-2023-082 | 01 NORTH | NRIS | 220828 | 170487 | Multi - Kingsbury County 115 Voltage Conversion | Arlington - Kingsbury County 115 kV Ckt 1 New Line | Build a 25-mile 115 kV Ckt 1 line from Arlington 115 kV substation to Kingsbury County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. | 2024 ITP | Yes | Yes | 0.06684 | 2026-02-02 | 10003000 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220828 | 170487 | Multi - Kingsbury County 115 Voltage Conversion | Arlington - Kingsbury County 115 kV Ckt 1 New Line | Build a 25-mile 115 kV Ckt 1 line from Arlington 115 kV substation to Kingsbury County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. | 2024 ITP | Yes | Yes | 0.45707 | 2026-02-02 | 10003000 | 0
GEN-2023-057 | 04 SOUTHEAST | ERIS | 210544 | 112460 | Multi - Sooner - Wekiwa 345 kV and Sand Springs - Sheffield 138 kV | Sand Springs - Sheffield Steel 138 kV Terminal Upgrades | Upgrade any necessary terminal equipment at Sand Springs and/or Sheffield Steel to increase the summer rating to 278 MVA | 2019 ITP | Yes | Yes | 0.03187 | 2026-02-26 | 1242638 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.17703 | 2026-02-28 | 5300000 | 5300000
GEN-2023-150 | 04 SOUTHEAST | ERIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.05776 | 2026-02-28 | 5300000 | 5300000
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.06081 | 2026-02-28 | 5300000 | 5300000
GEN-2023-174 | 04 SOUTHEAST | ERIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03469 | 2026-02-28 | 5300000 | 5300000
GEN-2023-229 | 04 SOUTHEAST | ERIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.05694 | 2026-02-28 | 5300000 | 5300000
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.16667 | 2026-02-28 | 5300000 | 5300000
GEN-2023-150 | 04 SOUTHEAST | NRIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.06075 | 2026-02-28 | 5300000 | 5300000
GEN-2023-161 | 04 SOUTHEAST | NRIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.05774 | 2026-02-28 | 5300000 | 5300000
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.03501 | 2026-02-28 | 5300000 | 5300000
GEN-2023-229 | 04 SOUTHEAST | NRIS | 210483 | 72027 | Multi - Park Community - Sunshine 138 kV | Cogar - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 10.6 mile 69 kV line from Cogar - El Reno Jct to 138 kV. | DPA-2017-August-767-774-776 | Yes | Yes | 0.0435 | 2026-02-28 | 5300000 | 5300000
GEN-2023-135 | 04 SOUTHEAST | ERIS | 220737 | 157268 | XFR - Turk 138/115 kV | Turk 138/115 kV Transformer Ckt 1 (138 kV) | Replace current 138/115 transformer Ckt 1 at Turk 138 kV substation to achieve a summer emergency rating of 250 MVA. | 2023 ITP | Yes | Yes | 0.0324 | 2026-03-01 | 5250000 | 0
GEN-2023-151 | 04 SOUTHEAST | ERIS | 220737 | 157268 | XFR - Turk 138/115 kV | Turk 138/115 kV Transformer Ckt 1 (138 kV) | Replace current 138/115 transformer Ckt 1 at Turk 138 kV substation to achieve a summer emergency rating of 250 MVA. | 2023 ITP | Yes | Yes | 0.03017 | 2026-03-01 | 5250000 | 0
GEN-2023-204 | 04 SOUTHEAST | ERIS | 220737 | 157268 | XFR - Turk 138/115 kV | Turk 138/115 kV Transformer Ckt 1 (138 kV) | Replace current 138/115 transformer Ckt 1 at Turk 138 kV substation to achieve a summer emergency rating of 250 MVA. | 2023 ITP | Yes | Yes | 0.03234 | 2026-03-01 | 5250000 | 0
GEN-2023-212 | 04 SOUTHEAST | ERIS | 220737 | 157268 | XFR - Turk 138/115 kV | Turk 138/115 kV Transformer Ckt 1 (138 kV) | Replace current 138/115 transformer Ckt 1 at Turk 138 kV substation to achieve a summer emergency rating of 250 MVA. | 2023 ITP | Yes | Yes | 0.04781 | 2026-03-01 | 5250000 | 0
GEN-2023-212 | 04 SOUTHEAST | NRIS | 220737 | 157268 | XFR - Turk 138/115 kV | Turk 138/115 kV Transformer Ckt 1 (138 kV) | Replace current 138/115 transformer Ckt 1 at Turk 138 kV substation to achieve a summer emergency rating of 250 MVA. | 2023 ITP | Yes | Yes | 0.04362 | 2026-03-01 | 5250000 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220828 | 170484 | Multi - Kingsbury County 115 Voltage Conversion | Manchester - Carpenter 115 kV Ckt 1 New Line | Build a 31.8-mile 115 kV Ckt 1 line from Manchester 115 kV substation to Carpenter 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. | 2024 ITP | Yes | Yes | 0.22439 | 2026-03-05 | 13326000 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03143 | 2026-05-01 | 8289302 | 0
GEN-2023-015 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08071 | 2026-05-01 | 8289302 | 0
GEN-2023-107 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0608 | 2026-05-01 | 8289302 | 0
GEN-2023-172 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06807 | 2026-05-01 | 8289302 | 0
GEN-2023-173 | 03 CENTRAL | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06807 | 2026-05-01 | 8289302 | 0
GEN-2023-009 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05527 | 2026-05-01 | 8289302 | 0
GEN-2023-022 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05394 | 2026-05-01 | 8289302 | 0
GEN-2023-030 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03413 | 2026-05-01 | 8289302 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.09112 | 2026-05-01 | 8289302 | 0
GEN-2023-038 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06215 | 2026-05-01 | 8289302 | 0
GEN-2023-059 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03699 | 2026-05-01 | 8289302 | 0
GEN-2023-059 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05347 | 2026-05-01 | 8289302 | 0
GEN-2023-069 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06033 | 2026-05-01 | 8289302 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04736 | 2026-05-01 | 8289302 | 0
GEN-2023-092 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05745 | 2026-05-01 | 8289302 | 0
GEN-2023-100 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.10192 | 2026-05-01 | 8289302 | 0
GEN-2023-101 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.38346 | 2026-05-01 | 8289302 | 0
GEN-2023-102 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.10192 | 2026-05-01 | 8289302 | 0
GEN-2023-104 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0858 | 2026-05-01 | 8289302 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0533 | 2026-05-01 | 8289302 | 0
GEN-2023-135 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04531 | 2026-05-01 | 8289302 | 0
GEN-2023-150 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.12838 | 2026-05-01 | 8289302 | 0
GEN-2023-151 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03805 | 2026-05-01 | 8289302 | 0
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04328 | 2026-05-01 | 8289302 | 0
GEN-2023-164 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.14916 | 2026-05-01 | 8289302 | 0
GEN-2023-165 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.14916 | 2026-05-01 | 8289302 | 0
GEN-2023-166 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05138 | 2026-05-01 | 8289302 | 0
GEN-2023-167 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05547 | 2026-05-01 | 8289302 | 0
GEN-2023-168 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05572 | 2026-05-01 | 8289302 | 0
GEN-2023-174 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08301 | 2026-05-01 | 8289302 | 0
GEN-2023-177 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06649 | 2026-05-01 | 8289302 | 0
GEN-2023-188 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.09529 | 2026-05-01 | 8289302 | 0
GEN-2023-193 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03827 | 2026-05-01 | 8289302 | 0
GEN-2023-204 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05968 | 2026-05-01 | 8289302 | 0
GEN-2023-205 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04431 | 2026-05-01 | 8289302 | 0
GEN-2023-210 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05213 | 2026-05-01 | 8289302 | 0
GEN-2023-212 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04518 | 2026-05-01 | 8289302 | 0
GEN-2023-227 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03892 | 2026-05-01 | 8289302 | 0
GEN-2023-229 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.13033 | 2026-05-01 | 8289302 | 0
GEN-2023-230 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03685 | 2026-05-01 | 8289302 | 0
GEN-2023-241 | 04 SOUTHEAST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03888 | 2026-05-01 | 8289302 | 0
GEN-2023-010 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.07893 | 2026-05-01 | 8289302 | 0
GEN-2023-110 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.21742 | 2026-05-01 | 8289302 | 0
GEN-2023-123 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.05831 | 2026-05-01 | 8289302 | 0
GEN-2023-176 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.1021 | 2026-05-01 | 8289302 | 0
GEN-2023-183 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.11917 | 2026-05-01 | 8289302 | 0
GEN-2023-237 | 05 SOUTHWEST | ERIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.11724 | 2026-05-01 | 8289302 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.0714 | 2026-05-01 | 8289302 | 0
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03225 | 2026-05-01 | 8289302 | 0
GEN-2023-100 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.1048 | 2026-05-01 | 8289302 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.33453 | 2026-05-01 | 8289302 | 0
GEN-2023-102 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.1048 | 2026-05-01 | 8289302 | 0
GEN-2023-104 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.14062 | 2026-05-01 | 8289302 | 0
GEN-2023-150 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.10463 | 2026-05-01 | 8289302 | 0
GEN-2023-164 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.12352 | 2026-05-01 | 8289302 | 0
GEN-2023-165 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.12352 | 2026-05-01 | 8289302 | 0
GEN-2023-177 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03372 | 2026-05-01 | 8289302 | 0
GEN-2023-188 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06025 | 2026-05-01 | 8289302 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04122 | 2026-05-01 | 8289302 | 0
GEN-2023-022 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04075 | 2026-05-01 | 8289302 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.08312 | 2026-05-01 | 8289302 | 0
GEN-2023-134 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.04515 | 2026-05-01 | 8289302 | 0
GEN-2023-229 | 04 SOUTHEAST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.03328 | 2026-05-01 | 8289302 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 210627 | 122796 | Multi - Border - Woodward 345 kV Tap | Chisholm Substation 345 kV Terminal Upgrades | Install any necessary terminal equipment to support a new line 345 kV line from Border - Woodward 345 kV substation with a summer emergency rating of 1792 MVA | 2020 ITP | Yes | Yes | 0.06023 | 2026-05-01 | 8289302 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 220737 | 157518 | Line - Pine & Peoria Tap 138 kV - 46Th Street Tap 138 kV-Tulsa North 138 kV Rebuild | Tulsa North 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Tulsa North 138 kV substation on the 46th Street Tap to Tulsa North 138 kV line to achieve a summer emergency rating of 278 MVA. | 2023 ITP | Yes | Yes | 0.04435 | 2026-05-02 | 150000 | 0
GEN-2023-063 | 04 SOUTHEAST | NRIS | 220737 | 157518 | Line - Pine & Peoria Tap 138 kV - 46Th Street Tap 138 kV-Tulsa North 138 kV Rebuild | Tulsa North 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Tulsa North 138 kV substation on the 46th Street Tap to Tulsa North 138 kV line to achieve a summer emergency rating of 278 MVA. | 2023 ITP | Yes | Yes | 0.04134 | 2026-05-02 | 150000 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220828 | 170468 | Multi - Kingsbury County 115 Voltage Conversion | Lake Preston - Kingsbury County 115 kV Ckt 1 New Line | Build a 5-mile 115 kV Ckt 1 line from Lake Preston 115 kV Ckt 1 line from Lake Preston 115 kV MOS to Kingsbury County 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. | 2024 ITP | Yes | Yes | 0.22439 | 2026-05-15 | 3406000 | 0
ASGI-2023-001 | 05 SOUTHWEST | ERIS | 220726 | 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs - Roadrunner 345 kV ckts 1 & 2 | Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.16403 | 2026-05-15 | 95479502 | 0
GEN-2023-001 | 05 SOUTHWEST | ERIS | 220726 | 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs - Roadrunner 345 kV ckts 1 & 2 | Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.03599 | 2026-05-15 | 95479502 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 220726 | 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs - Roadrunner 345 kV ckts 1 & 2 | Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.18143 | 2026-05-15 | 95479502 | 0
GEN-2023-236 | 05 SOUTHWEST | ERIS | 220726 | 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs - Roadrunner 345 kV ckts 1 & 2 | Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.03197 | 2026-05-15 | 95479502 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220726 | 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs - Roadrunner 345 kV ckts 1 & 2 | Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.07408 | 2026-05-15 | 95479502 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220726 | 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs - Roadrunner 345 kV ckts 1 & 2 | Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.03032 | 2026-05-15 | 95479502 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220726 | 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs - Roadrunner 345 kV ckts 1 & 2 | Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.05907 | 2026-05-15 | 95479502 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220726 | 156412 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Hobbs - Roadrunner 345 kV ckts 1 & 2 | Build a new 44.5 mile 345 kV double-circuit line from Hobbs 345 kV substation to Roadrunner 345 kV substation with a summer rating of at least 2640 MVA | 2021 ITP | Yes | Yes | 0.07158 | 2026-05-15 | 95479502 | 0
ASGI-2023-001 | 05 SOUTHWEST | ERIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.13167 | 2026-05-15 | 196135074 | 0
GEN-2023-001 | 05 SOUTHWEST | ERIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.12262 | 2026-05-15 | 196135074 | 0
GEN-2023-081 | 05 SOUTHWEST | ERIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.27457 | 2026-05-15 | 196135074 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.13535 | 2026-05-15 | 196135074 | 0
GEN-2023-201 | 05 SOUTHWEST | ERIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.20453 | 2026-05-15 | 196135074 | 0
GEN-2023-203 | 05 SOUTHWEST | ERIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.10941 | 2026-05-15 | 196135074 | 0
GEN-2023-236 | 05 SOUTHWEST | ERIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.16031 | 2026-05-15 | 196135074 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.03462 | 2026-05-15 | 196135074 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.08713 | 2026-05-15 | 196135074 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.28152 | 2026-05-15 | 196135074 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.18555 | 2026-05-15 | 196135074 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.07962 | 2026-05-15 | 196135074 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220726 | 156411 | Multi - Crossroads - Hobbs - Roadrunner 345 kV dbl ckt | Crossroads - Hobbs 345 kV ckts 1 & 2 | Build a new 90.5 mile 345 kV double-circuit line from Crossroads 345 kV substation to Hobbs 345 kV substation with a summer rating of at least 2640 MVA.. | 2021 ITP | Yes | Yes | 0.12772 | 2026-05-15 | 196135074 | 0
GEN-2023-205 | 04 SOUTHEAST | NRIS | 220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Yes | Yes | 0.09726 | 2026-05-31 | 736625 | 0
GEN-2023-210 | 04 SOUTHEAST | NRIS | 220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Yes | Yes | 0.03208 | 2026-05-31 | 736625 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Yes | Yes | 0.10547 | 2026-05-31 | 736625 | 0
GEN-2023-134 | 04 SOUTHEAST | NRIS | 220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Yes | Yes | 0.33917 | 2026-05-31 | 736625 | 0
GEN-2023-023 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.1044 | 2026-06-01 | 1329161 | 0
GEN-2023-033 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03832 | 2026-06-01 | 1329161 | 0
GEN-2023-037 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.10364 | 2026-06-01 | 1329161 | 0
GEN-2023-169 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03139 | 2026-06-01 | 1329161 | 0
GEN-2023-171 | 03 CENTRAL | ERIS | 220746 | 157203 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Lenexa South 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Lenexa South 161 kV substation on the Craig to Lenexa South 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03986 | 2026-06-01 | 1329161 | 0
GEN-2023-023 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.1044 | 2026-06-01 | 1329162 | 0
GEN-2023-033 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03832 | 2026-06-01 | 1329162 | 0
GEN-2023-037 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.10364 | 2026-06-01 | 1329162 | 0
GEN-2023-169 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03139 | 2026-06-01 | 1329162 | 0
GEN-2023-171 | 03 CENTRAL | ERIS | 220746 | 157202 | Sub - Craig 161 kV - Lenexa South 161 kV Ckt 2 Terminal Upgrades | Craig 161 kV Ckt 2 Terminal Upgrade | Upgrade any necessary terminal equipment at Craig 161 kV substation on the Lenexa South to Craig 161 kV line to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03986 | 2026-06-01 | 1329162 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220828 | 170479 | Multi - Kingsbury County 115 Voltage Conversion | Manchester - DeSmet 115 kV Ckt 1 New Line | Build a 12.5-mile 115 kV Ckt 1 line from Manchester 115 kV substation to DeSmet 115 kV MOS and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA. | 2024 ITP | Yes | Yes | 0.22439 | 2026-06-12 | 5718000 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220777 | 157296 | XFR-Phantom 345/115 kV Transformer & Capacitor Banks | XFR - Phantom 345/115 kV Transformer (345 kV) | Add new Phantom 345/115 kV transformer | DPA-2022-March-1564 | Yes | Yes | 0.06557 | 2026-06-15 | 2750988 | 2750988
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220777 | 159052 | XFR-Phantom 345/115 kV Transformer & Capacitor Banks | XFR - Phantom 345/115 kV Transformer (115 kV) | Add new Phantom 345/115 kV transformer | DPA-2022-March-1564 | Yes | Yes | 0.06557 | 2026-06-30 | 13138658 | 13138658
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Yes | Yes | 0.11165 | 2026-07-31 | 3500000 | 3500000
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Yes | Yes | 0.10849 | 2026-07-31 | 3500000 | 3500000
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Yes | Yes | 0.10083 | 2026-07-31 | 3500000 | 3500000
GEN-2023-161 | 04 SOUTHEAST | NRIS | 210483 | 72023 | Multi - Park Community - Sunshine 138 kV | El Reno - El Reno Jct 138 kV Ckt 1 Voltage Conversion | Convert 6.5 mile 69 kV line from El Reno - El Reno Jct to 138 kV. Complete necessary terminal upgrades at El Reno. | DPA-2017-August-767-774-776 | Yes | Yes | 0.10626 | 2026-07-31 | 3500000 | 3500000
GEN-2023-012 | 01 NORTH | NRIS | 220828 | 169974 | Multi - Madison, SD Area 115 kV System Voltage Conversion | Howard 115 kV New Substation | Install 115 kV new substation at Howard | 2024 ITP | Yes | Yes | 0.16888 | 2026-09-26 | 3795000 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220828 | 169975 | Multi - Madison, SD Area 115 kV System Voltage Conversion | Howard 115 kV New Substation | Install 115 kV new substation at Howard | 2024 ITP | Yes | Yes | 0.03375 | 2026-09-26 | 3795000 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.17918 | 2026-09-30 | 1170000 | 1170000
GEN-2023-150 | 04 SOUTHEAST | ERIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04501 | 2026-09-30 | 1170000 | 1170000
GEN-2023-174 | 04 SOUTHEAST | ERIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.2323 | 2026-09-30 | 1170000 | 1170000
GEN-2023-177 | 04 SOUTHEAST | ERIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.11541 | 2026-09-30 | 1170000 | 1170000
GEN-2023-210 | 04 SOUTHEAST | ERIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.03793 | 2026-09-30 | 1170000 | 1170000
GEN-2023-229 | 04 SOUTHEAST | ERIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.0522 | 2026-09-30 | 1170000 | 1170000
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.20807 | 2026-09-30 | 1170000 | 1170000
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.03112 | 2026-09-30 | 1170000 | 1170000
GEN-2023-150 | 04 SOUTHEAST | NRIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04845 | 2026-09-30 | 1170000 | 1170000
GEN-2023-177 | 04 SOUTHEAST | NRIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.10984 | 2026-09-30 | 1170000 | 1170000
GEN-2023-210 | 04 SOUTHEAST | NRIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.04239 | 2026-09-30 | 1170000 | 1170000
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.03074 | 2026-09-30 | 1170000 | 1170000
GEN-2023-229 | 04 SOUTHEAST | NRIS | 210617 | 143256 | Multi - Lil Axe - Lexington 138 kV Voltage Conversion | Canadian Switch138 kV Terminal Upgrades | Convert 69 kV terminal equipment at Canadian Switch to 138 kV | DPA-2020-May-1203 | Yes | Yes | 0.03359 | 2026-09-30 | 1170000 | 1170000
GEN-2023-012 | 01 NORTH | NRIS | 220828 | 170474 | Multi - Kingsbury County 115 Voltage Conversion | Lake Preston - DeSmet 115 kV Ckt 1 New Line | Build a 16-mile 115 kV Ckt 1 line from Lake Preston 115 kV MOS to DeSmet 115 kV MOS and upgrade any necessary terminal equipment to achieve a summer emergency rating of 193 MVA. | 2024 ITP | Yes | Yes | 0.22439 | 2026-10-30 | 6353000 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.17008 | 2026-11-30 | 385021 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.15391 | 2026-11-30 | 385021 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.04985 | 2026-11-30 | 385021 | 0
GEN-2023-097 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.15385 | 2026-11-30 | 385021 | 0
GEN-2023-012 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.04439 | 2026-11-30 | 385021 | 0
GEN-2023-105 | 01 NORTH | NRIS | 210675 | 144231 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad Switched Shunt | Install a switched shunt at Finstad. | 2021 ITP | Yes | Yes | 0.04917 | 2026-11-30 | 385021 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.16756 | 2026-11-30 | 5085047 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.16441 | 2026-11-30 | 5085047 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.03667 | 2026-11-30 | 5085047 | 0
GEN-2023-097 | 01 NORTH | NRIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.15385 | 2026-11-30 | 5085047 | 0
GEN-2023-012 | 01 NORTH | NRIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.04439 | 2026-11-30 | 5085047 | 0
GEN-2023-105 | 01 NORTH | NRIS | 210675 | 144238 | Multi - Tande - Finstad - Leland Olds 345 kV | Tande 345 kV Terminal Equipment | Install new terminal equipment at Tande to support a new 345 kV line from Finstad. Install a series compensation device at Finstad or Tande. | 2021 ITP | Yes | Yes | 0.04917 | 2026-11-30 | 5085047 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.17008 | 2026-11-30 | 10502349 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.15391 | 2026-11-30 | 10502349 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.04985 | 2026-11-30 | 10502349 | 0
GEN-2023-097 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.13756 | 2026-11-30 | 10502349 | 0
GEN-2023-012 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.04689 | 2026-11-30 | 10502349 | 0
GEN-2023-105 | 01 NORTH | NRIS | 210675 | 144237 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds 345 kV Substation | Build a new 345 kV Substation with terminal equipment to support a new line from Finstad 345 kV substation. | 2021 ITP | Yes | Yes | 0.05482 | 2026-11-30 | 10502349 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.17008 | 2026-11-30 | 18932308 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.15391 | 2026-11-30 | 18932308 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.04985 | 2026-11-30 | 18932308 | 0
GEN-2023-097 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.13756 | 2026-11-30 | 18932308 | 0
GEN-2023-012 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.04689 | 2026-11-30 | 18932308 | 0
GEN-2023-105 | 01 NORTH | NRIS | 210675 | 144230 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad 345 kV New Substation | Build a new 345 kV Substation including 345 kV terminals for lines from Leland Olds 345 kV substation, Tande 345 kV substation and high side terminal equipment for Finstad 345/115 kV Ckt 1 transformer and Finstad 345/115 kV Ckt 2 transformer | 2021 ITP | Yes | Yes | 0.05482 | 2026-11-30 | 18932308 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.16756 | 2026-11-30 | 85324831 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.16441 | 2026-11-30 | 85324831 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.03667 | 2026-11-30 | 85324831 | 0
GEN-2023-097 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.15385 | 2026-11-30 | 85324831 | 0
GEN-2023-012 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.04439 | 2026-11-30 | 85324831 | 0
GEN-2023-105 | 01 NORTH | NRIS | 210675 | 143714 | Multi - Tande - Finstad - Leland Olds 345 kV | Finstad - Tande 345 kV New Line | Build a 48 mile 345 kV line from Finstad to Tande. | 2021 ITP | Yes | Yes | 0.04917 | 2026-11-30 | 85324831 | 0
GEN-2023-097 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.13756 | 2026-11-30 | 220230034 | 0
GEN-2023-012 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.04689 | 2026-11-30 | 220230034 | 0
GEN-2023-105 | 01 NORTH | NRIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.05482 | 2026-11-30 | 220230034 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.17008 | 2026-11-30 | 220230034 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.15391 | 2026-11-30 | 220230034 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210675 | 144236 | Multi - Tande - Finstad - Leland Olds 345 kV | Leland Olds - Finstad - 345 kV New Line | Build a 123 mile 345 kV line from Leland Olds to Finstad. | 2021 ITP | Yes | Yes | 0.04985 | 2026-11-30 | 220230034 | 0
GEN-2023-057 | 04 SOUTHEAST | ERIS | 220774 | 157530 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Osage 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Osage 138 kV substation on the Osage to Webb City Tap 138 kV line to achieve a summer emergency rating of 561 MVA. | 2023 ITP | Yes | Yes | 0.12769 | 2026-12-01 | 1203344 | 0
GEN-2023-057 | 04 SOUTHEAST | NRIS | 220774 | 157530 | Line - Osage - Webb City Tap - Shidler 138 kV Rebuild | Osage 138 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Osage 138 kV substation on the Osage to Webb City Tap 138 kV line to achieve a summer emergency rating of 561 MVA. | 2023 ITP | Yes | Yes | 0.11119 | 2026-12-01 | 1203344 | 0
GEN-2023-001 | 05 SOUTHWEST | ERIS | 210714 | 156288 | Device - Lea Road 115 kV Capacitor Bank | Lea Road 115 kV Capacitor Bank | Install 28.8 MVAR capacitor bank at Lea Road 115 kV substation | 2022 ITP | Yes | Yes | 0.05024 | 2026-12-15 | 5048131 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 210714 | 156288 | Device - Lea Road 115 kV Capacitor Bank | Lea Road 115 kV Capacitor Bank | Install 28.8 MVAR capacitor bank at Lea Road 115 kV substation | 2022 ITP | Yes | Yes | 0.04898 | 2026-12-15 | 5048131 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.17703 | 2026-12-30 | 15333000 | 15333000
GEN-2023-150 | 04 SOUTHEAST | ERIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.05776 | 2026-12-30 | 15333000 | 15333000
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.06081 | 2026-12-30 | 15333000 | 15333000
GEN-2023-174 | 04 SOUTHEAST | ERIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03469 | 2026-12-30 | 15333000 | 15333000
GEN-2023-229 | 04 SOUTHEAST | ERIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.05694 | 2026-12-30 | 15333000 | 15333000
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.16667 | 2026-12-30 | 15333000 | 15333000
GEN-2023-150 | 04 SOUTHEAST | NRIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.06075 | 2026-12-30 | 15333000 | 15333000
GEN-2023-161 | 04 SOUTHEAST | NRIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.05774 | 2026-12-30 | 15333000 | 15333000
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03501 | 2026-12-30 | 15333000 | 15333000
GEN-2023-229 | 04 SOUTHEAST | NRIS | 210489 | 82111 | Line - Cogar - OU SW 138 kV | Cogar - Cleveland Jct 138 kV Ckt 1 Voltage Conversion | Convert 12.0 mile 69 kV line from Cogar - Cleveland Junction to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.0435 | 2026-12-30 | 15333000 | 15333000
GEN-2023-027 | 04 SOUTHEAST | ERIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12168 | 2026-12-31 | 730200 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03251 | 2026-12-31 | 730200 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.06484 | 2026-12-31 | 730200 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.37359 | 2026-12-31 | 730200 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.036 | 2026-12-31 | 730200 | 0
GEN-2023-027 | 04 SOUTHEAST | NRIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12122 | 2026-12-31 | 730200 | 0
GEN-2023-028 | 04 SOUTHEAST | NRIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.05083 | 2026-12-31 | 730200 | 0
GEN-2023-049 | 04 SOUTHEAST | NRIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.083 | 2026-12-31 | 730200 | 0
GEN-2023-055 | 04 SOUTHEAST | NRIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.39391 | 2026-12-31 | 730200 | 0
GEN-2023-213 | 04 SOUTHEAST | NRIS | 220741 | 156302 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03632 | 2026-12-31 | 730200 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12168 | 2026-12-31 | 730200 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03251 | 2026-12-31 | 730200 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.06484 | 2026-12-31 | 730200 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.37359 | 2026-12-31 | 730200 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.036 | 2026-12-31 | 730200 | 0
GEN-2023-027 | 04 SOUTHEAST | NRIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12122 | 2026-12-31 | 730200 | 0
GEN-2023-028 | 04 SOUTHEAST | NRIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.05083 | 2026-12-31 | 730200 | 0
GEN-2023-049 | 04 SOUTHEAST | NRIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.083 | 2026-12-31 | 730200 | 0
GEN-2023-055 | 04 SOUTHEAST | NRIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.39391 | 2026-12-31 | 730200 | 0
GEN-2023-213 | 04 SOUTHEAST | NRIS | 220741 | 156305 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr 161 kV Terminal Equipment Ckt 2 | Install any necessary terminal equipment at Kerr 161 kV substation to support the line from Kerr 161 kV substation to Maid 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03632 | 2026-12-31 | 730200 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.12168 | 2026-12-31 | 1107600 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.03251 | 2026-12-31 | 1107600 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.06484 | 2026-12-31 | 1107600 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.37359 | 2026-12-31 | 1107600 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.036 | 2026-12-31 | 1107600 | 0
GEN-2023-027 | 04 SOUTHEAST | NRIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.12122 | 2026-12-31 | 1107600 | 0
GEN-2023-028 | 04 SOUTHEAST | NRIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.05083 | 2026-12-31 | 1107600 | 0
GEN-2023-049 | 04 SOUTHEAST | NRIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.083 | 2026-12-31 | 1107600 | 0
GEN-2023-055 | 04 SOUTHEAST | NRIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.39391 | 2026-12-31 | 1107600 | 0
GEN-2023-213 | 04 SOUTHEAST | NRIS | 220741 | 156303 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Equipment | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA | 2023 ITP | Yes | Yes | 0.03632 | 2026-12-31 | 1107600 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12168 | 2026-12-31 | 1107600 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03251 | 2026-12-31 | 1107600 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.06484 | 2026-12-31 | 1107600 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.37359 | 2026-12-31 | 1107600 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.036 | 2026-12-31 | 1107600 | 0
GEN-2023-027 | 04 SOUTHEAST | NRIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12122 | 2026-12-31 | 1107600 | 0
GEN-2023-028 | 04 SOUTHEAST | NRIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.05083 | 2026-12-31 | 1107600 | 0
GEN-2023-049 | 04 SOUTHEAST | NRIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.083 | 2026-12-31 | 1107600 | 0
GEN-2023-055 | 04 SOUTHEAST | NRIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.39391 | 2026-12-31 | 1107600 | 0
GEN-2023-213 | 04 SOUTHEAST | NRIS | 220741 | 156306 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Maid 161 kV Terminal Upgrade Ckt 2 | Install any necessary terminal equipment at Maid 161 kV substation to support the line from Maid 161 kV substation to Kerr 161 kV substation with a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03632 | 2026-12-31 | 1107600 | 0
GEN-2023-012 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.0551 | 2026-12-31 | 1786830 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.0428 | 2026-12-31 | 1786830 | 0
GEN-2023-082 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05962 | 2026-12-31 | 1786830 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05372 | 2026-12-31 | 1786830 | 0
GEN-2023-105 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04805 | 2026-12-31 | 1786830 | 0
GEN-2023-154 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05511 | 2026-12-31 | 1786830 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05181 | 2026-12-31 | 1786830 | 0
GEN-2023-077 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.31179 | 2026-12-31 | 1786830 | 0
GEN-2023-078 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.31179 | 2026-12-31 | 1786830 | 0
GEN-2023-079 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.31179 | 2026-12-31 | 1786830 | 0
GEN-2023-199 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.07526 | 2026-12-31 | 1786830 | 0
GEN-2023-216 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.06482 | 2026-12-31 | 1786830 | 0
GEN-2023-217 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.06482 | 2026-12-31 | 1786830 | 0
GEN-2023-218 | 02 NEBRASKA | ERIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.06482 | 2026-12-31 | 1786830 | 0
GEN-2023-216 | 02 NEBRASKA | NRIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03294 | 2026-12-31 | 1786830 | 0
GEN-2023-217 | 02 NEBRASKA | NRIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03294 | 2026-12-31 | 1786830 | 0
GEN-2023-218 | 02 NEBRASKA | NRIS | 210680 | 143662 | Line - S3454 - S3740 345 kV | S3740 345 kV Terminal Upgrades | Install terminal equipment at S3740 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03294 | 2026-12-31 | 1786830 | 0
GEN-2023-012 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05635 | 2026-12-31 | 2070042 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05166 | 2026-12-31 | 2070042 | 0
GEN-2023-082 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.06142 | 2026-12-31 | 2070042 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04986 | 2026-12-31 | 2070042 | 0
GEN-2023-105 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03879 | 2026-12-31 | 2070042 | 0
GEN-2023-154 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04994 | 2026-12-31 | 2070042 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04993 | 2026-12-31 | 2070042 | 0
GEN-2023-011 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03317 | 2026-12-31 | 2070042 | 0
GEN-2023-077 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.08969 | 2026-12-31 | 2070042 | 0
GEN-2023-078 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.08969 | 2026-12-31 | 2070042 | 0
GEN-2023-079 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.08969 | 2026-12-31 | 2070042 | 0
GEN-2023-199 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.08315 | 2026-12-31 | 2070042 | 0
GEN-2023-216 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05882 | 2026-12-31 | 2070042 | 0
GEN-2023-217 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05882 | 2026-12-31 | 2070042 | 0
GEN-2023-218 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.05882 | 2026-12-31 | 2070042 | 0
GEN-2023-222 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03579 | 2026-12-31 | 2070042 | 0
GEN-2023-223 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.03579 | 2026-12-31 | 2070042 | 0
GEN-2023-224 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04183 | 2026-12-31 | 2070042 | 0
GEN-2023-225 | 02 NEBRASKA | ERIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04183 | 2026-12-31 | 2070042 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04888 | 2026-12-31 | 2070042 | 0
GEN-2023-199 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.0866 | 2026-12-31 | 2070042 | 0
GEN-2023-222 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04411 | 2026-12-31 | 2070042 | 0
GEN-2023-223 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.04411 | 2026-12-31 | 2070042 | 0
GEN-2023-216 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.06918 | 2026-12-31 | 2070042 | 0
GEN-2023-217 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.06918 | 2026-12-31 | 2070042 | 0
GEN-2023-218 | 02 NEBRASKA | NRIS | 210680 | 143661 | Line - S3454 - S3740 345 kV | S3454 345 kV Terminal Upgrades | Install terminal equipment at S3454 substation 345 kV to support a new 345 kV line from S3454 to S3740. | 2021 ITP | Yes | Yes | 0.06918 | 2026-12-31 | 2070042 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12168 | 2026-12-31 | 5846250 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03251 | 2026-12-31 | 5846250 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.06484 | 2026-12-31 | 5846250 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.37359 | 2026-12-31 | 5846250 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.036 | 2026-12-31 | 5846250 | 0
GEN-2023-027 | 04 SOUTHEAST | NRIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12122 | 2026-12-31 | 5846250 | 0
GEN-2023-028 | 04 SOUTHEAST | NRIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.05083 | 2026-12-31 | 5846250 | 0
GEN-2023-049 | 04 SOUTHEAST | NRIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.083 | 2026-12-31 | 5846250 | 0
GEN-2023-055 | 04 SOUTHEAST | NRIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.39391 | 2026-12-31 | 5846250 | 0
GEN-2023-213 | 04 SOUTHEAST | NRIS | 220741 | 156301 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 1 Rebuild #2 | Rebuild 5.5 miles of 161 kV Ckt 1 line from Kerr 161 kV substation to Maid 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03632 | 2026-12-31 | 5846250 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12168 | 2026-12-31 | 5846250 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03251 | 2026-12-31 | 5846250 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.06484 | 2026-12-31 | 5846250 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.37359 | 2026-12-31 | 5846250 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.036 | 2026-12-31 | 5846250 | 0
GEN-2023-027 | 04 SOUTHEAST | NRIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.12122 | 2026-12-31 | 5846250 | 0
GEN-2023-028 | 04 SOUTHEAST | NRIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.05083 | 2026-12-31 | 5846250 | 0
GEN-2023-049 | 04 SOUTHEAST | NRIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.083 | 2026-12-31 | 5846250 | 0
GEN-2023-055 | 04 SOUTHEAST | NRIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.39391 | 2026-12-31 | 5846250 | 0
GEN-2023-213 | 04 SOUTHEAST | NRIS | 220741 | 156304 | Line - Kerr 161 kV - Maid 161 kV Ckt 1 & Ckt 2 Rebuild | Kerr - Maid 161 kV Ckt 2 Rebuild | Rebuild 5.5 miles of 161 kV Ckt 2 line from Kerr 161 kV to Maid 161 kV and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2023 ITP | Yes | Yes | 0.03632 | 2026-12-31 | 5846250 | 0
GEN-2023-023 | 03 CENTRAL | ERIS | 220816 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Transformer Ckt 2 (161 kV) | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.05565 | 2026-12-31 | 9823936 | 0
GEN-2023-032 | 03 CENTRAL | ERIS | 220816 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Transformer Ckt 2 (161 kV) | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.03694 | 2026-12-31 | 9823936 | 0
GEN-2023-033 | 03 CENTRAL | ERIS | 220816 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Transformer Ckt 2 (161 kV) | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.05726 | 2026-12-31 | 9823936 | 0
GEN-2023-036 | 03 CENTRAL | ERIS | 220816 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Transformer Ckt 2 (161 kV) | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.04665 | 2026-12-31 | 9823936 | 0
GEN-2023-037 | 03 CENTRAL | ERIS | 220816 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Transformer Ckt 2 (161 kV) | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.06247 | 2026-12-31 | 9823936 | 0
GEN-2023-169 | 03 CENTRAL | ERIS | 220816 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Transformer Ckt 2 (161 kV) | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.0477 | 2026-12-31 | 9823936 | 0
GEN-2023-171 | 03 CENTRAL | ERIS | 220816 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Transformer Ckt 2 (161 kV) | Install a second Nashua 345/161 kV Transformer to achieve a minimum rating of 650/715 MVA | 2024 ITP | Yes | Yes | 0.04075 | 2026-12-31 | 9823936 | 0
GEN-2023-033 | 03 CENTRAL | NRIS | 220816 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Transformer Ckt 2 (161 kV) | Install new 345/161 transformer at Nashua 161 kV substation | 2024 ITP | Yes | Yes | 0.04424 | 2026-12-31 | 9823936 | 0
GEN-2023-169 | 03 CENTRAL | NRIS | 220816 | 170428 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Transformer Ckt 2 (161 kV) | Install new 345/161 transformer at Nashua 161 kV substation | 2024 ITP | Yes | Yes | 0.03409 | 2026-12-31 | 9823936 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.54826 | 2026-12-31 | 12224000 | 12224000
GEN-2023-150 | 04 SOUTHEAST | ERIS | 210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.04304 | 2026-12-31 | 12224000 | 12224000
GEN-2023-174 | 04 SOUTHEAST | ERIS | 210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.0425 | 2026-12-31 | 12224000 | 12224000
GEN-2023-229 | 04 SOUTHEAST | ERIS | 210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03944 | 2026-12-31 | 12224000 | 12224000
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.56086 | 2026-12-31 | 12224000 | 12224000
GEN-2023-150 | 04 SOUTHEAST | NRIS | 210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.04456 | 2026-12-31 | 12224000 | 12224000
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.04219 | 2026-12-31 | 12224000 | 12224000
GEN-2023-229 | 04 SOUTHEAST | NRIS | 210489 | 82112 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Amber Tap 138 kV Ckt 1 Voltage Conversion | Convert 13.8 mile 69 kV line from Cleveland Jct - Amber Tap to 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03311 | 2026-12-31 | 12224000 | 12224000
GEN-2023-077 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.32055 | 2026-12-31 | 64071687 | 0
GEN-2023-078 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.32055 | 2026-12-31 | 64071687 | 0
GEN-2023-079 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.32055 | 2026-12-31 | 64071687 | 0
GEN-2023-199 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03833 | 2026-12-31 | 64071687 | 0
GEN-2023-216 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03533 | 2026-12-31 | 64071687 | 0
GEN-2023-217 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03533 | 2026-12-31 | 64071687 | 0
GEN-2023-218 | 02 NEBRASKA | ERIS | 210680 | 143660 | Line - S3454 - S3740 345 kV | S3454 - S3740 345 kV New Line | Build an approximately 29 mile 345 kV line from S3454 to S3740 Ckt 1. | 2021 ITP | Yes | Yes | 0.03533 | 2026-12-31 | 64071687 | 0
GEN-2023-077 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03413 | 2027-01-01 | 114179 | 0
GEN-2023-078 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03413 | 2027-01-01 | 114179 | 0
GEN-2023-079 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03413 | 2027-01-01 | 114179 | 0
GEN-2023-222 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.0304 | 2027-01-01 | 114179 | 0
GEN-2023-223 | 02 NEBRASKA | ERIS | 220744 | 157386 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Sub 1214 161 kV substation on the 70th & Bluff to Sub 1214 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.0304 | 2027-01-01 | 114179 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.37123 | 2027-02-28 | 9932652 | 9932652
GEN-2023-150 | 04 SOUTHEAST | ERIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.1008 | 2027-02-28 | 9932652 | 9932652
GEN-2023-161 | 04 SOUTHEAST | ERIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.04227 | 2027-02-28 | 9932652 | 9932652
GEN-2023-229 | 04 SOUTHEAST | ERIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.09638 | 2027-02-28 | 9932652 | 9932652
GEN-2023-035 | 04 SOUTHEAST | NRIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.3942 | 2027-02-28 | 9932652 | 9932652
GEN-2023-150 | 04 SOUTHEAST | NRIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.10531 | 2027-02-28 | 9932652 | 9932652
GEN-2023-161 | 04 SOUTHEAST | NRIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03755 | 2027-02-28 | 9932652 | 9932652
GEN-2023-210 | 04 SOUTHEAST | NRIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.03505 | 2027-02-28 | 9932652 | 9932652
GEN-2023-088 | 04 SOUTHEAST | NRIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.0772 | 2027-02-28 | 9932652 | 9932652
GEN-2023-229 | 04 SOUTHEAST | NRIS | 210489 | 82115 | Line - Cogar - OU SW 138 kV | Cleveland Jct - Anadarko 138 kV Ckt 1 Voltage Conversion | Convert 11.1 miles of double circuit 69 kV line from Cleveland Junction - Anadarko to single circuit 138 kV. | DPA-2017-December-815 | Yes | Yes | 0.07661 | 2027-02-28 | 9932652 | 9932652
GEN-2023-010 | 05 SOUTHWEST | ERIS | 220750 | 157377 | Sub - Moore Co 115 kV Terminal Upgrade | Moore Co 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Moore Co 115 kV substation to achieve a summer emergency rating of 175 MVA. | 2023 ITP | Yes | Yes | 0.03634 | 2027-03-15 | 4117021 | 0
GEN-2023-082 | 01 NORTH | NRIS | 220748 | 157948 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.14479 | 2027-04-01 | 264000 | 0
GEN-2023-216 | 02 NEBRASKA | NRIS | 220748 | 157948 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.07145 | 2027-04-01 | 264000 | 0
GEN-2023-217 | 02 NEBRASKA | NRIS | 220748 | 157948 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.07145 | 2027-04-01 | 264000 | 0
GEN-2023-218 | 02 NEBRASKA | NRIS | 220748 | 157948 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point 115 kV Terminal Upgrade | Upgrade any necessary terminal equipment at Gavin Point 115 kV substation on the Gavins Point to Yankton Junction 115 kV line to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.07145 | 2027-04-01 | 264000 | 0
GEN-2023-061 | 03 CENTRAL | ERIS | 220871 | 170416 | XFR - Catoosa 161/138 kV | Catoosa 161 kV Terminal Equipment | Install any necessary terminal equipment to support 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.03682 | 2027-04-01 | 453000 | 0
GEN-2023-194 | 03 CENTRAL | ERIS | 220871 | 170416 | XFR - Catoosa 161/138 kV | Catoosa 161 kV Terminal Equipment | Install any necessary terminal equipment to support 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.03405 | 2027-04-01 | 453000 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220871 | 170416 | XFR - Catoosa 161/138 kV | Catoosa 161 kV Terminal Equipment | Install any necessary terminal equipment to support 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.14243 | 2027-04-01 | 453000 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220871 | 170416 | XFR - Catoosa 161/138 kV | Catoosa 161 kV Terminal Equipment | Install any necessary terminal equipment to support 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.13462 | 2027-04-01 | 453000 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220871 | 170416 | XFR - Catoosa 161/138 kV | Catoosa 161 kV Terminal Equipment | Install any necessary terminal equipment to support 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.14639 | 2027-04-01 | 453000 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 220871 | 170416 | XFR - Catoosa 161/138 kV | Catoosa 161 kV Terminal Equipment | Install any necessary terminal equipment to support 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.21165 | 2027-04-01 | 453000 | 0
GEN-2023-138 | 04 SOUTHEAST | ERIS | 220871 | 170416 | XFR - Catoosa 161/138 kV | Catoosa 161 kV Terminal Equipment | Install any necessary terminal equipment to support 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.08809 | 2027-04-01 | 453000 | 0
GEN-2023-213 | 04 SOUTHEAST | ERIS | 220871 | 170416 | XFR - Catoosa 161/138 kV | Catoosa 161 kV Terminal Equipment | Install any necessary terminal equipment to support 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.04803 | 2027-04-01 | 453000 | 0
GEN-2023-082 | 01 NORTH | NRIS | 220748 | 157946 | Line - Gavins Point 115 kV - Yankton Junction 115 kV Rebuild | Gavins Point - Yankton Junction 115 kV Ckt 1 Rebuild (WAPA) | Rebuild 4 miles of 115 kV Ckt 1 line from Gavins Point 115 kV substation to Yankton Junction 115 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 239 MVA. | 2023 ITP | Yes | Yes | 0.14479 | 2027-04-01 | 2539625 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220871 | 170191 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (GRDA) | Switch in the 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.04655 | 2027-04-01 | 7641150 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220871 | 170191 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (GRDA) | Switch in the 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.044 | 2027-04-01 | 7641150 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220871 | 170191 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (GRDA) | Switch in the 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.04785 | 2027-04-01 | 7641150 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 220871 | 170191 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (GRDA) | Switch in the 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.06917 | 2027-04-01 | 7641150 | 0
GEN-2023-063 | 04 SOUTHEAST | NRIS | 220871 | 170191 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (GRDA) | Switch in the 161/138 transformer at Catoosa 161 kV substation with a summer emergency rating of 96 MVA. | 2024 ITP | Yes | Yes | 0.06429 | 2027-04-01 | 7641150 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 210708 | 156300 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis 138 kV Ckt 1 Terminal Upgrade | Replace wave traps at 36th & Lewis 138 kV substation | 2022 ITP | Yes | Yes | 0.04032 | 2027-06-01 | 540691 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 210708 | 156300 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis 138 kV Ckt 1 Terminal Upgrade | Replace wave traps at 36th & Lewis 138 kV substation | 2022 ITP | Yes | Yes | 0.06232 | 2027-06-01 | 540691 | 0
GEN-2023-027 | 04 SOUTHEAST | NRIS | 210708 | 156300 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis 138 kV Ckt 1 Terminal Upgrade | Replace wave traps at 36th & Lewis 138 kV substation | 2022 ITP | Yes | Yes | 0.04682 | 2027-06-01 | 540691 | 0
GEN-2023-063 | 04 SOUTHEAST | NRIS | 210708 | 156300 | Line - 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | 36th & Lewis 138 kV Ckt 1 Terminal Upgrade | Replace wave traps at 36th & Lewis 138 kV substation | 2022 ITP | Yes | Yes | 0.06883 | 2027-06-01 | 540691 | 0
GEN-2023-100 | 04 SOUTHEAST | ERIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.03982 | 2027-10-30 | 1200000 | 0
GEN-2023-102 | 04 SOUTHEAST | ERIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.03982 | 2027-10-30 | 1200000 | 0
GEN-2023-104 | 04 SOUTHEAST | ERIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.09318 | 2027-10-30 | 1200000 | 0
GEN-2023-161 | 04 SOUTHEAST | ERIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.03407 | 2027-10-30 | 1200000 | 0
GEN-2023-009 | 04 SOUTHEAST | NRIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.05765 | 2027-10-30 | 1200000 | 0
GEN-2023-035 | 04 SOUTHEAST | NRIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.04997 | 2027-10-30 | 1200000 | 0
GEN-2023-069 | 04 SOUTHEAST | NRIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.05647 | 2027-10-30 | 1200000 | 0
GEN-2023-092 | 04 SOUTHEAST | NRIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.05737 | 2027-10-30 | 1200000 | 0
GEN-2023-100 | 04 SOUTHEAST | NRIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.04551 | 2027-10-30 | 1200000 | 0
GEN-2023-102 | 04 SOUTHEAST | NRIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.04551 | 2027-10-30 | 1200000 | 0
GEN-2023-104 | 04 SOUTHEAST | NRIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.15122 | 2027-10-30 | 1200000 | 0
GEN-2023-210 | 04 SOUTHEAST | NRIS | 200419 | 51531 | Multi - DeGrasse - Knob Hill 138 kV New Line and DeGrasse 345/138 kV Transformer | DeGrasse 138 kV Substation (WFEC) | Tap the existing 138 kV line from Mooreland to Rose Valley and terminate both end points into the new DeGrasse substation. WFEC and Oklahoma Gas and Electric Company shall decide who shall build how much of these Network Upgrades and shall provide such information, along with specific cost estimates for each DTO's portion of the Network Upgrades, to SPP in its response to this NTC. | 2016 ITPNT | Yes | Yes | 0.05586 | 2027-10-30 | 1200000 | 0
GEN-2023-012 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03411 | 2027-12-31 | 842000 | 0
GEN-2023-062 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.06232 | 2027-12-31 | 842000 | 0
GEN-2023-082 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03645 | 2027-12-31 | 842000 | 0
GEN-2023-097 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04274 | 2027-12-31 | 842000 | 0
GEN-2023-105 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.07572 | 2027-12-31 | 842000 | 0
GEN-2023-154 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.05717 | 2027-12-31 | 842000 | 0
GEN-2023-182 | 01 NORTH | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03906 | 2027-12-31 | 842000 | 0
GEN-2023-077 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03736 | 2027-12-31 | 842000 | 0
GEN-2023-078 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03736 | 2027-12-31 | 842000 | 0
GEN-2023-079 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03736 | 2027-12-31 | 842000 | 0
GEN-2023-116 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.12296 | 2027-12-31 | 842000 | 0
GEN-2023-117 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.12296 | 2027-12-31 | 842000 | 0
GEN-2023-133 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04142 | 2027-12-31 | 842000 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.11183 | 2027-12-31 | 842000 | 0
GEN-2023-222 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03559 | 2027-12-31 | 842000 | 0
GEN-2023-223 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03559 | 2027-12-31 | 842000 | 0
GEN-2023-224 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03723 | 2027-12-31 | 842000 | 0
GEN-2023-225 | 02 NEBRASKA | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03723 | 2027-12-31 | 842000 | 0
GEN-2023-107 | 03 CENTRAL | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.04321 | 2027-12-31 | 842000 | 0
GEN-2023-172 | 03 CENTRAL | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03112 | 2027-12-31 | 842000 | 0
GEN-2023-173 | 03 CENTRAL | ERIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.03112 | 2027-12-31 | 842000 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.15819 | 2027-12-31 | 842000 | 0
GEN-2023-199 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.12703 | 2027-12-31 | 842000 | 0
GEN-2023-222 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.09465 | 2027-12-31 | 842000 | 0
GEN-2023-223 | 02 NEBRASKA | NRIS | 210618 | 50446 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Holt Co. Substation 345 kV | Add line bay terminal equipment as necessary to connect, commission and operate the 345 kV line from Thedford to Holt County Substation. | 2012 ITP10 | Yes | Yes | 0.09465 | 2027-12-31 | 842000 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.04193 | 2027-12-31 | 2177750 | 0
GEN-2023-150 | 04 SOUTHEAST | ERIS | 220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.06865 | 2027-12-31 | 2177750 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.04982 | 2027-12-31 | 2177750 | 0
GEN-2023-035 | 04 SOUTHEAST | NRIS | 220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.04028 | 2027-12-31 | 2177750 | 0
GEN-2023-150 | 04 SOUTHEAST | NRIS | 220774 | 157395 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ck 2 Terminal Upgrade | Install any necessary terminal equipment at Gracemont 138 kV substation to support a second line from Gracemont to Anadarko 138 kV substation with a summer emergency rating of 286 MVA. | 2023 ITP | Yes | Yes | 0.06736 | 2027-12-31 | 2177750 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 220774 | 158637 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Gracemont 138 kV substation to support a third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA | 2023 ITP | Yes | Yes | 0.04193 | 2027-12-31 | 2177750 | 0
GEN-2023-150 | 04 SOUTHEAST | ERIS | 220774 | 158637 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Gracemont 138 kV substation to support a third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA | 2023 ITP | Yes | Yes | 0.06865 | 2027-12-31 | 2177750 | 0
GEN-2023-035 | 04 SOUTHEAST | NRIS | 220774 | 158637 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Gracemont 138 kV substation to support a third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA | 2023 ITP | Yes | Yes | 0.04028 | 2027-12-31 | 2177750 | 0
GEN-2023-150 | 04 SOUTHEAST | NRIS | 220774 | 158637 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Gracemont 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Gracemont 138 kV substation to support a third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA | 2023 ITP | Yes | Yes | 0.06736 | 2027-12-31 | 2177750 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220828 | 170490/170491 | Multi - Kingsbury County 115 Voltage Conversion | Carpenter 230/115 kV Transformer Ckt 1 (115 kV) | Install new 230/115 transformer at Carpenter 115 kV substation | 2024 ITP | Yes | Yes | 0.22439 | 2027-12-31 | 4317000 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 220774 | 157879 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138 kV Ckt 3 New Line (OGE) | Build new 15 mile 138 kV Ckt 3 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.04193 | 2027-12-31 | 10000000 | 0
GEN-2023-150 | 04 SOUTHEAST | ERIS | 220774 | 157879 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138 kV Ckt 3 New Line (OGE) | Build new 15 mile 138 kV Ckt 3 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.06865 | 2027-12-31 | 10000000 | 0
GEN-2023-035 | 04 SOUTHEAST | NRIS | 220774 | 157879 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138 kV Ckt 3 New Line (OGE) | Build new 15 mile 138 kV Ckt 3 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.04028 | 2027-12-31 | 10000000 | 0
GEN-2023-150 | 04 SOUTHEAST | NRIS | 220774 | 157879 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138 kV Ckt 3 New Line (OGE) | Build new 15 mile 138 kV Ckt 3 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.06736 | 2027-12-31 | 10000000 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.04193 | 2027-12-31 | 10000000 | 0
GEN-2023-150 | 04 SOUTHEAST | ERIS | 220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.06865 | 2027-12-31 | 10000000 | 0
GEN-2023-035 | 04 SOUTHEAST | NRIS | 220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.04028 | 2027-12-31 | 10000000 | 0
GEN-2023-150 | 04 SOUTHEAST | NRIS | 220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.06736 | 2027-12-31 | 10000000 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 220774 | 157897 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko - Gracemont 138kV Ckt 2 New Line (OGE) | Build new 15-mile 138 kV Ckt 2 line from Anadarko 138 kV substation to Gracemont 138 kV substation as a double circuit to achieve a summer emergency rating of 478 MVA. | 2023 ITP | Yes | Yes | 0.04982 | 2027-12-31 | 10000000 | 0
GEN-2023-038 | 04 SOUTHEAST | NRIS | 210586 | 112443 | Line - Russett - South Brown 138 kV | Russett - South Brown 138 kV Ckt 1 Rebuild | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 2020 ITP | Yes | Yes | 0.06611 | 2027-12-31 | 10267390 | 0
GEN-2023-069 | 04 SOUTHEAST | NRIS | 210586 | 112443 | Line - Russett - South Brown 138 kV | Russett - South Brown 138 kV Ckt 1 Rebuild | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 2020 ITP | Yes | Yes | 0.05931 | 2027-12-31 | 10267390 | 0
GEN-2023-092 | 04 SOUTHEAST | NRIS | 210586 | 112443 | Line - Russett - South Brown 138 kV | Russett - South Brown 138 kV Ckt 1 Rebuild | Rebuild 18.62 miles of 138 kV line from Russett to South Brown and upgrade terminal equipment at South Brown as needed to achieve a summer emergency rating of 234 MVA | 2020 ITP | Yes | Yes | 0.07661 | 2027-12-31 | 10267390 | 0
GEN-2023-012 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03898 | 2027-12-31 | 16186000 | 0
GEN-2023-062 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.06152 | 2027-12-31 | 16186000 | 0
GEN-2023-082 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04114 | 2027-12-31 | 16186000 | 0
GEN-2023-097 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04648 | 2027-12-31 | 16186000 | 0
GEN-2023-105 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.07463 | 2027-12-31 | 16186000 | 0
GEN-2023-154 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.06037 | 2027-12-31 | 16186000 | 0
GEN-2023-182 | 01 NORTH | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.0431 | 2027-12-31 | 16186000 | 0
GEN-2023-077 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03457 | 2027-12-31 | 16186000 | 0
GEN-2023-078 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03457 | 2027-12-31 | 16186000 | 0
GEN-2023-079 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03457 | 2027-12-31 | 16186000 | 0
GEN-2023-116 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.13471 | 2027-12-31 | 16186000 | 0
GEN-2023-117 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.13471 | 2027-12-31 | 16186000 | 0
GEN-2023-133 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.05143 | 2027-12-31 | 16186000 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.11605 | 2027-12-31 | 16186000 | 0
GEN-2023-199 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03228 | 2027-12-31 | 16186000 | 0
GEN-2023-222 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03061 | 2027-12-31 | 16186000 | 0
GEN-2023-223 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03061 | 2027-12-31 | 16186000 | 0
GEN-2023-224 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03225 | 2027-12-31 | 16186000 | 0
GEN-2023-225 | 02 NEBRASKA | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03225 | 2027-12-31 | 16186000 | 0
GEN-2023-015 | 03 CENTRAL | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03281 | 2027-12-31 | 16186000 | 0
GEN-2023-107 | 03 CENTRAL | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04613 | 2027-12-31 | 16186000 | 0
GEN-2023-172 | 03 CENTRAL | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03313 | 2027-12-31 | 16186000 | 0
GEN-2023-173 | 03 CENTRAL | ERIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03313 | 2027-12-31 | 16186000 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.16064 | 2027-12-31 | 16186000 | 0
GEN-2023-199 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.12703 | 2027-12-31 | 16186000 | 0
GEN-2023-222 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.09465 | 2027-12-31 | 16186000 | 0
GEN-2023-223 | 02 NEBRASKA | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.09465 | 2027-12-31 | 16186000 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03011 | 2027-12-31 | 16186000 | 0
GEN-2023-105 | 01 NORTH | NRIS | 200220 | 50444 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. Substation 345 kV | Build new Cherry County 345 kV substation and install necessary terminal equipment. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04159 | 2027-12-31 | 16186000 | 0
GEN-2023-012 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03898 | 2027-12-31 | 224639813 | 0
GEN-2023-062 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.06152 | 2027-12-31 | 224639813 | 0
GEN-2023-082 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04114 | 2027-12-31 | 224639813 | 0
GEN-2023-097 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04648 | 2027-12-31 | 224639813 | 0
GEN-2023-105 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.07463 | 2027-12-31 | 224639813 | 0
GEN-2023-154 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.06037 | 2027-12-31 | 224639813 | 0
GEN-2023-182 | 01 NORTH | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.0431 | 2027-12-31 | 224639813 | 0
GEN-2023-077 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03457 | 2027-12-31 | 224639813 | 0
GEN-2023-078 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03457 | 2027-12-31 | 224639813 | 0
GEN-2023-079 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03457 | 2027-12-31 | 224639813 | 0
GEN-2023-116 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.13471 | 2027-12-31 | 224639813 | 0
GEN-2023-117 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.13471 | 2027-12-31 | 224639813 | 0
GEN-2023-133 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.05143 | 2027-12-31 | 224639813 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.11605 | 2027-12-31 | 224639813 | 0
GEN-2023-199 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03228 | 2027-12-31 | 224639813 | 0
GEN-2023-222 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03061 | 2027-12-31 | 224639813 | 0
GEN-2023-223 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03061 | 2027-12-31 | 224639813 | 0
GEN-2023-224 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03225 | 2027-12-31 | 224639813 | 0
GEN-2023-225 | 02 NEBRASKA | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03225 | 2027-12-31 | 224639813 | 0
GEN-2023-015 | 03 CENTRAL | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03281 | 2027-12-31 | 224639813 | 0
GEN-2023-107 | 03 CENTRAL | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04613 | 2027-12-31 | 224639813 | 0
GEN-2023-172 | 03 CENTRAL | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03313 | 2027-12-31 | 224639813 | 0
GEN-2023-173 | 03 CENTRAL | ERIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03313 | 2027-12-31 | 224639813 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.16064 | 2027-12-31 | 224639813 | 0
GEN-2023-199 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.11346 | 2027-12-31 | 224639813 | 0
GEN-2023-222 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.07898 | 2027-12-31 | 224639813 | 0
GEN-2023-223 | 02 NEBRASKA | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.07898 | 2027-12-31 | 224639813 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03011 | 2027-12-31 | 224639813 | 0
GEN-2023-105 | 01 NORTH | NRIS | 200220 | 50442 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Gentleman 345 kV Ckt 1 | Build new 110-mile 345 kV line from Gerald Gentleman Station substation to new Cherry County substation. This upgrade is contingent upon approval from Western Area Power Administration ("WAPA") to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04159 | 2027-12-31 | 224639813 | 0
GEN-2023-012 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03411 | 2027-12-31 | 254838000 | 0
GEN-2023-062 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.06232 | 2027-12-31 | 254838000 | 0
GEN-2023-082 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03645 | 2027-12-31 | 254838000 | 0
GEN-2023-097 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04274 | 2027-12-31 | 254838000 | 0
GEN-2023-105 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.07572 | 2027-12-31 | 254838000 | 0
GEN-2023-154 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.05717 | 2027-12-31 | 254838000 | 0
GEN-2023-182 | 01 NORTH | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03906 | 2027-12-31 | 254838000 | 0
GEN-2023-077 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03736 | 2027-12-31 | 254838000 | 0
GEN-2023-078 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03736 | 2027-12-31 | 254838000 | 0
GEN-2023-079 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03736 | 2027-12-31 | 254838000 | 0
GEN-2023-116 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.12296 | 2027-12-31 | 254838000 | 0
GEN-2023-117 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.12296 | 2027-12-31 | 254838000 | 0
GEN-2023-133 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04142 | 2027-12-31 | 254838000 | 0
GEN-2023-153 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.11183 | 2027-12-31 | 254838000 | 0
GEN-2023-222 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03559 | 2027-12-31 | 254838000 | 0
GEN-2023-223 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03559 | 2027-12-31 | 254838000 | 0
GEN-2023-224 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03723 | 2027-12-31 | 254838000 | 0
GEN-2023-225 | 02 NEBRASKA | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03723 | 2027-12-31 | 254838000 | 0
GEN-2023-107 | 03 CENTRAL | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.04321 | 2027-12-31 | 254838000 | 0
GEN-2023-172 | 03 CENTRAL | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03112 | 2027-12-31 | 254838000 | 0
GEN-2023-173 | 03 CENTRAL | ERIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.03112 | 2027-12-31 | 254838000 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.15819 | 2027-12-31 | 254838000 | 0
GEN-2023-199 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.12703 | 2027-12-31 | 254838000 | 0
GEN-2023-222 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.09465 | 2027-12-31 | 254838000 | 0
GEN-2023-223 | 02 NEBRASKA | NRIS | 200220 | 50445 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV | Cherry Co. - Holt Co. 345 kV Ckt 1 | Build new 117-mile 345 kV line from new Cherry County substation to new Holt County substation. This upgrade is contingent upon approval from WAPA to tap the Grand Island - Fort Thompson 345 kV line. | 2012 ITP10 | Yes | Yes | 0.09465 | 2027-12-31 | 254838000 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Yes | Yes | 0.04193 | 2028-05-31 | 405535 | 0
GEN-2023-150 | 04 SOUTHEAST | ERIS | 220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Yes | Yes | 0.06865 | 2028-05-31 | 405535 | 0
GEN-2023-035 | 04 SOUTHEAST | NRIS | 220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Yes | Yes | 0.04028 | 2028-05-31 | 405535 | 0
GEN-2023-150 | 04 SOUTHEAST | NRIS | 220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Yes | Yes | 0.06736 | 2028-05-31 | 405535 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 220773 | 122756 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Substation Rebuild and Line Re-termination | Rebuild Anadarko SPA 138 kV substation to support a new second and third 138 kV line from Anadarko to Gracemont to achieve a summer emergency rating of 478 MVA. Re-terminate all existing lines into the new station. | 2023 ITP | Yes | Yes | 0.04982 | 2028-05-31 | 405535 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 220773 | 157396 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV substation to support a third line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.04193 | 2028-05-31 | 483360 | 0
GEN-2023-150 | 04 SOUTHEAST | ERIS | 220773 | 157396 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV substation to support a third line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.06865 | 2028-05-31 | 483360 | 0
GEN-2023-035 | 04 SOUTHEAST | NRIS | 220773 | 157396 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV substation to support a third line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.04028 | 2028-05-31 | 483360 | 0
GEN-2023-150 | 04 SOUTHEAST | NRIS | 220773 | 157396 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 3 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV substation to support a third line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.06736 | 2028-05-31 | 483360 | 0
GEN-2023-035 | 04 SOUTHEAST | ERIS | 220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.04193 | 2028-05-31 | 2500000 | 0
GEN-2023-150 | 04 SOUTHEAST | ERIS | 220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.06865 | 2028-05-31 | 2500000 | 0
GEN-2023-035 | 04 SOUTHEAST | NRIS | 220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.04028 | 2028-05-31 | 2500000 | 0
GEN-2023-150 | 04 SOUTHEAST | NRIS | 220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.06736 | 2028-05-31 | 2500000 | 0
GEN-2023-088 | 04 SOUTHEAST | NRIS | 220773 | 158638 | Line - Anadarko - Gracemont 138 kV double Ckt 2 & 3 | Anadarko SPA 138 kV Ckt 2 Terminal Equipment | Install any necessary terminal equipment at Anadarko SPA 138 kV to support a second 138 kV line from Anadarko to Gracemont. | 2023 ITP | Yes | Yes | 0.04982 | 2028-05-31 | 2500000 | 0
GEN-2023-059 | 04 SOUTHEAST | ERIS | 220737 | 157264 | Line - Flournoy 138 kV- Oak Pan-Harr 138 kV - Longwood 138 kV | Longwood 138 kV Terminal Upgrade | Replace sub conductor at Longwood on the Longwood to Noram 138 kV Line to achieve a minimum rating of 434 MVA | DISIS-2022-001 | Yes | Yes | 0.0308 | 2028-06-01 | 150000 | 150000
GEN-2023-059 | 04 SOUTHEAST | ERIS | 220737 | 157264 | Line - Flournoy 138 kV- Oak Pan-Harr 138 kV - Longwood 138 kV | Longwood 138 kV Terminal Upgrade | Replace sub conductor at Longwood on the Longwood to Noram 138 kV Line to achieve a minimum rating of 434 MVA | DISIS-2022-001 | Yes | Yes | 0.03003 | 2028-06-01 | 150000 | 150000
GEN-2023-230 | 04 SOUTHEAST | ERIS | 220737 | 157264 | Line - Flournoy 138 kV- Oak Pan-Harr 138 kV - Longwood 138 kV | Longwood 138 kV Terminal Upgrade | Replace sub conductor at Longwood on the Longwood to Noram 138 kV Line to achieve a minimum rating of 434 MVA | DISIS-2022-001 | Yes | Yes | 0.1421 | 2028-06-01 | 150000 | 150000
GEN-2023-230 | 04 SOUTHEAST | NRIS | 220737 | 157264 | Line - Flournoy 138 kV- Oak Pan-Harr 138 kV - Longwood 138 kV | Longwood 138 kV Terminal Upgrade | Replace sub conductor at Longwood on the Longwood to Noram 138 kV Line to achieve a minimum rating of 434 MVA | DISIS-2022-001 | Yes | Yes | 0.1305 | 2028-06-01 | 150000 | 150000
GEN-2023-033 | 03 CENTRAL | NRIS | 220816 | 170429 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Terminal Equipment (345 kV) | Rebuild Nashua 345 kV Station to a breaker-and-a-half configuration and install any 345 kV terminal equipment to support 345/161 transformer at Nashua 345 kV substation | 2024 ITP | Yes | Yes | 0.04424 | 2028-06-01 | 21991020 | 0
GEN-2023-169 | 03 CENTRAL | NRIS | 220816 | 170429 | XFR - Nashua 345/161 kV Ckt2 | Nashua 345/161 kV Terminal Equipment (345 kV) | Rebuild Nashua 345 kV Station to a breaker-and-a-half configuration and install any 345 kV terminal equipment to support 345/161 transformer at Nashua 345 kV substation | 2024 ITP | Yes | Yes | 0.03409 | 2028-06-01 | 21991020 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.08635 | 2028-12-15 | 5577000 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03979 | 2028-12-15 | 5577000 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.11026 | 2028-12-15 | 5577000 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.09135 | 2028-12-15 | 5577000 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.10292 | 2028-12-15 | 5577000 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.1381 | 2028-12-15 | 5577000 | 0
GEN-2023-158 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04526 | 2028-12-15 | 5577000 | 0
GEN-2023-159 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04526 | 2028-12-15 | 5577000 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04045 | 2028-12-15 | 5577000 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04077 | 2028-12-15 | 5577000 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.09988 | 2028-12-15 | 5577000 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.08511 | 2028-12-15 | 5577000 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.13466 | 2028-12-15 | 5577000 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.0751 | 2028-12-15 | 5577000 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.09667 | 2028-12-15 | 5577000 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220780 | 158630 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 (230 kV) | Expand and replace 230 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04266 | 2028-12-15 | 5577000 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.08635 | 2028-12-15 | 10434902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.03979 | 2028-12-15 | 10434902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.11026 | 2028-12-15 | 10434902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.09135 | 2028-12-15 | 10434902 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.10292 | 2028-12-15 | 10434902 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.1381 | 2028-12-15 | 10434902 | 0
GEN-2023-158 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.04526 | 2028-12-15 | 10434902 | 0
GEN-2023-159 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.04526 | 2028-12-15 | 10434902 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.04045 | 2028-12-15 | 10434902 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.04077 | 2028-12-15 | 10434902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.09988 | 2028-12-15 | 10434902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.08511 | 2028-12-15 | 10434902 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.13466 | 2028-12-15 | 10434902 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.0751 | 2028-12-15 | 10434902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.09667 | 2028-12-15 | 10434902 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220780 | 158629 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 2 (345 kV) | Install new 345/230 transformer at Potter County 345 kV substation ckt 2 | 2023 ITP | Yes | Yes | 0.04266 | 2028-12-15 | 10434902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.08635 | 2028-12-15 | 10545000 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.03979 | 2028-12-15 | 10545000 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.11026 | 2028-12-15 | 10545000 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.09135 | 2028-12-15 | 10545000 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.10292 | 2028-12-15 | 10545000 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.1381 | 2028-12-15 | 10545000 | 0
GEN-2023-158 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04526 | 2028-12-15 | 10545000 | 0
GEN-2023-159 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04526 | 2028-12-15 | 10545000 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04045 | 2028-12-15 | 10545000 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04077 | 2028-12-15 | 10545000 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.09988 | 2028-12-15 | 10545000 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.08511 | 2028-12-15 | 10545000 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.13466 | 2028-12-15 | 10545000 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.0751 | 2028-12-15 | 10545000 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.09667 | 2028-12-15 | 10545000 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220780 | 158632 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345 kV Substation Expansion | Expand and replace 345 kV terminal equipment at Potter County substation to support the replacement of the 345/230 kV transformer ckt 1 and the new 345/230 kV transformer ckt 2 | 2023 ITP | Yes | Yes | 0.04266 | 2028-12-15 | 10545000 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220780 | 158631 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 | Replace existing 345/230 kV transformer at Potter County substation ckt 1 | 2023 ITP | Yes | Yes | 0.1381 | 2028-12-15 | 10977332 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220780 | 158631 | XFR-Potter County 345/230 kV Ckt1 & Ckt2 | Potter County 345/230 kV Transformer Ckt 1 | Replace existing 345/230 kV transformer at Potter County substation ckt 1 | 2023 ITP | Yes | Yes | 0.13466 | 2028-12-15 | 10977332 | 0
GEN-2023-222 | 02 NEBRASKA | ERIS | 220745 | 157385 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 - 70th & Bluff 161 kV Ckt 1 Rebuild (LES) | Rebuild 17.7 miles of 161 kV Ckt 1 line from Sub 1214 161 kV substation to 70th & Bluff161 kV substation with a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.0304 | 2029-03-01 | 1453879 | 0
GEN-2023-223 | 02 NEBRASKA | ERIS | 220745 | 157385 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | Sub 1214 - 70th & Bluff 161 kV Ckt 1 Rebuild (LES) | Rebuild 17.7 miles of 161 kV Ckt 1 line from Sub 1214 161 kV substation to 70th & Bluff161 kV substation with a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.0304 | 2029-03-01 | 1453879 | 0
GEN-2023-012 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.05922 | 2029-09-12 | 9263038 | 0
GEN-2023-062 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.1175 | 2029-09-12 | 9263038 | 0
GEN-2023-082 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.04386 | 2029-09-12 | 9263038 | 0
GEN-2023-097 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.11793 | 2029-09-12 | 9263038 | 0
GEN-2023-182 | 01 NORTH | ERIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.48615 | 2029-09-12 | 9263038 | 0
GEN-2023-082 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.03398 | 2029-09-12 | 9263038 | 0
GEN-2023-097 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.06887 | 2029-09-12 | 9263038 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.0489 | 2029-09-12 | 9263038 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.10335 | 2029-09-12 | 9263038 | 0
GEN-2023-105 | 01 NORTH | NRIS | 220747 | 158019 | Device - Groton 345 kV Reactor | Groton 345 kV Reactor | Install 2nd 68 MVAR reactor at Groton 345 kV substation | 2023 ITP | Yes | Yes | 0.05083 | 2029-09-12 | 9263038 | 0
GEN-2023-062 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.12651 | 2029-09-12 | 9455440 | 0
GEN-2023-097 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.12459 | 2029-09-12 | 9455440 | 0
GEN-2023-154 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.08382 | 2029-09-12 | 9455440 | 0
GEN-2023-182 | 01 NORTH | ERIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.05538 | 2029-09-12 | 9455440 | 0
GEN-2023-097 | 01 NORTH | NRIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.0804 | 2029-09-12 | 9455440 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.05426 | 2029-09-12 | 9455440 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.10775 | 2029-09-12 | 9455440 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.10775 | 2029-09-12 | 9455440 | 0
GEN-2023-105 | 01 NORTH | NRIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.08925 | 2029-09-12 | 9455440 | 0
GEN-2023-105 | 01 NORTH | NRIS | 220747 | 157375 | Device - Broadland 345 kV Reactor | Broadland 345 kV Reactor | Install 2nd 75 MVAR reactor at Broadland 345 kV substation | 2023 ITP | Yes | Yes | 0.08925 | 2029-09-12 | 9455440 | 0
GEN-2023-077 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03413 | 2029-12-31 | 2849669 | 0
GEN-2023-078 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03413 | 2029-12-31 | 2849669 | 0
GEN-2023-079 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.03413 | 2029-12-31 | 2849669 | 0
GEN-2023-222 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.0304 | 2029-12-31 | 2849669 | 0
GEN-2023-223 | 02 NEBRASKA | ERIS | 220745 | 157387 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161 kV Terminal Upgrade | Upgrade any necessary terminal equipment at 70th & Bluff 161 kV substation on the Sub 1214 to 70th & Bluff 161 kV line to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.0304 | 2029-12-31 | 2849669 | 0
GEN-2023-222 | 02 NEBRASKA | ERIS | 220745 | 157397 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.0304 | 2029-12-31 | 6114594 | 0
GEN-2023-223 | 02 NEBRASKA | ERIS | 220745 | 157397 | Multi - Sub 1214 - 70th & Bluff 161 kV Rebuild | 70th & Bluff 161/115 kV Transformer Ckt 1 (115 kV) | Upgrade 161/115 transformer Ckt 1 at 70th & Bluff 115 kV substation to achieve a summer emergency rating of 215 MVA. | 2023 ITP | Yes | Yes | 0.0304 | 2029-12-31 | 6114594 | 0
GEN-2023-088 | 04 SOUTHEAST | ERIS | 220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Yes | Yes | 0.10372 | 2026-05-31 | 736625 | 0
GEN-2023-134 | 04 SOUTHEAST | ERIS | 220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Yes | Yes | 0.3487 | 2026-05-31 | 736625 | 0
GEN-2023-205 | 04 SOUTHEAST | ERIS | 220812 | 170168 | Device - Maud Tap 138 kV Terminal Equipment | Maud Tap 138 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Maud Tap 138 kV substation for the line from Maud Tap 138 kV substation to Earlsboro 138 kV substation with a summer emergency rating of 286 MVA. | 2024 ITP | Yes | Yes | 0.10481 | 2026-05-31 | 736625 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 220817 | 159259 | XFR - Road Runner 345/115 kV Ckt 2 | Roadrunner 345/115 kV Transformer Ckt 2 (345 kV) | Install 345 kV terminal equipment to support 345/115 kV transformer at Roadrunner 345 kV substation with a summer emergency rating of 435 MVA. | 2024 ITP | Yes | Yes | 0.06109 | TBD | 1336373 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 220817 | 159258 | XFR - Road Runner 345/115 kV Ckt 2 | Roadrunner 345/115 kV Transformer Ckt 2 (115 kV) | Install a new 345/115 kV transformer at Roadrunner 115 kV substation and expand the 115 kV bus. | 2024 ITP | Yes | Yes | 0.06109 | TBD | 1357050 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 220804 | 170385 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (345 kV) | Install 345 kV terminal equipment to support 345/138 transformer at Tulsa North 345 kV substation with a summer emergency rating of 675 MVA. | 2024 ITP | Yes | Yes | 0.05031 | TBD | 1537869 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 220804 | 170385 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (345 kV) | Install 345 kV terminal equipment to support 345/138 transformer at Tulsa North 345 kV substation with a summer emergency rating of 675 MVA. | 2024 ITP | Yes | Yes | 0.1491 | TBD | 1537869 | 0
GEN-2023-027 | 04 SOUTHEAST | NRIS | 220804 | 170385 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (345 kV) | Install 345 kV terminal equipment to support 345/138 transformer at Tulsa North 345 kV substation with a summer emergency rating of 675 MVA. | 2024 ITP | Yes | Yes | 0.03442 | TBD | 1537869 | 0
GEN-2023-063 | 04 SOUTHEAST | NRIS | 220804 | 170385 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (345 kV) | Install 345 kV terminal equipment to support 345/138 transformer at Tulsa North 345 kV substation with a summer emergency rating of 675 MVA. | 2024 ITP | Yes | Yes | 0.13342 | TBD | 1537869 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.20301 | TBD | 2137638 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.2041 | TBD | 2137638 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.35298 | TBD | 2137638 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.23579 | TBD | 2137638 | 0
GEN-2023-005 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 2137638 | 0
GEN-2023-060 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 2137638 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.27972 | TBD | 2137638 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.15767 | TBD | 2137638 | 0
GEN-2023-142 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 2137638 | 0
GEN-2023-143 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 2137638 | 0
GEN-2023-158 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07614 | TBD | 2137638 | 0
GEN-2023-159 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07614 | TBD | 2137638 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07769 | TBD | 2137638 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07196 | TBD | 2137638 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.27139 | TBD | 2137638 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.20142 | TBD | 2137638 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.17594 | TBD | 2137638 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.10636 | TBD | 2137638 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.25739 | TBD | 2137638 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220889 | 170053 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Potter 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07107 | TBD | 2137638 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.09051 | TBD | 2137638 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.09172 | TBD | 2137638 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.46319 | TBD | 2137638 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.18793 | TBD | 2137638 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.06122 | TBD | 2137638 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07946 | TBD | 2137638 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.14776 | TBD | 2137638 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.15006 | TBD | 2137638 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.08517 | TBD | 2137638 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.05011 | TBD | 2137638 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170104 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Ckt 1 Terminal Upgrade #1 | Install any necessary terminal equipment at Crossroads 765 kV substation to support a new line from Crossroads 765 kV substation to Phantom 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.18808 | TBD | 2137638 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.09051 | TBD | 2137638 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.09172 | TBD | 2137638 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.46319 | TBD | 2137638 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.18793 | TBD | 2137638 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.06122 | TBD | 2137638 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07946 | TBD | 2137638 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.14776 | TBD | 2137638 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.15006 | TBD | 2137638 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.08517 | TBD | 2137638 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.05011 | TBD | 2137638 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170090 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Phantom 765 kV substation to support a new line from Phantom 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.18808 | TBD | 2137638 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.20301 | TBD | 2137638 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.2041 | TBD | 2137638 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.35298 | TBD | 2137638 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.23579 | TBD | 2137638 | 0
GEN-2023-005 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 2137638 | 0
GEN-2023-060 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 2137638 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.27972 | TBD | 2137638 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.15767 | TBD | 2137638 | 0
GEN-2023-142 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 2137638 | 0
GEN-2023-143 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 2137638 | 0
GEN-2023-158 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07614 | TBD | 2137638 | 0
GEN-2023-159 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07614 | TBD | 2137638 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07769 | TBD | 2137638 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07196 | TBD | 2137638 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.27139 | TBD | 2137638 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.20142 | TBD | 2137638 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.17594 | TBD | 2137638 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.10636 | TBD | 2137638 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.25739 | TBD | 2137638 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220889 | 170052 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765 kV Ckt 1 Terminal Upgrade | Install any necessary terminal equipment at Potter 765 kV substation to support a new line from Potter 765 kV substation to Crossroads 765 kV substation Ckt 1 with a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07107 | TBD | 2137638 | 0
GEN-2023-061 | 03 CENTRAL | ERIS | 220880 | 159382 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | N Reed Spring - S Reed Spring 161 kV Ckt 1 Rebuild | Rebuild 1.5 mile Ckt 1 line from N Reed Spring 161 kV substation to S Reed Spring 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Yes | Yes | 0.04495 | TBD | 2353884 | 0
GEN-2023-061 | 03 CENTRAL | NRIS | 220880 | 159382 | Line - N Reed Spring 161 kV - S Reed Spring 161 kV Rebuild | N Reed Spring - S Reed Spring 161 kV Ckt 1 Rebuild | Rebuild 1.5 mile Ckt 1 line from N Reed Spring 161 kV substation to S Reed Spring 161 kV substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 557 MVA. | 2024 ITP | Yes | Yes | 0.05318 | TBD | 2353884 | 0
GEN-2023-184 | 05 SOUTHWEST | ERIS | 220817 | 170355 | XFR - Road Runner 345/115 kV #3 | Roadrunner 345/115 kV Transformer Ckt 3 (345 kV) | Install 345 kV terminal equipment to support a Ckt 3 345/115 kV transformer at Roadrunner 345 kV substation with a summer emergency rating of 435 MVA. | 2024 ITP | Yes | Yes | 0.06109 | TBD | 3128845 | 0
GEN-2023-028 | 04 SOUTHEAST | ERIS | 220804 | 170415 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (AEP) | Install any necessary terminal equipment to support connecting GRDA's third 161/138 kV transformer at Catoosa 138 kV substation with a summer emergency rating of 188 MVA. | 2024 ITP | Yes | Yes | 0.04655 | TBD | 4765714 | 0
GEN-2023-049 | 04 SOUTHEAST | ERIS | 220804 | 170415 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (AEP) | Install any necessary terminal equipment to support connecting GRDA's third 161/138 kV transformer at Catoosa 138 kV substation with a summer emergency rating of 188 MVA. | 2024 ITP | Yes | Yes | 0.044 | TBD | 4765714 | 0
GEN-2023-055 | 04 SOUTHEAST | ERIS | 220804 | 170415 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (AEP) | Install any necessary terminal equipment to support connecting GRDA's third 161/138 kV transformer at Catoosa 138 kV substation with a summer emergency rating of 188 MVA. | 2024 ITP | Yes | Yes | 0.04785 | TBD | 4765714 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 220804 | 170415 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (AEP) | Install any necessary terminal equipment to support connecting GRDA's third 161/138 kV transformer at Catoosa 138 kV substation with a summer emergency rating of 188 MVA. | 2024 ITP | Yes | Yes | 0.06917 | TBD | 4765714 | 0
GEN-2023-063 | 04 SOUTHEAST | NRIS | 220804 | 170415 | XFR - Catoosa 161/138 kV | Catoosa 161/138 kV Transformer (AEP) | Install any necessary terminal equipment to support connecting GRDA's third 161/138 kV transformer at Catoosa 138 kV substation with a summer emergency rating of 188 MVA. | 2024 ITP | Yes | Yes | 0.06429 | TBD | 4765714 | 0
GEN-2023-027 | 04 SOUTHEAST | ERIS | 220804 | 170384 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (138 kV) | Install new 345/138 transformer at Tulsa North 138 kV substation | 2024 ITP | Yes | Yes | 0.05031 | TBD | 11484217 | 0
GEN-2023-063 | 04 SOUTHEAST | ERIS | 220804 | 170384 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (138 kV) | Install new 345/138 transformer at Tulsa North 138 kV substation | 2024 ITP | Yes | Yes | 0.1491 | TBD | 11484217 | 0
GEN-2023-027 | 04 SOUTHEAST | NRIS | 220804 | 170384 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (138 kV) | Install new 345/138 transformer at Tulsa North 138 kV substation | 2024 ITP | Yes | Yes | 0.03442 | TBD | 11484217 | 0
GEN-2023-063 | 04 SOUTHEAST | NRIS | 220804 | 170384 | XFR - Tulsa North 345/138 kV | Tulsa North 345/138 kV Transformer Ckt 2 (138 kV) | Install new 345/138 transformer at Tulsa North 138 kV substation | 2024 ITP | Yes | Yes | 0.13342 | TBD | 11484217 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.20301 | TBD | 12648300 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.2041 | TBD | 12648300 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.35298 | TBD | 12648300 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.23579 | TBD | 12648300 | 0
GEN-2023-005 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.0368 | TBD | 12648300 | 0
GEN-2023-060 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.0368 | TBD | 12648300 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.27972 | TBD | 12648300 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.15767 | TBD | 12648300 | 0
GEN-2023-142 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.0368 | TBD | 12648300 | 0
GEN-2023-143 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.0368 | TBD | 12648300 | 0
GEN-2023-158 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.07614 | TBD | 12648300 | 0
GEN-2023-159 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.07614 | TBD | 12648300 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.07769 | TBD | 12648300 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.07196 | TBD | 12648300 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.27139 | TBD | 12648300 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.20142 | TBD | 12648300 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.17594 | TBD | 12648300 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.10636 | TBD | 12648300 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.25739 | TBD | 12648300 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220889 | 170564 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 1 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.07107 | TBD | 12648300 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.20301 | TBD | 12648300 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.2041 | TBD | 12648300 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.35298 | TBD | 12648300 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.23579 | TBD | 12648300 | 0
GEN-2023-005 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.0368 | TBD | 12648300 | 0
GEN-2023-060 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.0368 | TBD | 12648300 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.27972 | TBD | 12648300 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.15767 | TBD | 12648300 | 0
GEN-2023-142 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.0368 | TBD | 12648300 | 0
GEN-2023-143 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.0368 | TBD | 12648300 | 0
GEN-2023-158 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.07614 | TBD | 12648300 | 0
GEN-2023-159 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.07614 | TBD | 12648300 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.07769 | TBD | 12648300 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.07196 | TBD | 12648300 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.27139 | TBD | 12648300 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.20142 | TBD | 12648300 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.17594 | TBD | 12648300 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.10636 | TBD | 12648300 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.25739 | TBD | 12648300 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220889 | 170067 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765 kV Reactor 2 | Install -150 MVAR reactor at Crossroads 765 kV substation | 2024 ITP | Yes | Yes | 0.07107 | TBD | 12648300 | 0
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | Branson North - Branson Northwest - North Branson - Reeds Spring 161 kV Rebuild | Branson North - Branson Northwest - North Branson - Reeds Spring 161 kV Rebuild | Rebuild Branson North - Branson Northwest - North Branson - Reeds Spring 161 kV line | 2024 ITP | Yes | Yes | 0.04424 | TBD | 17108010 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.20301 | TBD | 17914575 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.2041 | TBD | 17914575 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.35298 | TBD | 17914575 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.23579 | TBD | 17914575 | 0
GEN-2023-005 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.0368 | TBD | 17914575 | 0
GEN-2023-060 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.0368 | TBD | 17914575 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.27972 | TBD | 17914575 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.15767 | TBD | 17914575 | 0
GEN-2023-142 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.0368 | TBD | 17914575 | 0
GEN-2023-143 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.0368 | TBD | 17914575 | 0
GEN-2023-158 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.07614 | TBD | 17914575 | 0
GEN-2023-159 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.07614 | TBD | 17914575 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.07769 | TBD | 17914575 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.07196 | TBD | 17914575 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.27139 | TBD | 17914575 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.20142 | TBD | 17914575 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.17594 | TBD | 17914575 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.10636 | TBD | 17914575 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.25739 | TBD | 17914575 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220889 | 170078 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Crossroads | Install 765 kV Substation at Crossroads | 2024 ITP | Yes | Yes | 0.07107 | TBD | 17914575 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.09051 | TBD | 17914575 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.09172 | TBD | 17914575 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.46319 | TBD | 17914575 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.18793 | TBD | 17914575 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.06122 | TBD | 17914575 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.07946 | TBD | 17914575 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.14776 | TBD | 17914575 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.15006 | TBD | 17914575 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.08517 | TBD | 17914575 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.05011 | TBD | 17914575 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170079 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Phantom | Install 765 kV Substation at Phantom | 2024 ITP | Yes | Yes | 0.18808 | TBD | 17914575 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.20301 | TBD | 17914575 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.2041 | TBD | 17914575 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.35298 | TBD | 17914575 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.23579 | TBD | 17914575 | 0
GEN-2023-005 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.0368 | TBD | 17914575 | 0
GEN-2023-060 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.0368 | TBD | 17914575 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.27972 | TBD | 17914575 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.15767 | TBD | 17914575 | 0
GEN-2023-142 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.0368 | TBD | 17914575 | 0
GEN-2023-143 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.0368 | TBD | 17914575 | 0
GEN-2023-158 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.07614 | TBD | 17914575 | 0
GEN-2023-159 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.07614 | TBD | 17914575 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.07769 | TBD | 17914575 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.07196 | TBD | 17914575 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.27139 | TBD | 17914575 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.20142 | TBD | 17914575 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.17594 | TBD | 17914575 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.10636 | TBD | 17914575 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.25739 | TBD | 17914575 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220889 | 170080 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | New 765 kV Substation at Potter | Install 765 kV Substation at Potter | 2024 ITP | Yes | Yes | 0.07107 | TBD | 17914575 | 0
GEN-2023-061 | 03 CENTRAL | ERIS | 220881 | 170133 | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Rebuild 11.15 miles 161 kV line from Aurora HT to Monett | 2024 ITP | Yes | Yes | 0.11811 | TBD | 21553353 | 0
GEN-2023-194 | 03 CENTRAL | ERIS | 220881 | 170133 | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Rebuild 11.15 miles 161 kV line from Aurora HT to Monett | 2024 ITP | Yes | Yes | 0.0676 | TBD | 21553353 | 0
GEN-2023-061 | 03 CENTRAL | NRIS | 220881 | 170133 | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Aurora H.T. - Monett 161 kV Ckt 1 Rebuild | Rebuild 11.15 miles 161 kV line from Aurora HT to Monett | 2024 ITP | Yes | Yes | 0.13193 | TBD | 21553353 | 0
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Build a second 345/115kV transformer at Antelope | Build a second 345/115kV transformer at Antelope | Build a new Antelope 345/115 kV transformer 2 with a rating of 417 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.04053 | TBD | 33500000 | 33500000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Build a second 345/115kV transformer at Antelope | Build a second 345/115kV transformer at Antelope | Build a new Antelope 345/115 kV transformer 2 with a rating of 417 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.04053 | TBD | 33500000 | 33500000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Build a second 345/115kV transformer at Antelope | Build a second 345/115kV transformer at Antelope | Build a new Antelope 345/115 kV transformer 2 with a rating of 417 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.04053 | TBD | 33500000 | 33500000
GEN-2023-216 | 02 NEBRASKA | NRIS | TBD | TBD | Build a second 345/115kV transformer at Antelope | Build a second 345/115kV transformer at Antelope | Build a new Antelope 345/115 kV transformer 2 with a rating of 417 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.08858 | TBD | 33500000 | 33500000
GEN-2023-217 | 02 NEBRASKA | NRIS | TBD | TBD | Build a second 345/115kV transformer at Antelope | Build a second 345/115kV transformer at Antelope | Build a new Antelope 345/115 kV transformer 2 with a rating of 417 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.08858 | TBD | 33500000 | 33500000
GEN-2023-218 | 02 NEBRASKA | NRIS | TBD | TBD | Build a second 345/115kV transformer at Antelope | Build a second 345/115kV transformer at Antelope | Build a new Antelope 345/115 kV transformer 2 with a rating of 417 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.08858 | TBD | 33500000 | 33500000
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170068 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03785 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170068 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.0944 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170068 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.06734 | TBD | 62489902 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170068 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.07373 | TBD | 62489902 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170068 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.06464 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170068 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.07367 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170068 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.06015 | TBD | 62489902 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170068 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.06748 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170068 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.07179 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.0375 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.0375 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03746 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03746 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03674 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03674 | TBD | 62489902 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.07283 | TBD | 62489902 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.07283 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.04121 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.04121 | TBD | 62489902 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03026 | TBD | 62489902 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170560 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03026 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.0375 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.0375 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03746 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03746 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03674 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03674 | TBD | 62489902 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.07283 | TBD | 62489902 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.07283 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.04121 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.04121 | TBD | 62489902 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03026 | TBD | 62489902 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170563 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Crossroads 345 kV substation | 2024 ITP | Yes | Yes | 0.03026 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03017 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03017 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03017 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03057 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03057 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03057 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.1544 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.1544 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.1544 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06264 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06264 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06264 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.04925 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.04925 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.04925 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.05002 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.05002 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.05002 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06269 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06269 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170091 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06269 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03017 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03017 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03017 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03057 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03057 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03057 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.1544 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.1544 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.1544 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06264 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06264 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06264 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.04925 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.04925 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.04925 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.05002 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.05002 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.05002 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06269 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06269 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170558 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06269 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03017 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03017 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03017 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03057 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03057 | TBD | 62489902 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.03057 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.1544 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.1544 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.1544 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06264 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06264 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06264 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.04925 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.04925 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.04925 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.05002 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.05002 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.05002 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06269 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06269 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170561 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Phantom 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Phantom 345 kV substation | 2024 ITP | Yes | Yes | 0.06269 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170096 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.03785 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170096 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.0944 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170096 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06734 | TBD | 62489902 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170096 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.07373 | TBD | 62489902 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170096 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06464 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170096 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.07367 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170096 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06015 | TBD | 62489902 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170096 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06748 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170096 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 1 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.07179 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170559 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.03785 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170559 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.0944 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170559 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06734 | TBD | 62489902 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170559 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.07373 | TBD | 62489902 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170559 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06464 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170559 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.07367 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170559 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06015 | TBD | 62489902 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170559 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06748 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170559 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 2 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.07179 | TBD | 62489902 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170562 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.03785 | TBD | 62489902 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170562 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.0944 | TBD | 62489902 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170562 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06734 | TBD | 62489902 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170562 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.07373 | TBD | 62489902 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170562 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06464 | TBD | 62489902 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170562 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.07367 | TBD | 62489902 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170562 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06015 | TBD | 62489902 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170562 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.06748 | TBD | 62489902 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170562 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter 765/345 kV Transformer Ckt 3 (345 kV) | Install new 765/345 transformer at Potter 345 kV substation | 2024 ITP | Yes | Yes | 0.07179 | TBD | 62489902 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 220896 | 170229 | Line - Holt County 345 kV - Antelope 345 kV New Line | Antelope - Holt County 345 kV Ckt 1 New Line | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.091 | TBD | 90400000 | 0
GEN-2023-199 | 02 NEBRASKA | NRIS | 220896 | 170229 | Line - Holt County 345 kV - Antelope 345 kV New Line | Antelope - Holt County 345 kV Ckt 1 New Line | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.20308 | TBD | 90400000 | 0
GEN-2023-222 | 02 NEBRASKA | NRIS | 220896 | 170229 | Line - Holt County 345 kV - Antelope 345 kV New Line | Antelope - Holt County 345 kV Ckt 1 New Line | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.09947 | TBD | 90400000 | 0
GEN-2023-223 | 02 NEBRASKA | NRIS | 220896 | 170229 | Line - Holt County 345 kV - Antelope 345 kV New Line | Antelope - Holt County 345 kV Ckt 1 New Line | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.09947 | TBD | 90400000 | 0
GEN-2023-216 | 02 NEBRASKA | NRIS | 220896 | 170229 | Line - Holt County 345 kV - Antelope 345 kV New Line | Antelope - Holt County 345 kV Ckt 1 New Line | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.15044 | TBD | 90400000 | 0
GEN-2023-217 | 02 NEBRASKA | NRIS | 220896 | 170229 | Line - Holt County 345 kV - Antelope 345 kV New Line | Antelope - Holt County 345 kV Ckt 1 New Line | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.15044 | TBD | 90400000 | 0
GEN-2023-218 | 02 NEBRASKA | NRIS | 220896 | 170229 | Line - Holt County 345 kV - Antelope 345 kV New Line | Antelope - Holt County 345 kV Ckt 1 New Line | Build a 24 mile 345 kV Ckt1 new line from Holt County 345 kV Ck1 substation to Antelope 345 kV Ck1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.15044 | TBD | 90400000 | 0
GEN-2023-222 | 02 NEBRASKA | NRIS | 220882 | 170392 | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Elm Creek - Tobias 345 kV Ckt 1 New Line (NPPD) | Build 84 mile 345 kV Ckt 1 line from Elm Creek 345 kV Ckt 1 substation to Tobias 345 kV Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.08296 | TBD | 137721276 | 0
GEN-2023-223 | 02 NEBRASKA | NRIS | 220882 | 170392 | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Elm Creek - Tobias 345 kV Ckt 1 New Line (NPPD) | Build 84 mile 345 kV Ckt 1 line from Elm Creek 345 kV Ckt 1 substation to Tobias 345 kV Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.08296 | TBD | 137721276 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220882 | 170392 | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Elm Creek - Tobias 345 kV Ckt 1 New Line (NPPD) | Build 84 mile 345 kV Ckt 1 line from Elm Creek 345 kV Ckt 1 substation to Tobias 345 kV Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.03367 | TBD | 137721276 | 0
GEN-2023-061 | 03 CENTRAL | NRIS | 220882 | 170392 | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Elm Creek - Tobias 345 kV Ckt 1 New Line (NPPD) | Build 84 mile 345 kV Ckt 1 line from Elm Creek 345 kV Ckt 1 substation to Tobias 345 kV Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.03729 | TBD | 137721276 | 0
GEN-2023-064 | 04 SOUTHEAST | NRIS | 220882 | 170392 | Line - Elm Creek 345 kV - Tobias 345 kV New Line | Elm Creek - Tobias 345 kV Ckt 1 New Line (NPPD) | Build 84 mile 345 kV Ckt 1 line from Elm Creek 345 kV Ckt 1 substation to Tobias 345 kV Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | No | Yes | 0.03208 | TBD | 137721276 | 0
GEN-2023-062 | 01 NORTH | ERIS | 220869 | 169762 | Dawson County - Williston 230 kV Ckt 1 New Line | Dawson County - Williston 230 kV Ckt 1 New Line | Build a new DAWSONC4 to WILISTN4 230 kV line 1 (67.2 miles) to a standard rating of 796 MVA | 2024 ITP | Yes | Yes | 0.07949 | TBD | 220100000 | 0
GEN-2023-097 | 01 NORTH | ERIS | 220869 | 169762 | Dawson County - Williston 230 kV Ckt 1 New Line | Dawson County - Williston 230 kV Ckt 1 New Line | Build a new DAWSONC4 to WILISTN4 230 kV line 1 (67.2 miles) to a standard rating of 796 MVA | 2024 ITP | Yes | Yes | 0.08438 | TBD | 220100000 | 0
GEN-2023-097 | 01 NORTH | NRIS | 220869 | 169762 | Dawson County - Williston 230 kV Ckt 1 New Line | Dawson County - Williston 230 kV Ckt 1 New Line | Build a new DAWSONC4 to WILISTN4 230 kV line 1 (67.2 miles) to a standard rating of 796 MVA | 2024 ITP | Yes | Yes | 0.08219 | TBD | 220100000 | 0
GEN-2023-034 | 03 CENTRAL | NRIS | 220886 | 159336 | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Buffalo Flats - Delaware 345 kV Ckt 1 New Line | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.0306 | TBD | 467686128 | 0
GEN-2023-050 | 03 CENTRAL | NRIS | 220886 | 159336 | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Buffalo Flats - Delaware 345 kV Ckt 1 New Line | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.07888 | TBD | 467686128 | 0
GEN-2023-065 | 03 CENTRAL | NRIS | 220886 | 159336 | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Buffalo Flats - Delaware 345 kV Ckt 1 New Line | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.03528 | TBD | 467686128 | 0
GEN-2023-100 | 04 SOUTHEAST | NRIS | 220886 | 159336 | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Buffalo Flats - Delaware 345 kV Ckt 1 New Line | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.04326 | TBD | 467686128 | 0
GEN-2023-102 | 04 SOUTHEAST | NRIS | 220886 | 159336 | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Buffalo Flats - Delaware 345 kV Ckt 1 New Line | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.04326 | TBD | 467686128 | 0
GEN-2023-104 | 04 SOUTHEAST | NRIS | 220886 | 159336 | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | Buffalo Flats - Delaware 345 kV Ckt 1 New Line | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.03298 | TBD | 467686128 | 0
GEN-2023-075 | 04 SOUTHEAST | NRIS | 220886 | 159336 | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | BuffaloFlats - Deleware 345 kV Ckt 1 New Line | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.1315 | TBD | 467686128 | 0
GEN-2023-076 | 04 SOUTHEAST | NRIS | 220886 | 159336 | Line - Buffalo Flats 345 kV - Delaware 345 kV New Line | BuffaloFlats - Deleware 345 kV Ckt 1 New Line | Build a 154.6 mile 345 kV Ckt 1 new line from Delaware 345 kV Ckt1 substation to Buffalo Flats 345 kV Ckt1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.1315 | TBD | 467686128 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.20301 | TBD | 519610441 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.2041 | TBD | 519610441 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.35298 | TBD | 519610441 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.23579 | TBD | 519610441 | 0
GEN-2023-005 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 519610441 | 0
GEN-2023-060 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 519610441 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.27972 | TBD | 519610441 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.15767 | TBD | 519610441 | 0
GEN-2023-142 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 519610441 | 0
GEN-2023-143 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.0368 | TBD | 519610441 | 0
GEN-2023-158 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07614 | TBD | 519610441 | 0
GEN-2023-159 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07614 | TBD | 519610441 | 0
GEN-2023-178 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07769 | TBD | 519610441 | 0
GEN-2023-195 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07196 | TBD | 519610441 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.27139 | TBD | 519610441 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.20142 | TBD | 519610441 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.17594 | TBD | 519610441 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.10636 | TBD | 519610441 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.25739 | TBD | 519610441 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | 220889 | 170051 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Potter - Crossroads 765 kV Ckt 1 New Line | Build 123.7 mile 765 kV Ckt 1 line from Potter substation to Crossroads substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07107 | TBD | 519610441 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.09051 | TBD | 521264386 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.09172 | TBD | 521264386 | 0
ASGI-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.46319 | TBD | 521264386 | 0
GEN-2023-001 | 05 SOUTHWEST | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.18793 | TBD | 521264386 | 0
GEN-2023-081 | 05 SOUTHWEST | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.06122 | TBD | 521264386 | 0
GEN-2023-086 | 05 SOUTHWEST | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.07946 | TBD | 521264386 | 0
GEN-2023-201 | 05 SOUTHWEST | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.14776 | TBD | 521264386 | 0
GEN-2023-203 | 05 SOUTHWEST | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.15006 | TBD | 521264386 | 0
GEN-2023-209 | 05 SOUTHWEST | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.08517 | TBD | 521264386 | 0
GEN-2023-228 | 05 SOUTHWEST | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.05011 | TBD | 521264386 | 0
GEN-2023-236 | 05 SOUTHWEST | NRIS | 220889 | 170054 | Line - Potter 765 kV - Crossroads 765 kV - Phantom 765 kV | Crossroads - Phantom 765 kV Ckt 1 New Line | Build 120.5 mile 765 kV Ckt 1 line from Crossroads substation to Phantom substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 5300 MVA. | 2024 ITP | Yes | Yes | 0.18808 | TBD | 521264386 | 0
GEN-2023-153 | 02 NEBRASKA | NRIS | 220887 | 169968 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Holcomb - Sidney 345 kV Ckt 1 New Line | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.07064 | TBD | 977728865 | 0
GEN-2023-199 | 02 NEBRASKA | NRIS | 220887 | 169968 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Holcomb - Sidney 345 kV Ckt 1 New Line | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.03562 | TBD | 977728865 | 0
GEN-2023-222 | 02 NEBRASKA | NRIS | 220887 | 169968 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Holcomb - Sidney 345 kV Ckt 1 New Line | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.042 | TBD | 977728865 | 0
GEN-2023-223 | 02 NEBRASKA | NRIS | 220887 | 169968 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Holcomb - Sidney 345 kV Ckt 1 New Line | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.042 | TBD | 977728865 | 0
GEN-2023-015 | 03 CENTRAL | NRIS | 220887 | 169968 | Line - Holcomb - Sidney 345 kV Ckt 1 New Line | Holcomb - Sidney 345 kV Ckt 1 New Line | Build a new 300 mile 345 kV Ckt 1 line from Holcomb 345 kV Ckt 1 substation to Sidney 345 Ckt 1 substation and upgrade any necessary terminal equipment to achieve a summer emergency rating of 1792 MVA. | 2024 ITP | Yes | Yes | 0.05872 | TBD | 977728865 | 0
GEN-2023-101 | 04 SOUTHEAST | ERIS | 220817 | 170296 | Sub - Conway 115 kV - Kirby 115 kV Terminal Upgrades | Conway 115 kV Terminal Upgrade | Install any necessary terminal equipment at Conway 115 kV substation to support a line from Conway 115 kV substation to Kirby 115 kV substation with a summer emergency rating of 197 MVA. | 2024 ITP | Yes | Yes | 0.03261 | TBD | 0 | 0
GEN-2023-208 | 05 SOUTHWEST | ERIS | 220817 | 170296 | Sub - Conway 115 kV - Kirby 115 kV Terminal Upgrades | Conway 115 kV Terminal Upgrade | Install any necessary terminal equipment at Conway 115 kV substation to support a line from Conway 115 kV substation to Kirby 115 kV substation with a summer emergency rating of 197 MVA. | 2024 ITP | Yes | Yes | 0.03335 | TBD | 0 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220817 | 170296 | Sub - Conway 115 kV - Kirby 115 kV Terminal Upgrades | Conway 115 kV Terminal Upgrade | Install any necessary terminal equipment at Conway 115 kV substation to support a line from Conway 115 kV substation to Kirby 115 kV substation with a summer emergency rating of 197 MVA. | 2024 ITP | Yes | Yes | 0.04095 | TBD | 0 | 0
GEN-2023-208 | 05 SOUTHWEST | ERIS | 220817 | 170297 | Sub - Conway 115 kV - Kirby 115 kV Terminal Upgrades | Kirby 115 kV Terminal Upgrade | Install any necessary terminal equipment at Kirby 115 kV substation to support a line from Kirby 115 kV substation to Conway 115 kV substation with a summer emergency rating of 197 MVA. | 2024 ITP | Yes | Yes | 0.03335 | TBD | 0 | 0
GEN-2023-082 | 01 NORTH | ERIS | 220828 | TBD | Multi - Kingsbury County 115 Voltage Conversion | Kingsbury County 115 kV Voltage Conversion | Convert 8.6 miles Kingsbury County to Oldham to 115 kV | 2024 ITP | Yes | Yes | 0.03561 | 2026-10-30 | 84007000 | 0
GEN-2023-023 | 03 CENTRAL | ERIS | TBD | TBD | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Terminal Upgrade on Martin City East to Martin City West 161 kV line | 2024 ITP | Yes | Yes | 0.03061 | TBD | 786451 | 0
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Terminal Upgrade on Martin City East to Martin City West 161 kV line | 2024 ITP | Yes | Yes | 0.05722 | TBD | 786451 | 0
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Terminal Upgrade on Martin City East to Martin City West 161 kV line | 2024 ITP | Yes | Yes | 0.0461 | TBD | 786451 | 0
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Terminal Upgrade on Martin City East to Martin City West 161 kV line | 2024 ITP | Yes | Yes | 0.04624 | TBD | 786451 | 0
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Terminal Upgrade on Martin City East to Martin City West 161 kV line | 2024 ITP | Yes | Yes | 0.0381 | TBD | 786451 | 0
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Terminal Upgrade on Martin City East to Martin City West 161 kV line | 2024 ITP | Yes | Yes | 0.04377 | TBD | 786451 | 0
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Terminal Upgrade on Martin City East to Martin City West 161 kV line | 2024 ITP | Yes | Yes | 0.05018 | TBD | 786451 | 0
GEN-2023-101 | 04 SOUTHEAST | NRIS | 220817 | 170297 | Sub - Conway 115 kV - Kirby 115 kV Terminal Upgrades | Kirby 115 kV Terminal Upgrade | Install any necessary terminal equipment at Kirby 115 kV substation to support a line from Kirby 115 kV substation to Conway 115 kV substation with a summer emergency rating of 197 MVA. | 2024 ITP | Yes | Yes | 0.04095 | TBD | 0 | 0
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Beckham to Potter 345 kV Line | Build New Beckham to Potter 345 kV Line | Build a new Beckham to Potter 345 kV line (149.64 miles) to a minimum rating of 1792 MVA | 2024 ITP | Yes | Yes | 0.03032 | 2029-11-12 | 248416354 | 0
GEN-2023-073 | 03 CENTRAL | ERIS | TBD | TBD | Farber - Sumner County No. 10 Belle Plain 138 kV Rebuild | Farber - Sumner County No. 10 Belle Plain 138 kV Rebuild | Rebuild 10.33 miles 138 kV line from Farber to Sumner County line to 286 MVA | 2024 ITP | Yes | Yes | 0.03341 | TBD | 11639947 | 0
GEN-2023-073 | 03 CENTRAL | NRIS | TBD | TBD | Farber - Sumner County No. 10 Belle Plain 138 kV Rebuild | Farber - Sumner County No. 10 Belle Plain 138 kV Rebuild | Rebuild 10.33 miles 138 kV line from Farber to Sumner County line to 286 MVA | 2024 ITP | Yes | Yes | 0.03713 | TBD | 11639947 | 0
GEN-2023-082 | 01 NORTH | NRIS | 220828 | TBD | Multi - Kingsbury County 115 Voltage Conversion | Kingsbury County 115 kV Voltage Conversion | Convert 8.6 miles Kingsbury County to Oldham to 115 kV | 2024 ITP | Yes | Yes | 0.0518 | 2026-10-30 | 84007000 | 0
GEN-2023-012 | 01 NORTH | NRIS | 220828 | TBD | Multi - Kingsbury County 115 Voltage Conversion | Kingsbury County 115 kV Voltage Conversion | Convert 8.6 miles Kingsbury County to Oldham to 115 kV | 2024 ITP | Yes | Yes | 0.31854 | 2026-10-30 | 84007000 | 0
GEN-2023-149 | 03 CENTRAL | NRIS | TBD | TBD | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Martin City (East) - Martin City (West) 161 kV Terminal Equipment | Terminal Upgrade on Martin City East to Martin City West 161 kV line | 2024 ITP | Yes | Yes | 0.09694 | TBD | 786451 | 0
GEN-2023-062 | 01 NORTH | ERIS | TBD | 143236 | Neset to Tioga 230kV Rebuild | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.04218 | TBD (12-month lead time) | 437516 | 437516
GEN-2023-097 | 01 NORTH | ERIS | TBD | 143236 | Neset to Tioga 230kV Rebuild | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.08485 | TBD (12-month lead time) | 437516 | 437516
GEN-2023-097 | 01 NORTH | NRIS | TBD | 143236 | Neset to Tioga 230kV Rebuild | Neset to Tioga 230kV Rebuild (DISIS-2017-001) (BEPC) | Rebuild the existing Neset to Tioga 230kV 1.0 mile line to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.05812 | TBD (12-month lead time) | 437516 | 437516
GEN-2023-062 | 01 NORTH | ERIS | TBD | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.04218 | TBD (12-month lead time) | 800000 | 800000
GEN-2023-097 | 01 NORTH | ERIS | TBD | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.08485 | TBD (12-month lead time) | 800000 | 800000
GEN-2023-097 | 01 NORTH | NRIS | TBD | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.05812 | TBD (12-month lead time) | 800000 | 800000
GEN-2023-012 | 01 NORTH | NRIS | TBD | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.04345 | TBD (12-month lead time) | 800000 | 800000
GEN-2023-105 | 01 NORTH | NRIS | TBD | 143237 | Tioga 230kV Terminal Upgrades | Tioga 230kV Terminal Upgrades (DISIS-2017-001) (MDU) | Upgrade terminal equipment at Tioga 230kV to achieve a minimum Summer/Emergency rating of 725 MVA | DISIS-2017-001 | Yes | Yes | 0.03468 | TBD (12-month lead time) | 800000 | 800000
GEN-2023-023 | 03 CENTRAL | ERIS | TBD | 159069 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | DISIS-2017-002 | Yes | Yes | 0.10243 | TBD (24 month lead time) | 112911 | 112911
GEN-2023-037 | 03 CENTRAL | ERIS | TBD | 159069 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Terminal upgrades on the Roanridge to Nashua 161 kV line 1 | Upgrade terminal equipment on the Roanridge to Nashua 161 kV line 1 to achieve a minimum rating of 340 MVA | DISIS-2017-002 | Yes | Yes | 0.12946 | TBD (24 month lead time) | 112911 | 112911
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | 158555 | N North Boston to GEN-2018-003-TAP 138 kV Rebuild | N North Boston to GEN-2018-003-TAP 138 kV Rebuild | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line with a minimum summer emergency rating of 170 MVA | DISIS-2018-001 | Yes | Yes | 0.03962 | TBD (30 month lead time) | 5006798 | 5006798
GEN-2023-212 | 04 SOUTHEAST | NRIS | TBD | 158555 | N North Boston to GEN-2018-003-TAP 138 kV Rebuild | N North Boston to GEN-2018-003-TAP 138 kV Rebuild | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line with a minimum summer emergency rating of 170 MVA | DISIS-2018-001 | Yes | Yes | 0.0411 | TBD (30 month lead time) | 5006798 | 5006798
GEN-2023-062 | 01 NORTH | ERIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | DISIS-2017-001 | Yes | Yes | 0.12651 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2023-097 | 01 NORTH | ERIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | DISIS-2017-001 | Yes | Yes | 0.12459 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2023-182 | 01 NORTH | ERIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | DISIS-2017-001 | Yes | Yes | 0.05538 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2023-097 | 01 NORTH | NRIS | TBD | 143226 | Broadland 345/230kV Transformer Replacement | Broadland 345/230kV Transformer Replacement (DISIS-2017-001) | Replace the existing Broadland 345/230kV Transformer to achieve a minimum Summer/Normal rating of 471 MVA | DISIS-2017-001 | Yes | Yes | 0.0804 | TBD (33 month lead time) | 10061320 | 10061320
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | 5SEDALA to G20-072-TAP 161 kV Ckt 1 Terminal Upgrade | 5SEDALA to G20-072-TAP 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the 5SEDALA to G20-072-TAP 161 kV line Ckt 1 to achieve a minimum rating of 342 MVA | DISIS-2021-001 | Yes | Yes | 0.04402 | TBD (36 month lead time) | 100000 | 100000
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | 5SEDALA to G20-072-TAP 161 kV Ckt 1 Terminal Upgrade | 5SEDALA to G20-072-TAP 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the 5SEDALA to G20-072-TAP 161 kV line Ckt 1 to achieve a minimum rating of 342 MVA | DISIS-2021-001 | Yes | Yes | 0.04147 | TBD (36 month lead time) | 100000 | 100000
GEN-2023-170 | 03 CENTRAL | ERIS | TBD | TBD | 5SEDALA to G20-072-TAP 161 kV Ckt 1 Terminal Upgrade | 5SEDALA to G20-072-TAP 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the 5SEDALA to G20-072-TAP 161 kV line Ckt 1 to achieve a minimum rating of 342 MVA | DISIS-2021-001 | Yes | Yes | 0.0656 | TBD (36 month lead time) | 100000 | 100000
GEN-2023-032 | 03 CENTRAL | NRIS | TBD | TBD | 5SEDALA to G20-072-TAP 161 kV Ckt 1 Terminal Upgrade | 5SEDALA to G20-072-TAP 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the 5SEDALA to G20-072-TAP 161 kV line Ckt 1 to achieve a minimum rating of 342 MVA | DISIS-2021-001 | Yes | Yes | 0.05211 | TBD (36 month lead time) | 100000 | 100000
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment at ARCHIE 5 161 kV to achieve a minimum rating of 249 MVA | DISIS-2021-001 | Yes | Yes | 0.04142 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment at ARCHIE 5 161 kV to achieve a minimum rating of 249 MVA | DISIS-2021-001 | Yes | Yes | 0.34536 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-032 | 03 CENTRAL | NRIS | TBD | TBD | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment at ARCHIE 5 161 kV to achieve a minimum rating of 249 MVA | DISIS-2021-001 | Yes | Yes | 0.09241 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-033 | 03 CENTRAL | NRIS | TBD | TBD | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment at ARCHIE 5 161 kV to achieve a minimum rating of 249 MVA | DISIS-2021-001 | Yes | Yes | 0.1069 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-149 | 03 CENTRAL | NRIS | TBD | TBD | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment at ARCHIE 5 161 kV to achieve a minimum rating of 249 MVA | DISIS-2021-001 | Yes | Yes | 0.12589 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-169 | 03 CENTRAL | NRIS | TBD | TBD | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment at ARCHIE 5 161 kV to achieve a minimum rating of 249 MVA | DISIS-2021-001 | Yes | Yes | 0.10716 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.05818 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.05639 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.05455 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.05485 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.05424 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.05718 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.04777 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-077 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03846 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-078 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03846 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-079 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03846 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03975 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03975 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.04291 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03413 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.0592 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.06261 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.06261 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.06261 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-224 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.0322 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-225 | 02 NEBRASKA | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.0322 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.12827 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.09782 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-034 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03335 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.12659 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.0451 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-065 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03217 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-073 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03898 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03855 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-149 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.12932 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.11076 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-170 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.08672 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.0996 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-219 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.04276 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-220 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.05678 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-221 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.05635 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.04862 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-132 | 04 SOUTHEAST | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03031 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.04464 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-033 | 03 CENTRAL | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.05546 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.05516 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-149 | 03 CENTRAL | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.29753 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-169 | 03 CENTRAL | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.04204 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-056 | 04 SOUTHEAST | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03443 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-064 | 04 SOUTHEAST | NRIS | TBD | TBD | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade | DISIS-2021-001 Phase 2 Contingent Upgrade – Upgrade Terminal Equipment on the PECULR 7 to PHILL 7 345 kV line Ckt 1 to achieve a minimum rating of 875 MVA (Minimum Rate A of 741 MVA required; Evergy has confirmed an actual Rate A/B of 956 MVA for this upgrade.) | DISIS-2021-001 | Yes | Yes | 0.03719 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.05697 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-062 | 01 NORTH | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.05526 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.05854 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.05671 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.0544 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.05687 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.05598 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.04959 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-077 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.06868 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-078 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.06868 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-079 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.06868 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.04062 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.04062 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.04397 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.03848 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.06238 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.06277 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.06277 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.06277 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-222 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.05569 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-223 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.05569 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-224 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.0625 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-225 | 02 NEBRASKA | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.0625 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-006 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.03053 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.04309 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.07909 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.09321 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.04148 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-073 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.03265 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.11646 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-149 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.10511 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.08607 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-170 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.06958 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.0768 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.03108 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-219 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.0331 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-220 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.04534 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-221 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.04499 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.04536 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-032 | 03 CENTRAL | NRIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.1543 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-033 | 03 CENTRAL | NRIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.18931 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.05587 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-169 | 03 CENTRAL | NRIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.19634 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-056 | 04 SOUTHEAST | NRIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.0311 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-064 | 04 SOUTHEAST | NRIS | TBD | TBD | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the PHILL 7 to SIBLEY 7 345 kV line Ckt 1 to achieve a minimum rating of 756 MVA | DISIS-2021-001 | Yes | Yes | 0.0335 | TBD (36 month lead time) | 150000 | 150000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Correct existing Lidar clearance issues on Sidewinder to Andrews 345 kV line to increase the line rating to 1400MVA SN/SE. | DISIS-2020-001 | Yes | Yes | 0.03183 | TBD (36 month lead time) | 400000 | 400000
GEN-2023-081 | 05 SOUTHWEST | NRIS | TBD | TBD | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Correct existing Lidar clearance issues on Sidewinder to Andrews 345 kV line to increase the line rating to 1400MVA SN/SE. | DISIS-2020-001 | Yes | Yes | 0.03098 | TBD (36 month lead time) | 400000 | 400000
GEN-2023-201 | 05 SOUTHWEST | NRIS | TBD | TBD | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Correct existing Lidar clearance issues on Sidewinder to Andrews 345 kV line to increase the line rating to 1400MVA SN/SE. | DISIS-2020-001 | Yes | Yes | 0.05204 | TBD (36 month lead time) | 400000 | 400000
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Sidewinder to Andrews 345 kV Lidar Clearance Correction | Correct existing Lidar clearance issues on Sidewinder to Andrews 345 kV line to increase the line rating to 1400MVA SN/SE. | DISIS-2020-001 | Yes | Yes | 0.06051 | TBD (36 month lead time) | 400000 | 400000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | Correct existing Lidar clearance issues on Sidewinder to Hobbs 345 kV line to increase the line rating to 1400MVA SN/SE. | DISIS-2020-001 | Yes | Yes | 0.03183 | TBD (36 month lead time) | 400000 | 400000
GEN-2023-081 | 05 SOUTHWEST | NRIS | TBD | TBD | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | Correct existing Lidar clearance issues on Sidewinder to Hobbs 345 kV line to increase the line rating to 1400MVA SN/SE. | DISIS-2020-001 | Yes | Yes | 0.03098 | TBD (36 month lead time) | 400000 | 400000
GEN-2023-201 | 05 SOUTHWEST | NRIS | TBD | TBD | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | Correct existing Lidar clearance issues on Sidewinder to Hobbs 345 kV line to increase the line rating to 1400MVA SN/SE. | DISIS-2020-001 | Yes | Yes | 0.05204 | TBD (36 month lead time) | 400000 | 400000
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | Sidewinder to Hobbs 345 kV Lidar Clearance Correction | Correct existing Lidar clearance issues on Sidewinder to Hobbs 345 kV line to increase the line rating to 1400MVA SN/SE. | DISIS-2020-001 | Yes | Yes | 0.06051 | TBD (36 month lead time) | 400000 | 400000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new BROWN to SBROWN4 138kV line 2 | Build a new BROWN to SBROWN4 138kV line 2 | Build a new BROWN to SBROWN 138kV CKT2 (0.12 miles) to a typical rating of 286 MVA | DISIS-2021-001 | Yes | Yes | 0.03764 | TBD (36 month lead time) | 750000 | 750000
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new BROWN to SBROWN4 138kV line 2 | Build a new BROWN to SBROWN4 138kV line 2 | Build a new BROWN to SBROWN 138kV CKT2 (0.12 miles) to a typical rating of 286 MVA | DISIS-2021-001 | Yes | Yes | 0.03393 | TBD (36 month lead time) | 750000 | 750000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | 156498 | SPA Brown to Brown 138 kV Equipment Upgrade | SPA Brown to Brown 138 kV Equipment Upgrade | Upgrade the terminal equipment at Brown SPA to achieve a minimum summer/emergency rating of 478 MVA | DISIS-2017-002 | Yes | Yes | 0.03238 | TBD (36 month lead time) | 825000 | 825000
GEN-2023-034 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 75 MVAR cap bank at Viola 138 kV | Build a new 75 MVAR cap bank at Viola 138 kV | Build a new 75 MVAR cap bank at VIOLA 138 kV | DISIS-2021-001 | Yes | Yes | 0.22924 | TBD (36 month lead time) | 1000000 | 1000000
GEN-2023-065 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 75 MVAR cap bank at Viola 138 kV | Build a new 75 MVAR cap bank at Viola 138 kV | Build a new 75 MVAR cap bank at VIOLA 138 kV | DISIS-2021-001 | Yes | Yes | 0.03804 | TBD (36 month lead time) | 1000000 | 1000000
GEN-2023-075 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 75 MVAR cap bank at Viola 138 kV | Build a new 75 MVAR cap bank at Viola 138 kV | Build a new 75 MVAR cap bank at VIOLA 138 kV | DISIS-2021-001 | Yes | Yes | 0.03081 | TBD (36 month lead time) | 1000000 | 1000000
GEN-2023-076 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 75 MVAR cap bank at Viola 138 kV | Build a new 75 MVAR cap bank at Viola 138 kV | Build a new 75 MVAR cap bank at VIOLA 138 kV | DISIS-2021-001 | Yes | Yes | 0.03081 | TBD (36 month lead time) | 1000000 | 1000000
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | 156516 | Terminal Upgrades at Archie 161kV | Terminal Upgrades at Archie 161kV | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Yes | Yes | 0.11876 | TBD (36 month lead time) | 1455934 | 1455934
GEN-2023-032 | 03 CENTRAL | NRIS | TBD | 156516 | Terminal Upgrades at Archie 161kV | Terminal Upgrades at Archie 161kV | Upgrade terminal equipment at Archie 161 kV to achieve a minimum rating of 280 MVA | DISIS-2017-002 | Yes | Yes | 0.03119 | TBD (36 month lead time) | 1455934 | 1455934
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | JENSEN 4 to EL RENO4 138kV Line Rebuild | JENSEN 4 to EL RENO4 138kV Line Rebuild | Rebuild the existing JENSEN 4 to EL RENO4 138 kV line 1 (2.07 miles) to a minimum rating of 255 MVA | DISIS-2022-001 | Yes | Yes | 0.11175 | TBD (36 month lead time) | 1995809.13 | 1995809.13
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | JENSEN 4 to EL RENO4 138kV Line Rebuild | JENSEN 4 to EL RENO4 138kV Line Rebuild | Rebuild the existing JENSEN 4 to EL RENO4 138 kV line 1 (2.07 miles) to a minimum rating of 255 MVA | DISIS-2022-001 | Yes | Yes | 0.03995 | TBD (36 month lead time) | 1995809.13 | 1995809.13
GEN-2023-229 | 04 SOUTHEAST | ERIS | TBD | TBD | JENSEN 4 to EL RENO4 138kV Line Rebuild | JENSEN 4 to EL RENO4 138kV Line Rebuild | Rebuild the existing JENSEN 4 to EL RENO4 138 kV line 1 (2.07 miles) to a minimum rating of 255 MVA | DISIS-2022-001 | Yes | Yes | 0.03882 | TBD (36 month lead time) | 1995809.13 | 1995809.13
GEN-2023-035 | 04 SOUTHEAST | NRIS | TBD | TBD | JENSEN 4 to EL RENO4 138kV Line Rebuild | JENSEN 4 to EL RENO4 138kV Line Rebuild | Rebuild the existing JENSEN 4 to EL RENO4 138 kV line 1 (2.07 miles) to a minimum rating of 255 MVA | DISIS-2022-001 | Yes | Yes | 0.10087 | TBD (36 month lead time) | 1995809.13 | 1995809.13
GEN-2023-150 | 04 SOUTHEAST | NRIS | TBD | TBD | JENSEN 4 to EL RENO4 138kV Line Rebuild | JENSEN 4 to EL RENO4 138kV Line Rebuild | Rebuild the existing JENSEN 4 to EL RENO4 138 kV line 1 (2.07 miles) to a minimum rating of 255 MVA | DISIS-2022-001 | Yes | Yes | 0.04323 | TBD (36 month lead time) | 1995809.13 | 1995809.13
GEN-2023-229 | 04 SOUTHEAST | NRIS | TBD | TBD | JENSEN 4 to EL RENO4 138kV Line Rebuild | JENSEN 4 to EL RENO4 138kV Line Rebuild | Rebuild the existing JENSEN 4 to EL RENO4 138 kV line 1 (2.07 miles) to a minimum rating of 255 MVA | DISIS-2022-001 | Yes | Yes | 0.03522 | TBD (36 month lead time) | 1995809.13 | 1995809.13
GEN-2023-073 | 03 CENTRAL | NRIS | TBD | TBD | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.05164 | TBD (36 month lead time) | 526717200 | 526717200
GEN-2023-211 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.12545 | TBD (36 month lead time) | 289399200 | 289399200
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | HOC404 5 to BAX488 5 161kV Line Rebuild | HOC404 5 to BAX488 5 161kV Line Rebuild | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | DISIS-2022-001 | Yes | Yes | 0.03542 | TBD (36 month lead time) | 2543382.4 | 2543382.4
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | HOC404 5 to BAX488 5 161kV Line Rebuild | HOC404 5 to BAX488 5 161kV Line Rebuild | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | DISIS-2022-001 | Yes | Yes | 0.0936 | TBD (36 month lead time) | 2543382.4 | 2543382.4
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | HOC404 5 to BAX488 5 161kV Line Rebuild | HOC404 5 to BAX488 5 161kV Line Rebuild | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | DISIS-2022-001 | Yes | Yes | 0.16188 | TBD (36 month lead time) | 2543382.4 | 2543382.4
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | HOC404 5 to BAX488 5 161kV Line Rebuild | HOC404 5 to BAX488 5 161kV Line Rebuild | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | DISIS-2022-001 | Yes | Yes | 0.03313 | TBD (36 month lead time) | 2543382.4 | 2543382.4
GEN-2023-027 | 04 SOUTHEAST | ERIS | TBD | TBD | HOC404 5 to BAX488 5 161kV Line Rebuild | HOC404 5 to BAX488 5 161kV Line Rebuild | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | DISIS-2022-001 | Yes | Yes | 0.05911 | TBD (36 month lead time) | 2543382.4 | 2543382.4
GEN-2023-028 | 04 SOUTHEAST | ERIS | TBD | TBD | HOC404 5 to BAX488 5 161kV Line Rebuild | HOC404 5 to BAX488 5 161kV Line Rebuild | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | DISIS-2022-001 | Yes | Yes | 0.13352 | TBD (36 month lead time) | 2543382.4 | 2543382.4
GEN-2023-049 | 04 SOUTHEAST | ERIS | TBD | TBD | HOC404 5 to BAX488 5 161kV Line Rebuild | HOC404 5 to BAX488 5 161kV Line Rebuild | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | DISIS-2022-001 | Yes | Yes | 0.16081 | TBD (36 month lead time) | 2543382.4 | 2543382.4
GEN-2023-055 | 04 SOUTHEAST | ERIS | TBD | TBD | HOC404 5 to BAX488 5 161kV Line Rebuild | HOC404 5 to BAX488 5 161kV Line Rebuild | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | DISIS-2022-001 | Yes | Yes | 0.06935 | TBD (36 month lead time) | 2543382.4 | 2543382.4
GEN-2023-063 | 04 SOUTHEAST | ERIS | TBD | TBD | HOC404 5 to BAX488 5 161kV Line Rebuild | HOC404 5 to BAX488 5 161kV Line Rebuild | Rebuild 2.6 miles HOC404 5 to BAX488 5 161kV line ckt 1 to a minimum of 414 MVA | DISIS-2022-001 | Yes | Yes | 0.03884 | TBD (36 month lead time) | 2543382.4 | 2543382.4
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the 5LOSTVALY to TRUMAN5 161 kV line 1 | Rebuild the 5LOSTVALY to TRUMAN5 161 kV line 1 | Rebuild the 5LOSTVALY to TRUMAN5 161 kV line CKT1 (2.61 miles) to a minimum rating of 290 MVA | DISIS-2021-001 | Yes | Yes | 0.04284 | TBD (36 month lead time) | 3245500 | 3245500
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.0404 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03578 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03626 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04347 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03774 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04066 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05171 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05501 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05501 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05542 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06468 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03899 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04582 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04582 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04582 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-006 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03352 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.11948 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-023 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04546 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04187 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04393 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-034 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.08423 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04312 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-037 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04558 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.0445 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.0352 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-065 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.09093 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-073 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.08085 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-085 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03962 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04378 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-099 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05781 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.11228 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-149 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05166 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04318 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-170 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03471 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04404 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.124 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.124 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03758 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-219 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06508 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-220 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06692 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-221 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06724 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05532 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04355 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03349 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03589 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-075 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06034 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-076 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06034 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-100 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.20541 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.07763 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-102 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.20541 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.17559 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-138 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04818 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04845 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-161 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.0608 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04996 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04996 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-166 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03647 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-167 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03618 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-168 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03745 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-174 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03831 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03272 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05397 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03909 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-211 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06207 | TBD (36 month lead time) | 3733650 | 3733650
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05872 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05841 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.0583 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05307 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06083 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.0583 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05914 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06272 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.07393 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05835 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06212 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.0583 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.0583 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05805 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05805 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06276 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05831 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.099 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05872 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.0582 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05886 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05821 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06433 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06379 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05684 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.05865 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06268 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03206 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.08887 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03889 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-069 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03269 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.0372 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-100 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.17418 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-102 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.17418 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.11795 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04104 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-210 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03225 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-172 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04584 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-173 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04584 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-022 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.03192 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.04917 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-211 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150MVAR Capacitor Bank at THISTLE7 345kV | Build a new 150 MVAR Capacitor Bank at THISTLE7 345kV | DISIS-2022-001 | Yes | Yes | 0.06482 | TBD (36 month lead time) | 3733650 | 3733650
GEN-2023-063 | 04 SOUTHEAST | ERIS | TBD | TBD | GRDA1 5 to MCSTAP 5 161kV Line Rebuild | GRDA1 5 to MCSTAP 5 161kV Line Rebuild | Rebuild 4.33 miles GRDA1 5 to MCSTAP 5 161kV line ckt 1 to a minimum of 376 MVA | DISIS-2022-001 | Yes | Yes | 0.03783 | TBD (36 month lead time) | 4235709.92 | 4235709.92
GEN-2023-027 | 04 SOUTHEAST | NRIS | TBD | TBD | GRDA1 5 to MCSTAP 5 161kV Line Rebuild | GRDA1 5 to MCSTAP 5 161kV Line Rebuild | Rebuild 4.33 miles GRDA1 5 to MCSTAP 5 161kV line ckt 1 to a minimum of 376 MVA | DISIS-2022-001 | Yes | Yes | 0.03152 | TBD (36 month lead time) | 4235709.92 | 4235709.92
GEN-2023-213 | 04 SOUTHEAST | NRIS | TBD | TBD | GRDA1 5 to MCSTAP 5 161kV Line Rebuild | GRDA1 5 to MCSTAP 5 161kV Line Rebuild | Rebuild 4.33 miles GRDA1 5 to MCSTAP 5 161kV line ckt 1 to a minimum of 376 MVA | DISIS-2022-001 | Yes | Yes | 0.03219 | TBD (36 month lead time) | 4235709.92 | 4235709.92
GEN-2023-211 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Build a new BENTON to RANCHROAD 345 kV CKT1 & CKT2 | Build a new BENTON to RANCHROAD 345 kV line CKT1 & CKT2 (78.2 miles) to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.12545 | TBD (36 month lead time) | 289399200 | 289399200
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.06182 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.05505 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.05718 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07195 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.06143 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.06301 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07915 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.09175 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.09175 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.12486 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07789 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.06052 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07297 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07297 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07297 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-222 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03212 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-223 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03212 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-224 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03529 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-225 | 02 NEBRASKA | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03529 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.0988 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03105 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03047 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.05434 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.0314 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03048 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.09271 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.09271 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04144 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-100 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.0542 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04063 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-102 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.0542 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04952 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03173 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04566 | TBD (36 month lead time) | 4900000 | 4900000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03922 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03875 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03926 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.033 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04368 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03926 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03995 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04549 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03892 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03953 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04164 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03926 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03926 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03874 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03874 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03724 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03921 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.08282 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03921 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03909 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03943 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03842 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04694 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04625 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.0333 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03903 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.0321 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03355 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03429 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03429 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build 80 MVAR cap at PostRock 345 | Build 80 MVAR cap at PostRock 345 | Add a 80 MVAR Switched Shunt at PostRock 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04404 | TBD (36 month lead time) | 4900000 | 4900000
GEN-2023-135 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Rebuild the PATMOS to FULTON 115kV line CKT1 (14.95 miles) to a minimum rating of 172 MVA | DISIS-2021-001 | Yes | Yes | 0.03233 | TBD (36 month lead time) | 5093561 | 5093561
GEN-2023-151 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Rebuild the PATMOS to FULTON 115kV line CKT1 (14.95 miles) to a minimum rating of 172 MVA | DISIS-2021-001 | Yes | Yes | 0.0301 | TBD (36 month lead time) | 5093561 | 5093561
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Rebuild the PATMOS to FULTON 115kV line CKT1 (14.95 miles) to a minimum rating of 172 MVA | DISIS-2021-001 | Yes | Yes | 0.0312 | TBD (36 month lead time) | 5093561 | 5093561
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Rebuild the PATMOS to FULTON 115kV line CKT1 (14.95 miles) to a minimum rating of 172 MVA | DISIS-2021-001 | Yes | Yes | 0.04774 | TBD (36 month lead time) | 5093561 | 5093561
GEN-2023-212 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Rebuild 3PATMOS.W# to FULTON 3 115kV line 1 | Rebuild the PATMOS to FULTON 115kV line CKT1 (14.95 miles) to a minimum rating of 172 MVA | DISIS-2021-001 | Yes | Yes | 0.03846 | TBD (36 month lead time) | 5093561 | 5093561
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | Northeastern Switch to HAWTHRN4 138kV Line Rebuild | Northeastern Switch to HAWTHRN4 138kV Line Rebuild | Rebuild 2.42 miles N.E.S.-4 to HAWTHRN4 138kV line ckt 1 to a minimum of 192 MVA | DISIS-2022-001 | Yes | Yes | 0.03306 | TBD (36 month lead time) | 5566000 | 5566000
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | Northeastern Switch to HAWTHRN4 138kV Line Rebuild | Northeastern Switch to HAWTHRN4 138kV Line Rebuild | Rebuild 2.42 miles N.E.S.-4 to HAWTHRN4 138kV line ckt 1 to a minimum of 192 MVA | DISIS-2022-001 | Yes | Yes | 0.04293 | TBD (36 month lead time) | 5566000 | 5566000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.04884 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.04981 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05334 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05975 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05688 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05071 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05714 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.11037 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.11037 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.09381 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.11656 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05261 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05518 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05518 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05518 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.35064 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-023 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03247 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03124 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03321 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03263 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-037 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03253 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-099 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03498 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.25823 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03323 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03289 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.29857 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.29857 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03551 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.04996 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03091 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.08392 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.04103 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-161 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03837 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.04313 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.04313 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-168 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03011 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-174 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03238 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.04756 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05486 | TBD (36 month lead time) | 6222750 | 6222750
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07771 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07552 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07828 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05001 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.14895 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07828 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.08116 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.10704 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.06051 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07963 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.13684 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07828 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07828 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07578 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07578 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.11307 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07798 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.13403 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07764 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07745 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.0787 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07395 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.1132 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.11008 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05078 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.07679 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.08624 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.08347 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.06176 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05909 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.05909 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.48333 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.04161 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03942 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-172 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.19167 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-173 | 03 CENTRAL | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.19167 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03206 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-211 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03893 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | Build a new 250MVAR Capacitor Bank at CARPENTER 7 345kV | DISIS-2022-001 | Yes | Yes | 0.03309 | TBD (36 month lead time) | 6222750 | 6222750
GEN-2023-161 | 04 SOUTHEAST | ERIS | TBD | TBD | CTNWOOD4 to G22-231-TAP 138kV Line Rebuild | CTNWOOD4 to G22-231-TAP 138kV Line Rebuild | Rebuild 6.6 miles CTNWOOD4 to G22-231-TAP 138kV line ckt 1 to a minimum of 359 MVA | DISIS-2022-001 | Yes | Yes | 0.0308 | TBD (36 month lead time) | 6363449.4 | 6363449.4
GEN-2023-161 | 04 SOUTHEAST | NRIS | TBD | TBD | CTNWOOD4 to G22-231-TAP 138kV Line Rebuild | CTNWOOD4 to G22-231-TAP 138kV Line Rebuild | Rebuild 6.6 miles CTNWOOD4 to G22-231-TAP 138kV line ckt 1 to a minimum of 359 MVA | DISIS-2022-001 | Yes | Yes | 0.03113 | TBD (36 month lead time) | 6363449.4 | 6363449.4
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.08301 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07452 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.08404 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.10756 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.09064 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.088 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07925 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.24904 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.24904 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.17031 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.26223 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07625 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.09115 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.09115 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.09115 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.15262 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.22608 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-170 | 03 CENTRAL | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03022 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.14592 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.14592 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07284 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-100 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03796 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04093 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-102 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03796 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03572 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03321 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.07736 | TBD (36 month lead time) | 7000000 | 7000000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04328 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04262 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04341 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03482 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.05076 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04341 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.0443 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.05206 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04008 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04381 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04745 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04341 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04341 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04267 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04267 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04069 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04332 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.11839 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04326 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04316 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04357 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.04215 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.05399 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.05304 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03488 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.043 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.03295 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.13639 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.10058 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.10567 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.10567 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.08063 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-216 | 02 NEBRASKA | NRIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.0327 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-217 | 02 NEBRASKA | NRIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.0327 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-218 | 02 NEBRASKA | NRIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.0327 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-172 | 03 CENTRAL | NRIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.09021 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-173 | 03 CENTRAL | NRIS | TBD | TBD | Build 250 MVAR cap at Mingo 345 | Build 250 MVAR cap at Mingo 345 | Add a 250 MVAR Switched Shunt at Mingo 345 kV bus to improve steady state low voltage issues. | DISIS-2021-001 | Yes | Yes | 0.09021 | TBD (36 month lead time) | 7000000 | 7000000
GEN-2023-034 | 03 CENTRAL | ERIS | TBD | TBD | MIDLTNT4 to CRESWLN4 138kV Line Rebuild | MIDLTNT4 to CRESWLN4 138kV Line Rebuild | Rebuild 9.08 miles MIDLTNT4 to CRESWLN4 138kV line CKT 1 to a minimum of 397 MVA | DISIS-2022-001 | Yes | Yes | 0.04482 | TBD (36 month lead time) | 8754563.72 | 8754563.72
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | MIAMI to HOC404 5 161kV Line Rebuild | MIAMI to HOC404 5 161kV Line Rebuild | Rebuild 9.9 miles MIAMI to HOC404 5 161kV line ckt 1 to a minimum of 282 MVA | DISIS-2022-001 | Yes | Yes | 0.06465 | TBD (36 month lead time) | 9684417.6 | 9684417.6
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | MIAMI to HOC404 5 161kV Line Rebuild | MIAMI to HOC404 5 161kV Line Rebuild | Rebuild 9.9 miles MIAMI to HOC404 5 161kV line ckt 1 to a minimum of 282 MVA | DISIS-2022-001 | Yes | Yes | 0.11082 | TBD (36 month lead time) | 9684417.6 | 9684417.6
GEN-2023-027 | 04 SOUTHEAST | ERIS | TBD | TBD | MIAMI to HOC404 5 161kV Line Rebuild | MIAMI to HOC404 5 161kV Line Rebuild | Rebuild 9.9 miles MIAMI to HOC404 5 161kV line ckt 1 to a minimum of 282 MVA | DISIS-2022-001 | Yes | Yes | 0.03895 | TBD (36 month lead time) | 9684417.6 | 9684417.6
GEN-2023-028 | 04 SOUTHEAST | ERIS | TBD | TBD | MIAMI to HOC404 5 161kV Line Rebuild | MIAMI to HOC404 5 161kV Line Rebuild | Rebuild 9.9 miles MIAMI to HOC404 5 161kV line ckt 1 to a minimum of 282 MVA | DISIS-2022-001 | Yes | Yes | 0.13536 | TBD (36 month lead time) | 9684417.6 | 9684417.6
GEN-2023-049 | 04 SOUTHEAST | ERIS | TBD | TBD | MIAMI to HOC404 5 161kV Line Rebuild | MIAMI to HOC404 5 161kV Line Rebuild | Rebuild 9.9 miles MIAMI to HOC404 5 161kV line ckt 1 to a minimum of 282 MVA | DISIS-2022-001 | Yes | Yes | 0.16553 | TBD (36 month lead time) | 9684417.6 | 9684417.6
GEN-2023-055 | 04 SOUTHEAST | ERIS | TBD | TBD | MIAMI to HOC404 5 161kV Line Rebuild | MIAMI to HOC404 5 161kV Line Rebuild | Rebuild 9.9 miles MIAMI to HOC404 5 161kV line ckt 1 to a minimum of 282 MVA | DISIS-2022-001 | Yes | Yes | 0.0642 | TBD (36 month lead time) | 9684417.6 | 9684417.6
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | MIAMI to HOC404 5 161kV Line Rebuild | MIAMI to HOC404 5 161kV Line Rebuild | Rebuild 9.9 miles MIAMI to HOC404 5 161kV line ckt 1 to a minimum of 282 MVA | DISIS-2022-001 | Yes | Yes | 0.07305 | TBD (36 month lead time) | 9684417.6 | 9684417.6
GEN-2023-062 | 01 NORTH | ERIS | TBD | TBD | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to GOSPER 7 115 kV line 1 (8.61 miles) to a minimum emergency rating of 180 MVA | DISIS-2022-001 | Yes | Yes | 0.03005 | TBD (36 month lead time) | 11000000 | 11000000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to GOSPER 7 115 kV line 1 (8.61 miles) to a minimum emergency rating of 180 MVA | DISIS-2022-001 | Yes | Yes | 0.03532 | TBD (36 month lead time) | 11000000 | 11000000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to GOSPER 7 115 kV line 1 (8.61 miles) to a minimum emergency rating of 180 MVA | DISIS-2022-001 | Yes | Yes | 0.03573 | TBD (36 month lead time) | 11000000 | 11000000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to GOSPER 7 115 kV line 1 (8.61 miles) to a minimum emergency rating of 180 MVA | DISIS-2022-001 | Yes | Yes | 0.03961 | TBD (36 month lead time) | 11000000 | 11000000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to GOSPER 7 115 kV line 1 (8.61 miles) to a minimum emergency rating of 180 MVA | DISIS-2022-001 | Yes | Yes | 0.08539 | TBD (36 month lead time) | 11000000 | 11000000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to GOSPER 7 115 kV line 1 (8.61 miles) to a minimum emergency rating of 180 MVA | DISIS-2022-001 | Yes | Yes | 0.08365 | TBD (36 month lead time) | 11000000 | 11000000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the CAMBRIG7 to GOSPER 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to GOSPER 7 115 kV line 1 (8.61 miles) to a minimum emergency rating of 180 MVA | DISIS-2022-001 | Yes | Yes | 0.08365 | TBD (36 month lead time) | 11000000 | 11000000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 956 MVA | DISIS-2023-001 | No | Yes | 0.03005 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Build a new FINNEY7 to HOLCOMB7 345 kV line 2 | Build a new FINNEY7 to HOLCOMB7 345 kV line CKT2 (0.75 miles) to a minimum rating of 956 MVA | DISIS-2023-001 | No | Yes | 0.25136 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.119 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-062 | 01 NORTH | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.1052 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.135 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.11149 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.08812 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.11442 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.10604 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.17259 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.13383 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.13383 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild S3451 to G18-043-TAP Line_345kV | Rebuild approximately 12.83 miles of 345kV line from S3451 to G18-043-TAP | DISIS-2020-001 | Yes | Yes | 0.13383 | TBD (36 month lead time) | 14683216.52 | 14683216.52
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.03172 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.04318 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-100 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.03717 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.07334 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-102 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.03717 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.03596 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.0832 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-161 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.04199 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.10556 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.10556 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.14817 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-229 | 04 SOUTHEAST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.07129 | TBD (36 month lead time) | 14992216.4 | 14992216.4
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05733 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05742 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05549 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05319 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.04644 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05549 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05693 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05504 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.06865 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05464 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.04972 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05549 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05549 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05603 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05603 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.06077 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05571 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.09544 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05734 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05565 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05726 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05757 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05562 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05553 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.10858 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.05754 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.07438 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-027 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.03602 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-035 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.06395 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-063 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.03884 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.04841 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-150 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.07255 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-161 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.03263 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.09303 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.09303 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.18551 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-213 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.032 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.04794 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-229 | 04 SOUTHEAST | NRIS | TBD | TBD | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Sunnyside to G20-074-TAP 345 kV Line Rebuild | Rebuild 13.1 miles of 345 kV from Sunnyside to G20-074-Tap to a minimum of 1464 MVA | DISIS-2020-001 | Yes | Yes | 0.10358 | TBD (36 month lead time) | 14992216.4 | 14992216.4
GEN-2023-034 | 03 CENTRAL | ERIS | TBD | TBD | MIDLTNT4 to PECKHMT4 138kV Line Rebuild | MIDLTNT4 to PECKHMT4 138kV Line Rebuild | Rebuild 3.49 miles MIDLTNT4 to PECKHMT4 138kV line ckt 1 to a minimum of 325 MVA | DISIS-2022-001 | Yes | Yes | 0.04482 | TBD (36 month lead time) | 16159304.84 | 16159304.84
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | DISIS-2020-001 | Yes | Yes | 0.03006 | TBD (36 month lead time) | 16500000 | 16500000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | DISIS-2020-001 | Yes | Yes | 0.19507 | TBD (36 month lead time) | 16500000 | 16500000
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | DISIS-2020-001 | Yes | Yes | 0.07268 | TBD (36 month lead time) | 16500000 | 16500000
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | DISIS-2020-001 | Yes | Yes | 0.03312 | TBD (36 month lead time) | 16500000 | 16500000
GEN-2023-105 | 01 NORTH | NRIS | TBD | TBD | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build the FTTHOMP3 to FTTHOMP4 345kV Transformer 3 | Build a new FTTHOMP3 to FTTHOMP4 345-230 kV transformer 3 with a rating of 250/313 MVA | DISIS-2020-001 | Yes | Yes | 0.20197 | TBD (36 month lead time) | 16500000 | 16500000
GEN-2023-075 | 04 SOUTHEAST | ERIS | TBD | TBD | FARML 4 to G18-079-TAP 138kV Line Rebuild | FARML 4 to G18-079-TAP 138kV Line Rebuild | Rebuild 8.16 miles FARML 4 to G18-079-TAP 138kV line ckt 1 to a minimum of 403 MVA | DISIS-2022-001 | Yes | Yes | 0.03391 | TBD (36 month lead time) | 18768000 | 18768000
GEN-2023-076 | 04 SOUTHEAST | ERIS | TBD | TBD | FARML 4 to G18-079-TAP 138kV Line Rebuild | FARML 4 to G18-079-TAP 138kV Line Rebuild | Rebuild 8.16 miles FARML 4 to G18-079-TAP 138kV line ckt 1 to a minimum of 403 MVA | DISIS-2022-001 | Yes | Yes | 0.03391 | TBD (36 month lead time) | 18768000 | 18768000
GEN-2023-028 | 04 SOUTHEAST | NRIS | TBD | TBD | FARML 4 to G18-079-TAP 138kV Line Rebuild | FARML 4 to G18-079-TAP 138kV Line Rebuild | Rebuild 8.16 miles FARML 4 to G18-079-TAP 138kV line ckt 1 to a minimum of 403 MVA | DISIS-2022-001 | Yes | Yes | 0.05718 | TBD (36 month lead time) | 18768000 | 18768000
GEN-2023-049 | 04 SOUTHEAST | NRIS | TBD | TBD | FARML 4 to G18-079-TAP 138kV Line Rebuild | FARML 4 to G18-079-TAP 138kV Line Rebuild | Rebuild 8.16 miles FARML 4 to G18-079-TAP 138kV line ckt 1 to a minimum of 403 MVA | DISIS-2022-001 | Yes | Yes | 0.05704 | TBD (36 month lead time) | 18768000 | 18768000
GEN-2023-055 | 04 SOUTHEAST | NRIS | TBD | TBD | FARML 4 to G18-079-TAP 138kV Line Rebuild | FARML 4 to G18-079-TAP 138kV Line Rebuild | Rebuild 8.16 miles FARML 4 to G18-079-TAP 138kV line ckt 1 to a minimum of 403 MVA | DISIS-2022-001 | Yes | Yes | 0.05761 | TBD (36 month lead time) | 18768000 | 18768000
GEN-2023-057 | 04 SOUTHEAST | NRIS | TBD | TBD | FARML 4 to G18-079-TAP 138kV Line Rebuild | FARML 4 to G18-079-TAP 138kV Line Rebuild | Rebuild 8.16 miles FARML 4 to G18-079-TAP 138kV line ckt 1 to a minimum of 403 MVA | DISIS-2022-001 | Yes | Yes | 0.05323 | TBD (36 month lead time) | 18768000 | 18768000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.04046 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.03388 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.03388 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.03388 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.03388 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.06914 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.06914 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.03639 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.03589 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.10617 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.05423 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.04051 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.03894 | TBD (36 month lead time) | 20000000 | 20000000
ASGI-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.0503 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-081 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.0555 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-201 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.06475 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-203 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.07586 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-209 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.03113 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.04238 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 | Build a new Yoakum 345/230 kV transformer 2 to a minimum rating of 557/641 MVA | DISIS-2021-001 | Yes | Yes | 0.08243 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the existing Shell Creek 345/230 kV transformer ckt 1 with a rating of 360 MVA | DISIS-2021-001 | Yes | Yes | 0.03621 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the existing Shell Creek 345/230 kV transformer ckt 1 with a rating of 360 MVA | DISIS-2021-001 | Yes | Yes | 0.09627 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the existing Shell Creek 345/230 kV transformer ckt 1 with a rating of 360 MVA | DISIS-2021-001 | Yes | Yes | 0.09627 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the Shell Creek 345/230 kV transformer ckt 1 | Replace the existing Shell Creek 345/230 kV transformer ckt 1 with a rating of 360 MVA | DISIS-2021-001 | Yes | Yes | 0.09627 | TBD (36 month lead time) | 20000000 | 20000000
GEN-2023-227 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild JEFFRSN4 to WILKES 4 138kV line 1 | Rebuild JEFFRSN4 to WILKES 4 138kV line 1 | Rebuild the JEFFRSN4 to WILKES4 138kV line CKT1 (11.11 miles) to a minimum rating of 258 MVA | DISIS-2022-001 | Yes | Yes | 0.08346 | TBD (36 month lead time) | 22200000 | 22200000
GEN-2023-241 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild JEFFRSN4 to WILKES 4 138kV line 1 | Rebuild JEFFRSN4 to WILKES 4 138kV line 1 | Rebuild the JEFFRSN4 to WILKES4 138kV line CKT1 (11.11 miles) to a minimum rating of 258 MVA | DISIS-2022-001 | Yes | Yes | 0.04373 | TBD (36 month lead time) | 22200000 | 22200000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04175 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0444 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0418 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05906 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05268 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05268 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05454 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04833 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04401 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0496 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0496 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0496 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-006 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04299 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04197 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-023 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0638 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0572 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.06055 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-034 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.19122 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05916 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-037 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.06403 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.03528 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-065 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.13884 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-073 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.09436 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05657 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-099 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.08641 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04768 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-149 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.06377 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0591 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-170 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04421 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.06087 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04514 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04514 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-219 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.08909 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-220 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.08875 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-221 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.08909 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.03962 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04916 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.03757 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-057 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04558 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0347 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0456 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-161 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04764 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04506 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04506 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-166 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05642 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-167 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05434 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-168 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05524 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-174 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04567 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04409 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05264 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-205 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.03178 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-210 | 04 SOUTHEAST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04373 | TBD (36 month lead time) | 24000000 | 24000000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04946 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05031 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04969 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.06169 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04969 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04819 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.03825 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04552 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04932 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04969 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04969 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05056 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05056 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04976 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04948 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04999 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04908 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.0509 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.03536 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.03665 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.05388 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | RENFROW7 to G18-128-TAP 345kV Line Rebuild | RENFROW7 to G18-128-TAP 345kV Line Rebuild | Rebuild 20.87 miles RENFROW7 to G18-128-TAP 345kV line ckt 1 to a minimum of 1573 MVA | DISIS-2022-001 | Yes | Yes | 0.04977 | TBD (36 month lead time) | 24000000 | 24000000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.73785 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.08263 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.07181 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.0407 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.1137 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.05652 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.10893 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.10236 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.70433 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-209 | 05 SOUTHWEST | NRIS | TBD | 170509 | Sweetwater to Chisholm 230 kV Line Rebuild | Sweetwater to Chisholm 230 kV Line Rebuild | Rebuild the Sweetwater to Chisholm 230 kV 11.15 mile Line to a minimum rating of 581 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.04988 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Sweetwater to Demarcation 230 kV Line Rebuild | Sweetwater to Demarcation 230 kV Line Rebuild | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.70433 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-209 | 05 SOUTHWEST | NRIS | TBD | TBD | Sweetwater to Demarcation 230 kV Line Rebuild | Sweetwater to Demarcation 230 kV Line Rebuild | Rebuild the Sweetwater to Demarcation 230 kV 5 mile Line to a minimum rating of 588 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.04988 | TBD (36 month lead time) | 25920000 | 25920000
GEN-2023-062 | 01 NORTH | ERIS | TBD | TBD | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the existing GOSPER 7 to JOHN.2 7 115 kV line 1 (24.13 miles) to a minimum emergency rating of 175 MVA | DISIS-2022-001 | Yes | Yes | 0.03005 | TBD (36 month lead time) | 26000000 | 26000000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the existing GOSPER 7 to JOHN.2 7 115 kV line 1 (24.13 miles) to a minimum emergency rating of 175 MVA | DISIS-2022-001 | Yes | Yes | 0.03532 | TBD (36 month lead time) | 26000000 | 26000000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the existing GOSPER 7 to JOHN.2 7 115 kV line 1 (24.13 miles) to a minimum emergency rating of 175 MVA | DISIS-2022-001 | Yes | Yes | 0.03573 | TBD (36 month lead time) | 26000000 | 26000000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the existing GOSPER 7 to JOHN.2 7 115 kV line 1 (24.13 miles) to a minimum emergency rating of 175 MVA | DISIS-2022-001 | Yes | Yes | 0.03961 | TBD (36 month lead time) | 26000000 | 26000000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the existing GOSPER 7 to JOHN.2 7 115 kV line 1 (24.13 miles) to a minimum emergency rating of 175 MVA | DISIS-2022-001 | Yes | Yes | 0.08539 | TBD (36 month lead time) | 26000000 | 26000000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the existing GOSPER 7 to JOHN.2 7 115 kV line 1 (24.13 miles) to a minimum emergency rating of 175 MVA | DISIS-2022-001 | Yes | Yes | 0.08365 | TBD (36 month lead time) | 26000000 | 26000000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the GOSPER 7 to JOHN.2 7 115kV Line 1 | Rebuild the existing GOSPER 7 to JOHN.2 7 115 kV line 1 (24.13 miles) to a minimum emergency rating of 175 MVA | DISIS-2022-001 | Yes | Yes | 0.08365 | TBD (36 month lead time) | 26000000 | 26000000
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.05192 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.1202 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.14622 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.03935 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-027 | 04 SOUTHEAST | ERIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.03693 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-028 | 04 SOUTHEAST | ERIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.04347 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-049 | 04 SOUTHEAST | ERIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.05145 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-075 | 04 SOUTHEAST | ERIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.03505 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-076 | 04 SOUTHEAST | ERIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.03505 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-050 | 03 CENTRAL | NRIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.03235 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.09334 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-028 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.03227 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-049 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build new NEOSHO 5 to RIV4525 161kV Line 2 | Build a new NEOSHO 5 to RIV4525 161 kV line 2 (28.41 miles) to a standard rating of 558/558 MVA | DISIS-2022-001 | Yes | Yes | 0.04058 | TBD (36 month lead time) | 29709558.63 | 29709558.63
GEN-2023-062 | 01 NORTH | ERIS | TBD | TBD | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to MCCOOK 7 115 kV line 1 (28.11 miles) to a minimum emergency rating of 200 MVA | DISIS-2022-001 | Yes | Yes | 0.03005 | TBD (36 month lead time) | 30000000 | 30000000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to MCCOOK 7 115 kV line 1 (28.11 miles) to a minimum emergency rating of 200 MVA | DISIS-2022-001 | Yes | Yes | 0.03532 | TBD (36 month lead time) | 30000000 | 30000000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to MCCOOK 7 115 kV line 1 (28.11 miles) to a minimum emergency rating of 200 MVA | DISIS-2022-001 | Yes | Yes | 0.03573 | TBD (36 month lead time) | 30000000 | 30000000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to MCCOOK 7 115 kV line 1 (28.11 miles) to a minimum emergency rating of 200 MVA | DISIS-2022-001 | Yes | Yes | 0.03961 | TBD (36 month lead time) | 30000000 | 30000000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to MCCOOK 7 115 kV line 1 (28.11 miles) to a minimum emergency rating of 200 MVA | DISIS-2022-001 | Yes | Yes | 0.08539 | TBD (36 month lead time) | 30000000 | 30000000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to MCCOOK 7 115 kV line 1 (28.11 miles) to a minimum emergency rating of 200 MVA | DISIS-2022-001 | Yes | Yes | 0.08365 | TBD (36 month lead time) | 30000000 | 30000000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the CAMBRIG7 to MCCOOK 7 115kV Line 1 | Rebuild the existing CAMBRIG7 to MCCOOK 7 115 kV line 1 (28.11 miles) to a minimum emergency rating of 200 MVA | DISIS-2022-001 | Yes | Yes | 0.08365 | TBD (36 month lead time) | 30000000 | 30000000
GEN-2023-161 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild DGRASSE4 to MOORLND4 138 kV line 1 | Rebuild DGRASSE4 to MOORLND4 138 kV line 1 | Rebuild the DEGRASSE4 to MOORLND4 138kV line CKT1 (38.45 miles) to a minimum rating of 353 MVA | DISIS-2021-001 | Yes | Yes | 0.03407 | TBD (36 month lead time) | 39000000 | 39000000
GEN-2023-161 | 04 SOUTHEAST | ERIS | TBD | TBD | DGRASSE4 to MOORLND4 138kV Line Rebuild | DGRASSE4 to MOORLND4 138kV Line Rebuild | Rebuild 38.45 miles DGRASSE4 to MOORLND4 138kV line ckt 1 to a minimum of 474 MVA | DISIS-2022-001 | Yes | Yes | 0.03407 | TBD (36 month lead time) | 39000000 | 39000000
GEN-2023-077 | 02 NEBRASKA | ERIS | TBD | TBD | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build a new ST JOE 7 to G22-208-TAP 345 kV line 1 (16.8 miles) to a standard rating of 1792/1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0391 | TBD (36 month lead time) | 44000000 | 44000000
GEN-2023-078 | 02 NEBRASKA | ERIS | TBD | TBD | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build a new ST JOE 7 to G22-208-TAP 345 kV line 1 (16.8 miles) to a standard rating of 1792/1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0391 | TBD (36 month lead time) | 44000000 | 44000000
GEN-2023-079 | 02 NEBRASKA | ERIS | TBD | TBD | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build a new ST JOE 7 to G22-208-TAP 345 kV line 1 (16.8 miles) to a standard rating of 1792/1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0391 | TBD (36 month lead time) | 44000000 | 44000000
GEN-2023-099 | 03 CENTRAL | ERIS | TBD | TBD | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build a new ST JOE 7 to G22-208-TAP 345 kV line 1 (16.8 miles) to a standard rating of 1792/1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03794 | TBD (36 month lead time) | 44000000 | 44000000
GEN-2023-033 | 03 CENTRAL | NRIS | TBD | TBD | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build a new ST JOE 7 to G22-208-TAP 345 kV line 1 (16.8 miles) to a standard rating of 1792/1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03466 | TBD (36 month lead time) | 44000000 | 44000000
GEN-2023-169 | 03 CENTRAL | NRIS | TBD | TBD | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build new ST JOE 7 to G22-208-TAP 345kV Line 1 | Build a new ST JOE 7 to G22-208-TAP 345 kV line 1 (16.8 miles) to a standard rating of 1792/1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03021 | TBD (36 month lead time) | 44000000 | 44000000
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ARCHIE 5 to G17-108-TAP 161 kV line Ckt 1 | Rebuild the ARCHIE 5 to G17-108-TAP 161 kV line Ckt 1 | Rebuild the ARCHIE 5 to G17-108-TAP 161 kV line Ckt 1 and Upgrade the Terminal Equipment to achieve a minimum rating of 470 MVA | DISIS-2021-001 | Yes | Yes | 0.11876 | TBD (36 month lead time) | 44600000 | 44600000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.08301 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.07452 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.08404 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.10756 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.09064 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.088 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.07925 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.24904 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.24904 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.17031 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.26223 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.07625 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.09115 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.09115 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.09115 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.15262 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.22608 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.14592 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.14592 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.07284 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-100 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.03796 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04093 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-102 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.03796 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.03572 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.03321 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.07736 | TBD (36 month lead time) | 50000000 | 50000000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04328 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04262 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04341 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.03482 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.05076 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04341 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.0443 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.05206 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04008 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04381 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04745 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04341 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04341 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04267 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04267 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04069 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04332 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.11839 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04326 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04316 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04357 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.04215 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.05399 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.05304 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.03488 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.043 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the REDWILO3 to G22-015-TAP 345kV Line 1 (NPPD) | Rebuild the existing REDWILO3 to G22-015-TAP 345 kV line 1 (38.26 miles) to a minimum emergency rating of 1150 MVA | DISIS-2022-001 | Yes | Yes | 0.03295 | TBD (36 month lead time) | 50000000 | 50000000
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03145 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.035 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03357 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03356 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.0648 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.0648 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.05527 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.06876 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03105 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03224 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03224 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03224 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.18754 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.14829 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.1661 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.1661 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03091 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.0523 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03389 | TBD (36 month lead time) | 57245088.88 | 57245088.88
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04832 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04697 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04867 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03126 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.09245 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04867 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.05044 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.06638 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03771 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.0495 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.08498 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04867 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04867 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04713 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04713 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.07035 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04848 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.08248 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04828 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04815 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04893 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.046 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.07018 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.06826 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03173 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04775 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.05382 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03461 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03288 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03288 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-172 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.08707 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-173 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the HITCHLAND 7 to CARPENTER 7 345kV Line 1 | Rebuild the existing HITCHLAND 7 to CARPENTER 7 345 kV line 1 (50.02 miles) to a minimum rating of 1550 MVA | DISIS-2022-001 | Yes | Yes | 0.08707 | TBD (36 month lead time) | 57245088.88 | 57245088.88
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04577 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-022 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03451 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03029 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03115 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04697 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-135 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03572 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.11749 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.11749 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.14666 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03616 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03549 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03047 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.06439 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03216 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03638 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04371 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-038 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03738 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-038 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04491 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03758 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04515 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.0314 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.10879 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.13071 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.10879 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.13071 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-177 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.0344 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-177 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04134 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.13581 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.16318 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.07628 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.09165 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-022 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03517 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-022 | 04 SOUTHEAST | NRIS | TBD | TBD | Treasure Island to G20-075-TAP 345kV New Line | Treasure Island to G20-075-TAP 345kV New Line | Build a new Treasure Island to G20-075-TAP 345 kV line (14.4 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.04225 | TBD (36 month lead time) | 60480000 | 60480000
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.0312 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03394 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03188 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03152 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03181 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.04106 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.05212 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.05212 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-174 | 04 SOUTHEAST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03455 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03324 | TBD (36 month lead time) | 64740000 | 64740000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03168 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03236 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.06781 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.0404 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.07527 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.12581 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.2071 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03174 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03124 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.0332 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.30465 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03275 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.19034 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.25359 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G22-011 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 8.3 mile 345 kV lines from G22-011 TAP to G22-114 TAP 345kV CKT 1 and CKT 2 to a minimum of 1610 MVA | DISIS-2022-001 | Yes | Yes | 0.03474 | TBD (36 month lead time) | 64740000 | 64740000
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the GRTBEN6 to G22-065-TAP 230kV Line 1 | Rebuild the GRTBEN6 to G22-065-TAP 230kV Line 1 | Rebuild the existing GRTBEND6 to G22-065-TAP 230 kV line 1 (37.3 miles) to a minimum emergency rating of 470 MVA | DISIS-2022-001 | Yes | Yes | 0.04129 | TBD (36 month lead time) | 67140000 | 67140000
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the GRTBEN6 to G22-065-TAP 230kV Line 1 | Rebuild the GRTBEN6 to G22-065-TAP 230kV Line 1 | Rebuild the existing GRTBEND6 to G22-065-TAP 230 kV line 1 (37.3 miles) to a minimum emergency rating of 470 MVA | DISIS-2022-001 | Yes | Yes | 0.03793 | TBD (36 month lead time) | 67140000 | 67140000
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the GRTBEN6 to G22-065-TAP 230kV Line 1 | Rebuild the GRTBEN6 to G22-065-TAP 230kV Line 1 | Rebuild the existing GRTBEND6 to G22-065-TAP 230 kV line 1 (37.3 miles) to a minimum emergency rating of 470 MVA | DISIS-2022-001 | Yes | Yes | 0.03793 | TBD (36 month lead time) | 67140000 | 67140000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Andrews to Road Runner 345 kV Line | Build New Andrews to Road Runner 345 kV Line | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.10946 | TBD (36 month lead time) | 70410000 | 70410000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build New Andrews to Road Runner 345 kV Line | Build New Andrews to Road Runner 345 kV Line | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.11899 | TBD (36 month lead time) | 70410000 | 70410000
ASGI-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Andrews to Road Runner 345 kV Line | Build New Andrews to Road Runner 345 kV Line | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.05339 | TBD (36 month lead time) | 70410000 | 70410000
GEN-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Andrews to Road Runner 345 kV Line | Build New Andrews to Road Runner 345 kV Line | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.04291 | TBD (36 month lead time) | 70410000 | 70410000
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Build New Andrews to Road Runner 345 kV Line | Build New Andrews to Road Runner 345 kV Line | Build a new 38.5 mile 345 kV circuit from Andrews to Road Runner with a standard rating of 1792 MVA | DISIS-2020-001 | Yes | Yes | 0.03484 | TBD (36 month lead time) | 70410000 | 70410000
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | Build new ARCHIE 5 to G17-108-TAP 161kV Line 2 | Build new ARCHIE 5 to G17-108-TAP 161kV Line 2 | Build a new ARCHIE 5 to G17-108-TAP 161 kV line 2 (28.73 miles) to a standard rating of 280/470 MVA | DISIS-2022-001 | Yes | Yes | 0.11876 | TBD (36 month lead time) | 78000000 | 78000000
GEN-2023-032 | 03 CENTRAL | NRIS | TBD | TBD | Build new ARCHIE 5 to G17-108-TAP 161kV Line 2 | Build new ARCHIE 5 to G17-108-TAP 161kV Line 2 | Build a new ARCHIE 5 to G17-108-TAP 161 kV line 2 (28.73 miles) to a standard rating of 280/470 MVA | DISIS-2022-001 | Yes | Yes | 0.03119 | TBD (36 month lead time) | 78000000 | 78000000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Build a new AXTELL 7 to KEARNEY7 115 kV line 2 (10.74 miles) to a standard rating of 229/390 MVA | DISIS-2022-001 | Yes | Yes | 0.0575 | TBD (36 month lead time) | 78000000 | 78000000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Build a new AXTELL 7 to KEARNEY7 115 kV line 2 (10.74 miles) to a standard rating of 229/390 MVA | DISIS-2022-001 | Yes | Yes | 0.06353 | TBD (36 month lead time) | 78000000 | 78000000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Build new AXTELL 7 to KEARNEY7 115kV Line 2 | Build a new AXTELL 7 to KEARNEY7 115 kV line 2 (10.74 miles) to a standard rating of 229/390 MVA | DISIS-2022-001 | Yes | Yes | 0.06353 | TBD (36 month lead time) | 78000000 | 78000000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03128 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03357 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03105 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.05627 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03565 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03565 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03824 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03883 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03883 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03883 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-222 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03303 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-223 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03303 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-006 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.10932 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-023 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.05626 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03869 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.04831 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.04415 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-037 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.05731 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.05653 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03906 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-073 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.07349 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-099 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.14902 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.04531 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.04822 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.04417 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-219 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.23354 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-220 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.27359 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-221 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.27762 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.04424 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-027 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03833 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-028 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03991 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-049 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03988 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-055 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03971 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-057 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03199 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-063 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03637 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-075 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.04358 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-076 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.04358 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-138 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03458 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03182 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-211 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.0399 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-213 | 04 SOUTHEAST | ERIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03642 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-034 | 03 CENTRAL | NRIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.07982 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-050 | 03 CENTRAL | NRIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.10363 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.03283 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-065 | 03 CENTRAL | NRIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.04642 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-073 | 03 CENTRAL | NRIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.12753 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-149 | 03 CENTRAL | NRIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.04248 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-219 | 03 CENTRAL | NRIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.17681 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-220 | 03 CENTRAL | NRIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.21546 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-221 | 03 CENTRAL | NRIS | TBD | TBD | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 | Build a new EMPEC 7 to GEN-2021-096 345 kV line 1 (30 miles) to a standard rating of 1180 MVA | DISIS-2022-001 | Yes | Yes | 0.21957 | TBD (36 month lead time) | 83000000 | 83000000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Oklaunion to G22-011-TAP 345kV New Line | Oklaunion to G22-011-TAP 345kV New Line | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.0339 | TBD (36 month lead time) | 87780000 | 87780000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Oklaunion to G22-011-TAP 345kV New Line | Oklaunion to G22-011-TAP 345kV New Line | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.03764 | TBD (36 month lead time) | 87780000 | 87780000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Oklaunion to G22-011-TAP 345kV New Line | Oklaunion to G22-011-TAP 345kV New Line | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.06291 | TBD (36 month lead time) | 87780000 | 87780000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Oklaunion to G22-011-TAP 345kV New Line | Oklaunion to G22-011-TAP 345kV New Line | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.10355 | TBD (36 month lead time) | 87780000 | 87780000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Oklaunion to G22-011-TAP 345kV New Line | Oklaunion to G22-011-TAP 345kV New Line | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.15233 | TBD (36 month lead time) | 87780000 | 87780000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Oklaunion to G22-011-TAP 345kV New Line | Oklaunion to G22-011-TAP 345kV New Line | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.09517 | TBD (36 month lead time) | 87780000 | 87780000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Oklaunion to G22-011-TAP 345kV New Line | Oklaunion to G22-011-TAP 345kV New Line | Build a new Oklaunion to G22-011-TAP 345 kV line (20.9 miles) to a minimum rating of 1324 MVA | DISIS-2022-001 | Yes | Yes | 0.12679 | TBD (36 month lead time) | 87780000 | 87780000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03672 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.0365 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03631 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.04476 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.0331 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.0331 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03542 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03693 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.04589 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.04165 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.04165 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.04165 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-006 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.10376 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-023 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.0756 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.0722 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.07272 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-034 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03644 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.07244 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-037 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.07555 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.21073 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.07449 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-065 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.04372 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-073 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.05513 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-085 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.04028 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.07778 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-099 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.06541 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-149 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.10008 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.07153 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-170 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.05806 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.07347 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.10153 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-219 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.06735 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-220 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.07006 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-221 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.0699 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-231 | 03 CENTRAL | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.18263 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-022 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03468 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03338 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-057 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.05637 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-063 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.07258 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03193 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-075 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.60077 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-076 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.60077 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-088 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.0391 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-134 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03619 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-166 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.0316 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-167 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03196 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-168 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03099 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03232 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03212 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-205 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.04697 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-210 | 04 SOUTHEAST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03978 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03177 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | NEOSHO 7 to G22-092-TAP 345kV Line Rebuild | Rebuild 41.32 miles NEOSHO 7 to G22-092-TAP 345kV line ckt 1 to a minimum of 1294 MVA | DISIS-2022-001 | Yes | Yes | 0.03094 | TBD (36 month lead time) | 96314434 | 96314434
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03145 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.035 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03357 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03356 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.0648 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.0648 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.05527 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.06876 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03105 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03224 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03224 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03224 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.18754 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.14829 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.1661 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.1661 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03091 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.0523 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03389 | TBD (36 month lead time) | 100000000 | 100000000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04832 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04697 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04867 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03126 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.09245 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04867 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.05044 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.06638 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03771 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.0495 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.08498 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04867 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04867 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04713 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04713 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.07035 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04848 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.08248 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04828 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04815 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04893 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.046 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.07018 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.06826 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03173 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.04775 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.05382 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.0464 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03461 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03288 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.03288 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.2596 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-172 | 03 CENTRAL | NRIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.08707 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-173 | 03 CENTRAL | NRIS | TBD | TBD | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build new HITCHLAND 7 to CARPENTER 7 345kV Line 2 | Build a new HITCHLAND 7 to CARPENTER 7 345 kV line 2 (50.02 miles) to a standard rating of 1550/1550 MVA | DISIS-2022-001 | Yes | Yes | 0.08707 | TBD (36 month lead time) | 100000000 | 100000000
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.0314 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.0314 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.0376 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-015 | 03 CENTRAL | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.20586 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-107 | 03 CENTRAL | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.18687 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-172 | 03 CENTRAL | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.2262 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-173 | 03 CENTRAL | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.2262 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.0409 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.03614 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.04258 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.15574 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-172 | 03 CENTRAL | NRIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.24758 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-173 | 03 CENTRAL | NRIS | TBD | TBD | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2 | Build a new 345kV line from SPERVIL7 to G21-068-TAP with an emergency rating of 1792 MVA | DISIS-2021-001 | Yes | Yes | 0.24758 | TBD (36 month lead time) | 102596000 | 102596000
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.03605 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.03074 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.03144 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.03685 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-135 | 04 SOUTHEAST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.03051 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.03059 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.0304 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.04556 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.03499 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.05006 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.07966 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.12899 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.18328 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.11708 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | G20-009 TAP to G22-114 TAP 345kV Line Rebuild (CKT 1 and CKT 2) | Rebuild the 13.9 mile 345 kV lines from G20-009 TAP to G22-114 TAP CKT 1 and CKT 2 to a minimum rating of 1795 MVA | DISIS-2022-001 | Yes | Yes | 0.14508 | TBD (36 month lead time) | 108420000 | 108420000
GEN-2023-012 | 01 NORTH | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.08265 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-062 | 01 NORTH | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.06187 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-082 | 01 NORTH | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.09204 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-097 | 01 NORTH | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.08946 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-105 | 01 NORTH | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.08774 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-154 | 01 NORTH | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.09527 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-182 | 01 NORTH | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.08125 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-011 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.10094 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-077 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.10852 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-078 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.10852 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-079 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.10852 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-116 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.07871 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-117 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.07871 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-133 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.0876 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-153 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.08272 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.10883 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.10884 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.10884 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.10884 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-222 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.10095 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-223 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.10095 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-224 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.1172 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-225 | 02 NEBRASKA | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.1172 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-023 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.08494 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-032 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.07231 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-033 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.08381 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-034 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.03082 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-036 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.07942 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-037 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.08524 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-050 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.03785 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-061 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.03183 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-065 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.03144 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-073 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.0342 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.06705 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-099 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.05951 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-149 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.06182 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-169 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.07741 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-171 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.08498 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-194 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.03384 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-219 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.05109 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-220 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.05342 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-221 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the ST JOE 7 to COOPER 3 345kV Line 1 | Rebuild the existing ST JOE 7 to COOPER 3 345 kV line 1 (64.61 miles) to a minimum rating of 1240 MVA | DISIS-2021-001 | Yes | Yes | 0.05315 | TBD (36 month lead time) | 112283778.92 | 112283778.92
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.04074 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.03201 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.03655 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.03655 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.09617 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.05525 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.03412 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.06126 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.10177 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.1672 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.25503 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.15344 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.03846 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.03269 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.03269 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.09015 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | G17-151-Tap to G18-015-Tap 345 kV New Line | G17-151-Tap to G18-015-Tap 345 kV New Line | Build a second G17-151-Tap to G18-015-Tap 345 kV line (78.295 miles) to a minimum rating of 997.3 MVA | DISIS-2022-001 | Yes | Yes | 0.29723 | TBD (36 month lead time) | 117410790.525 | 117410790.525
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.10825 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.04516 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.05586 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.09939 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-135 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.18692 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-151 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.04597 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-174 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.03285 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.03605 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.03066 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.22809 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.15021 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | WELSH 7 to WILKES 7 345kV Line Rebuild | WELSH 7 to WILKES 7 345kV Line Rebuild | Rebuild 30.63 miles WELSH 7 to WILKES 7 345kV line ckt 1 to a minimum of 1393 MVA | DISIS-2022-001 | Yes | Yes | 0.03166 | TBD (36 month lead time) | 119457000 | 119457000
GEN-2023-009 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.14583 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-035 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04214 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-038 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.06434 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-059 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.26016 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-069 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.07793 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-092 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.13452 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03313 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-135 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.34046 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04265 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-161 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03498 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04239 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04239 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-166 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03646 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-167 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03776 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-168 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03763 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-174 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04899 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-177 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.0535 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.05288 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-204 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.50439 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-205 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03603 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-210 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.0352 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-212 | 04 SOUTHEAST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.08176 | TBD (36 month lead time) | 126087000 | 126087000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04124 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04142 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04106 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-008 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04315 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04106 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04094 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03873 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04218 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04088 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04106 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04106 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.0413 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.0413 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.0411 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04125 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04114 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04116 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04156 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03825 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03849 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04844 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04133 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.05385 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.07014 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-027 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.09892 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-038 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03381 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-056 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.03061 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-063 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.10575 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-064 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.04032 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.05922 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-135 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.42675 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-151 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.09199 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-180 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.05885 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.13931 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-205 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.12873 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-212 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.1685 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-213 | 04 SOUTHEAST | NRIS | TBD | TBD | LYDIA7 to WELSH Line Rebuild | LYDIA7 to WELSH Line Rebuild | Rebuild 32.33 miles LYDIA7 to WELSH 345 kV line ckt 1 to a minimum of 1222 MVA | DISIS-2022-001 | Yes | Yes | 0.09671 | TBD (36 month lead time) | 126087000 | 126087000
GEN-2023-100 | 04 SOUTHEAST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07832 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.14761 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-102 | 04 SOUTHEAST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07832 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-104 | 04 SOUTHEAST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06999 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04506 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0551 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0551 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05261 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-229 | 04 SOUTHEAST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06171 | TBD (36 month lead time) | 134640000 | 134640000
ASGI-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03456 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-001 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03463 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-005 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0314 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04503 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-060 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0314 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-081 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03398 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-086 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03184 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.12923 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-120 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03031 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06109 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-142 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0314 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-143 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0314 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-158 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0322 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-159 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0322 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.08552 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-178 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03176 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.11988 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-184 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03458 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-195 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03161 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-201 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03447 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-203 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03483 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-208 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03504 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-209 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03471 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05669 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-236 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0349 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.10884 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.09532 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-100 | 04 SOUTHEAST | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07642 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04799 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-102 | 04 SOUTHEAST | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07642 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.08113 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-150 | 04 SOUTHEAST | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04609 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05331 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05331 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-177 | 04 SOUTHEAST | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03171 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04077 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Woodward EHV to Beckham 345 kV New Line | Woodward EHV to Beckham 345 kV New Line | Build a new Woodward EHV to Beckham 345 kV line (74.8 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03133 | TBD (36 month lead time) | 134640000 | 134640000
GEN-2023-101 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05132 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-150 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06197 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-164 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.08215 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-165 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.08215 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-167 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03573 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-168 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0325 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-188 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.14124 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-210 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03115 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-229 | 04 SOUTHEAST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06704 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-010 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0365 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-110 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03253 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-123 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.03999 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-176 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.0528 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-183 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.07548 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-228 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.08495 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-237 | 05 SOUTHWEST | ERIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06877 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-150 | 04 SOUTHEAST | NRIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06787 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.08593 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.08593 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.13433 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-210 | 04 SOUTHEAST | NRIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.051 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.05861 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.06913 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-134 | 04 SOUTHEAST | NRIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04266 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-229 | 04 SOUTHEAST | NRIS | TBD | TBD | Lawton Eastside to Draper 345 kV New Line | Lawton Eastside to Draper 345 kV New Line | Build a new LES to Draper 345 kV line (84 miles) to a minimum rating of 1792 MVA | DISIS-2022-001 | Yes | Yes | 0.04694 | TBD (36 month lead time) | 352800000 | 352800000
GEN-2023-085 | 03 CENTRAL | ERIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal Upgrade at Clinton City to a minimum rating of 78 MVA | DISIS-2017-002 | Yes | Yes | 0.03565 | TBD (36 month lead time) | TBD | TBD
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal Upgrade at Clinton City to a minimum rating of 78 MVA | DISIS-2017-002 | Yes | Yes | 0.16832 | TBD (36 month lead time) | TBD | TBD
GEN-2023-149 | 03 CENTRAL | ERIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal Upgrade at Clinton City to a minimum rating of 78 MVA | DISIS-2017-002 | Yes | Yes | 0.03042 | TBD (36 month lead time) | TBD | TBD
GEN-2023-170 | 03 CENTRAL | ERIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal Upgrade at Clinton City to a minimum rating of 78 MVA | DISIS-2017-002 | Yes | Yes | 0.04566 | TBD (36 month lead time) | TBD | TBD
GEN-2023-032 | 03 CENTRAL | NRIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal Upgrade at Clinton City to a minimum rating of 78 MVA | DISIS-2017-002 | Yes | Yes | 0.06718 | TBD (36 month lead time) | TBD | TBD
GEN-2023-033 | 03 CENTRAL | NRIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal Upgrade at Clinton City to a minimum rating of 78 MVA | DISIS-2017-002 | Yes | Yes | 0.03782 | TBD (36 month lead time) | TBD | TBD
GEN-2023-169 | 03 CENTRAL | NRIS | TBD | TBD | Terminal upgrades at Clinton (owned by AECI) | Terminal upgrades at Clinton (owned by AECI) | Terminal Upgrade at Clinton City to a minimum rating of 78 MVA | DISIS-2017-002 | Yes | Yes | 0.04949 | TBD (36 month lead time) | TBD | TBD
GEN-2023-219 | 03 CENTRAL | NRIS | TBD | TBD | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | Build 2nd LANG 3 to G22-007-TAP 115 kV Line | Build a 2nd LANG 3 to G22-007-TAP 115 kV line (0.41mi approx.) | DISIS-2023-001 | No | Yes | 0.35529 | TBD (36-month lead time) | 22000000 | 22000000
GEN-2023-097 | 01 NORTH | NRIS | TBD | TBD | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | DISIS-2023-001 | No | Yes | 0.06549 | TBD (36-month lead time) | 818000 | 818000
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | DISIS-2023-001 | No | Yes | 0.08168 | TBD (36-month lead time) | 818000 | 818000
GEN-2023-012 | 01 NORTH | NRIS | TBD | TBD | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | DISIS-2023-001 | No | Yes | 0.0786 | TBD (36-month lead time) | 818000 | 818000
GEN-2023-012 | 01 NORTH | NRIS | TBD | TBD | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | Build a new 7.5MVAR Switched Shunt at HANLON1-ER8 69kV; Build a new 7.5MVAR Switched Shunt at HANLON2-ER8 69kV | DISIS-2023-001 | No | Yes | 0.08427 | TBD (36-month lead time) | 818000 | 818000
GEN-2023-034 | 03 CENTRAL | NRIS | TBD | TBD | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Build a new BENTON to ELMCREEK 345 kV CKT1 & CKT2 | Build a new BENTON to ELMCREEK 345 kV line CKT1 & CKT2 (142.4 miles) to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.03881 | TBD (36-month lead time) | 526717200 | 526717200
GEN-2023-172 | 03 CENTRAL | NRIS | TBD | TBD | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Upgrade terminal equipment at Cudahy 115 kV substation to increase minimum summer/emergency rating to 135 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.06686 | TBD (36-month lead time) | 250000 | 250000
GEN-2023-173 | 03 CENTRAL | NRIS | TBD | TBD | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Cudahy to Crooked Creek 115 kV Terminal Equipment Upgrades | Upgrade terminal equipment at Cudahy 115 kV substation to increase minimum summer/emergency rating to 135 MVA | DISIS-2018-002/2019-001 | Yes | Yes | 0.06686 | TBD (36-month lead time) | 250000 | 250000
GEN-2023-199 | 02 NEBRASKA | ERIS | TBD | TBD | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a second 345/230kV transformer at Hoskins | DISIS-2018-002/2019-001 | Yes | Yes | 0.09774 | TBD (36-month lead time) | 46900000 | 46900000
GEN-2023-216 | 02 NEBRASKA | ERIS | TBD | TBD | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a second 345/230kV transformer at Hoskins | DISIS-2018-002/2019-001 | Yes | Yes | 0.05898 | TBD (36-month lead time) | 46900000 | 46900000
GEN-2023-217 | 02 NEBRASKA | ERIS | TBD | TBD | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a second 345/230kV transformer at Hoskins | DISIS-2018-002/2019-001 | Yes | Yes | 0.05898 | TBD (36-month lead time) | 46900000 | 46900000
GEN-2023-218 | 02 NEBRASKA | ERIS | TBD | TBD | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a second 345/230kV transformer at Hoskins | DISIS-2018-002/2019-001 | Yes | Yes | 0.05898 | TBD (36-month lead time) | 46900000 | 46900000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | DISIS-2018-002/2019-001 | Yes | Yes | 0.11167 | TBD (36-month lead time) | 46900000 | 46900000
GEN-2023-216 | 02 NEBRASKA | NRIS | TBD | TBD | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | DISIS-2018-002/2019-001 | Yes | Yes | 0.03682 | TBD (36-month lead time) | 46900000 | 46900000
GEN-2023-217 | 02 NEBRASKA | NRIS | TBD | TBD | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | DISIS-2018-002/2019-001 | Yes | Yes | 0.03682 | TBD (36-month lead time) | 46900000 | 46900000
GEN-2023-218 | 02 NEBRASKA | NRIS | TBD | TBD | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | Build a Second 345-230 kV Transformer at Hoskins_345kV | DISIS-2018-002/2019-001 | Yes | Yes | 0.03682 | TBD (36-month lead time) | 46900000 | 46900000
GEN-2023-099 | 03 CENTRAL | ERIS | TBD | TBD | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the NMANHT6 to ELMCREK6 230 kV line Ckt 1 to achieve a minimum rating of 450 MVA | DISIS-2021-001 | Yes | Yes | 0.04289 | TBD (36-month lead time) | 50000 | 50000
GEN-2023-065 | 03 CENTRAL | NRIS | TBD | TBD | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the NMANHT6 to ELMCREK6 230 kV line Ckt 1 to achieve a minimum rating of 450 MVA | DISIS-2021-001 | Yes | Yes | 0.03214 | TBD (36-month lead time) | 50000 | 50000
GEN-2023-172 | 03 CENTRAL | NRIS | TBD | TBD | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the NMANHT6 to ELMCREK6 230 kV line Ckt 1 to achieve a minimum rating of 450 MVA | DISIS-2021-001 | Yes | Yes | 0.04002 | TBD (36-month lead time) | 50000 | 50000
GEN-2023-173 | 03 CENTRAL | NRIS | TBD | TBD | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade | NMANHT6 to ELMCREK6 230 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the NMANHT6 to ELMCREK6 230 kV line Ckt 1 to achieve a minimum rating of 450 MVA | DISIS-2021-001 | Yes | Yes | 0.04002 | TBD (36-month lead time) | 50000 | 50000
GEN-2023-216 | 02 NEBRASKA | NRIS | TBD | TBD | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | DISIS-2023-001 | No | Yes | 0.30837 | TBD (36-month lead time) | 275518400 | 275518400
GEN-2023-217 | 02 NEBRASKA | NRIS | TBD | TBD | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | DISIS-2023-001 | No | Yes | 0.30837 | TBD (36-month lead time) | 275518400 | 275518400
GEN-2023-218 | 02 NEBRASKA | NRIS | TBD | TBD | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1 | Build a new substation east of Hosksins Substation. Loop in the Raun - Hoskins 345 kV Line, construct a new double circuit 345 kV line from Turtle Creek Substation, and construct a new 345 kV Line to G18-043 Tap. | DISIS-2023-001 | No | Yes | 0.30837 | TBD (36-month lead time) | 275518400 | 275518400
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1 | DISIS-2023-001 | No | Yes | 0.15039 | TBD (36-month lead time) | 92504000 | 92504000
GEN-2023-105 | 01 NORTH | NRIS | TBD | TBD | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | Build new GR PRAIRIE 3 to ANTELOPE 3 345kV Line 1 | Build a new GR PRAIRIE 3 to ANTELOPE 3 345 kV line 1 (50 miles) to a standard rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.07619 | TBD (36-month lead time) | 130000000 | 130000000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | DISIS-2023-001 | No | Yes | 0.0513 | TBD (36-month lead time) | 21623128 | 21623128
GEN-2023-194 | 03 CENTRAL | NRIS | TBD | TBD | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Build RIV4525 to G20-079-TAP 161 kV Line 2 | Build 2nd RIV4525 to G20-079-TAP 161 kV line to a minimum rating of 607 MVA | DISIS-2023-001 | No | Yes | 0.4535 | TBD (36-month lead time) | 21623128 | 21623128
GEN-2023-050 | 03 CENTRAL | NRIS | TBD | TBD | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | Build new STILWEL7 to G21-029-TAP 345 kV line to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.0549 | TBD (36-month lead time) | 89000000 | 89000000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | Build new STILWEL7 to G21-029-TAP 345 kV line to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.03392 | TBD (36-month lead time) | 89000000 | 89000000
GEN-2023-073 | 03 CENTRAL | NRIS | TBD | TBD | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | Build new STILWEL7 to G21-029-TAP 345 kV line to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.03279 | TBD (36-month lead time) | 89000000 | 89000000
GEN-2023-149 | 03 CENTRAL | NRIS | TBD | TBD | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | Build STILWEL7 to G21-029-TAP 345 kV Line 1 | Build new STILWEL7 to G21-029-TAP 345 kV line to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.27138 | TBD (36-month lead time) | 89000000 | 89000000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) | Rebuild 5MANSFDMN to G23-085-TAP 161 kV line 1 to a minimum rating of 231 MVA | DISIS-2023-001 | No | Yes | 0.04365 | TBD (36-month lead time) | 2220000 | 2220000
GEN-2023-085 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) | Rebuild 5MANSFDMN to G23-085-TAP 161 kV line 1 to a minimum rating of 231 MVA | DISIS-2023-001 | No | Yes | 0.70672 | TBD (36-month lead time) | 2220000 | 2220000
GEN-2023-033 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | Rebuild 5MOCITYB2 to G23-169-TAP 161 kV line 1 to a minimum rating of 278 MVA | DISIS-2023-001 | No | Yes | 0.27835 | TBD (36-month lead time) | 2000000 | 2000000
GEN-2023-169 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1 | Rebuild 5MOCITYB2 to G23-169-TAP 161 kV line 1 to a minimum rating of 278 MVA | DISIS-2023-001 | No | Yes | 0.64182 | TBD (36-month lead time) | 2000000 | 2000000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1 | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1 | Rebuild the existing BEATRCE7 to HARBINE7 115 kV line 1 (14.08 miles) to a minimum rating of 200 MVA | DISIS-2023-001 | No | Yes | 0.03394 | TBD (36-month lead time) | 14080000 | 14080000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1 | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1 | Rebuild the existing BEATRCE7 to HARBINE7 115 kV line 1 (14.08 miles) to a minimum rating of 200 MVA | DISIS-2023-001 | No | Yes | 0.03394 | TBD (36-month lead time) | 14080000 | 14080000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the COLMBUS4 to MEADOWGROVE4 230kV Line 1 | Rebuild the COLMBUS4 to MEADOWGROVE4 230kV Line 1 | Rebuild the existing COLMBUS4 to MEADOWGROVE4 230 kV line 1 (44.14 miles) to a minimum rating of 560 MVA | DISIS-2023-001 | No | Yes | 0.03636 | TBD (36-month lead time) | 83866000 | 83866000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1 | Rebuild EASTOWN7 to IATAN 7 345 kV line 1 to a minimum rating of 1270 MVA | DISIS-2023-001 | No | Yes | 0.04004 | TBD (36-month lead time) | 55000000 | 55000000
GEN-2023-082 | 01 NORTH | NRIS | TBD | TBD | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1 | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1 | Rebuild the existing FTRANDL4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | DISIS-2023-001 | No | Yes | 0.04554 | TBD (36-month lead time) | 84500000 | 84500000
GEN-2023-105 | 01 NORTH | NRIS | TBD | TBD | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1 | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1 | Rebuild the existing FTRANDL4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | DISIS-2023-001 | No | Yes | 0.05963 | TBD (36-month lead time) | 84500000 | 84500000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | Rebuild the existing FTTHOM2-LNX3 to GRPRAR2-LNX3 345 kV line 1 (123.95 miles) to a minimum rating of 1060 MVA | DISIS-2023-001 | No | Yes | 0.06394 | TBD (36-month lead time) | 40000000 | 40000000
GEN-2023-105 | 01 NORTH | NRIS | TBD | TBD | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | Rebuild the FTTHOM to GRPRAR 345kV Line 1 | Rebuild the existing FTTHOM2-LNX3 to GRPRAR2-LNX3 345 kV line 1 (123.95 miles) to a minimum rating of 1060 MVA | DISIS-2023-001 | No | Yes | 0.17559 | TBD (36-month lead time) | 40000000 | 40000000
GEN-2023-082 | 01 NORTH | NRIS | TBD | TBD | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | Rebuild the existing FTTHOMP4 to FTRANDL4 230 kV line 1 (87.32 miles) to a minimum rating of 600 MVA | DISIS-2023-001 | No | Yes | 0.04521 | TBD (36-month lead time) | 168000000 | 168000000
GEN-2023-105 | 01 NORTH | NRIS | TBD | TBD | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1 | Rebuild the existing FTTHOMP4 to FTRANDL4 230 kV line 1 (87.32 miles) to a minimum rating of 600 MVA | DISIS-2023-001 | No | Yes | 0.05919 | TBD (36-month lead time) | 168000000 | 168000000
GEN-2023-082 | 01 NORTH | NRIS | TBD | TBD | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1 | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1 | Rebuild the existing FTTHOMP4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | DISIS-2023-001 | No | Yes | 0.04554 | TBD (36-month lead time) | 84500000 | 84500000
GEN-2023-105 | 01 NORTH | NRIS | TBD | TBD | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1 | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1 | Rebuild the existing FTTHOMP4 to LAKPLAT-ER4 230 kV line 1 (43.34 miles) to a minimum rating of 605 MVA | DISIS-2023-001 | No | Yes | 0.05963 | TBD (36-month lead time) | 84500000 | 84500000
GEN-2023-105 | 01 NORTH | NRIS | TBD | TBD | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP | Loop the second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP and expand the G17-094-TAP substation | DISIS-2023-001 | No | Yes | 0.11336 | TBD (36-month lead time) | 15000000 | 35932692.3077
GEN-2023-032 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Rebuild LBRTYST5 to BRMGHAM5 161 kV line 1 to a minimum rating of 275 MVA | DISIS-2023-001 | No | Yes | 0.05518 | TBD (36-month lead time) | 9000000 | 9000000
GEN-2023-033 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Rebuild LBRTYST5 to BRMGHAM5 161 kV line 1 to a minimum rating of 275 MVA | DISIS-2023-001 | No | Yes | 0.68871 | TBD (36-month lead time) | 9000000 | 9000000
GEN-2023-036 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Rebuild LBRTYST5 to BRMGHAM5 161 kV line 1 to a minimum rating of 275 MVA | DISIS-2023-001 | No | Yes | 0.10257 | TBD (36-month lead time) | 9000000 | 9000000
GEN-2023-169 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1 | Rebuild LBRTYST5 to BRMGHAM5 161 kV line 1 to a minimum rating of 275 MVA | DISIS-2023-001 | No | Yes | 0.34479 | TBD (36-month lead time) | 9000000 | 9000000
GEN-2023-149 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | DISIS-2023-001 | No | Yes | 0.08497 | TBD (36-month lead time) | 31000000 | 31000000
GEN-2023-219 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | DISIS-2023-001 | No | Yes | 0.03712 | TBD (36-month lead time) | 31000000 | 31000000
GEN-2023-220 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | DISIS-2023-001 | No | Yes | 0.04577 | TBD (36-month lead time) | 31000000 | 31000000
GEN-2023-221 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | DISIS-2023-001 | No | Yes | 0.04477 | TBD (36-month lead time) | 31000000 | 31000000
GEN-2023-075 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | DISIS-2023-001 | No | Yes | 0.12553 | TBD (36-month lead time) | 31000000 | 31000000
GEN-2023-076 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1 | Rebuild NEOSHO 7 to G23-231-TAP 345 kV line 1 to a minimum rating of 1195 MVA | DISIS-2023-001 | No | Yes | 0.12553 | TBD (36-month lead time) | 31000000 | 31000000
GEN-2023-065 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the NEWTON 2 to ADAMS 2 69 kV Line 1 | Rebuild the NEWTON 2 to ADAMS 2 69 kV Line 1 | Rebuild NEWTON 2 to ADAMS 2 69 kV line 1 to a minimum rating of 82 MVA | DISIS-2023-001 | No | Yes | 0.22415 | TBD (36-month lead time) | 4500000 | 4500000
GEN-2023-194 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | Rebuild ORO110 to RIV4525 161 kV line 1 line to a minimum rating of 558 MVA | DISIS-2023-001 | No | Yes | 0.18785 | TBD (36-month lead time) | 25592475 | 25592475
GEN-2023-049 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | Rebuild the ORO110 5 to RIV4525 161 kV Line 1 | Rebuild ORO110 to RIV4525 161 kV line 1 line to a minimum rating of 558 MVA | DISIS-2023-001 | No | Yes | 0.03018 | TBD (36-month lead time) | 25592475 | 25592475
GEN-2023-012 | 01 NORTH | NRIS | TBD | TBD | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1 | Rebuild the PAHOJA__-BE4 to EAGLE___-NI4 230kV Line 1 | Rebuild the existing PAHOJA__-BE4 to EAGLE___-NI4 230 kV line 1 (22.24 miles) to a minimum rating of 450 MVA | DISIS-2023-001 | No | Yes | 0.05167 | TBD (36-month lead time) | 45100000 | 45100000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | DISIS-2023-001 | No | Yes | 0.15724 | TBD (36-month lead time) | 31064000 | 31064000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | DISIS-2023-001 | No | Yes | 0.15724 | TBD (36-month lead time) | 31064000 | 31064000
GEN-2023-216 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | DISIS-2023-001 | No | Yes | 0.16134 | TBD (36-month lead time) | 31064000 | 31064000
GEN-2023-217 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | DISIS-2023-001 | No | Yes | 0.16134 | TBD (36-month lead time) | 31064000 | 31064000
GEN-2023-218 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 | Rebuild the existing S3451-RAUN 3 to G18-043 TAP 345 kV line 1 (14.12 miles) to a minimum rating of 1485 MVA | DISIS-2023-001 | No | Yes | 0.16134 | TBD (36-month lead time) | 31064000 | 31064000
GEN-2023-012 | 01 NORTH | NRIS | TBD | TBD | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1 | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1 | Rebuild the existing SIOUXFL4 to PAHOJA__-BE4 230 kV line 1 (20.19 miles) to a minimum rating of 500 MVA | DISIS-2023-001 | No | Yes | 0.05167 | TBD (36-month lead time) | 42000000 | 42000000
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1 | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1 | Rebuild the existing SWEET W3 to GR ISLD3 345 kV line 1 (63.14 miles) to a minimum rating of 815 MVA | DISIS-2023-001 | No | Yes | 0.18361 | TBD (36-month lead time) | 138908000 | 138908000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1 | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1 | Rebuild the existing SWEET W3 to GR ISLD3 345 kV line 1 (63.14 miles) to a minimum rating of 815 MVA | DISIS-2023-001 | No | Yes | 0.04255 | TBD (36-month lead time) | 138908000 | 138908000
GEN-2023-050 | 03 CENTRAL | NRIS | TBD | TBD | Reconfigure the Neosho Transformers | Reconfigure the Neosho Transformers | Reconfigure the Neosho Transformers. Remove the two Neosho 161/138 kV transformers and add an additional 345/138 kV transformer. | DISIS-2023-001 | No | Yes | 0.03388 | TBD (36-month lead time) | 19662160 | 19662160
GEN-2023-085 | 03 CENTRAL | NRIS | TBD | TBD | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1 | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1 | Upgrade Terminal Equipment at CARTHAG5 to achieve a minimum summer/winter rating of 303/326 MVA | DISIS-2023-001 | No | Yes | 0.05149 | TBD (36-month lead time) | 250000 | 250000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1 | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1 | Upgrade Terminal Equipment at CARTHAG5 to achieve a minimum summer/winter rating of 303/326 MVA | DISIS-2023-001 | No | Yes | 0.2449 | TBD (36-month lead time) | 250000 | 250000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line 1 | Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line 1 | Upgrade Terminal Equipment on the RIV4525 to G20-079-TAP 161 kV Line 1 to a minimum Rate B of 607 MVA | DISIS-2023-001 | No | Yes | 0.05057 | TBD (36-month lead time) | 5165042 | 5165042
GEN-2023-194 | 03 CENTRAL | NRIS | TBD | TBD | Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line 1 | Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line 1 | Upgrade Terminal Equipment on the RIV4525 to G20-079-TAP 161 kV Line 1 to a minimum Rate B of 607 MVA | DISIS-2023-001 | No | Yes | 0.44706 | TBD (36-month lead time) | 5165042 | 5165042
GEN-2023-075 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the Neosho 345/161 kV Transformer | Upgrade the Neosho 345/161 kV Transformer | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | DISIS-2023-001 | No | Yes | 0.05015 | TBD (36-month lead time) | 12000000 | 12000000
GEN-2023-076 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the Neosho 345/161 kV Transformer | Upgrade the Neosho 345/161 kV Transformer | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | DISIS-2023-001 | No | Yes | 0.05015 | TBD (36-month lead time) | 12000000 | 12000000
GEN-2023-050 | 03 CENTRAL | NRIS | TBD | TBD | Upgrade the Neosho 345/161 kV Transformer | Upgrade the Neosho 345/161 kV Transformer | Upgrade Existing Neosho 345/161 kV Transformer to a rating of 650/715 MVA | DISIS-2023-001 | No | Yes | 0.09141 | TBD (36-month lead time) | 12000000 | 12000000
GEN-2023-087 | 03 CENTRAL | ERIS | TBD | TBD | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to achieve a minimum rating of 280 MVA. A revised facility study will be needed to account for substation modification | DISIS-2017-002 | Yes | Yes | 0.11876 | TBD (48 month lead time) | 41157960 | 41157960
GEN-2023-032 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line | Rebuild the decommissioned Archie to G17-108-TAP 161 kV line to achieve a minimum rating of 280 MVA. A revised facility study will be needed to account for substation modification | DISIS-2017-002 | Yes | Yes | 0.03119 | TBD (48 month lead time) | 41157960 | 41157960
GEN-2023-073 | 03 CENTRAL | NRIS | TBD | TBD | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.06154 | TBD (36-month lead time) | 204600000 | 204600000
GEN-2023-100 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.05219 | TBD (36-month lead time) | 204600000 | 204600000
GEN-2023-102 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.05219 | TBD (36-month lead time) | 204600000 | 204600000
GEN-2023-211 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.14747 | TBD (36-month lead time) | 204600000 | 204600000
GEN-2023-211 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Build a new BUFFALO FLATS to OPENSKY 345 kV CKT1 | Build a new BUFFALO FLATS to OPENSKY 345 kV line CKT1 (66 miles) to a minimum rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.14747 | TBD (36-month lead time) | 204600000 | 204600000
GEN-2023-153 | 02 NEBRASKA | NRIS | TBD | TBD | Build a new Gentleman Satellite substation | Build a new Gentleman Satellite substation | Build a new Gentleman Satellite substation | DISIS-2023-001 | No | Yes | 0.15039 | TBD (36-month lead time) | 100000000 | 100000000
ASGI-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.0529 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.03679 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-005 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.05404 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-060 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.05404 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-081 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.069 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-142 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.05404 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-143 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.05404 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-158 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.05845 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-159 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.05845 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-178 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.05292 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-195 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.06039 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-201 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.05635 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 | Build a new TOLK7 345/230 kV Transformer 3 to a minimum rating of 644 MVA | DISIS-2023-001 | No | Yes | 0.04686 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.07599 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.06604 | TBD (36-month lead time) | 16400000 | 16400000
ASGI-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.03307 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-201 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.03045 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.11483 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.03188 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 | Build a new TUCO7 345/230 kV Transformer 3 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.13769 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.07599 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.06604 | TBD (36-month lead time) | 16400000 | 16400000
ASGI-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.03307 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-201 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.03045 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.11483 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.03188 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 | Build a new TUCO7 345/230 kV Transformer 4 to a minimum rating of 675 MVA | DISIS-2023-001 | No | Yes | 0.13769 | TBD (36-month lead time) | 16400000 | 16400000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.12476 | TBD (36-month lead time) | 4743000 | 4743000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.10887 | TBD (36-month lead time) | 4743000 | 4743000
GEN-2023-086 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.03538 | TBD (36-month lead time) | 4743000 | 4743000
GEN-2023-209 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.04565 | TBD (36-month lead time) | 4743000 | 4743000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.19483 | TBD (36-month lead time) | 4743000 | 4743000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line 3 | Build a new TUCO7 to CRAWFISH 345 kV line CKT3 (1.53 miles) to a standard rating of 1792 MVA | DISIS-2023-001 | No | Yes | 0.23075 | TBD (36-month lead time) | 4743000 | 4743000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.11358 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.03794 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-069 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.04243 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.03798 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-100 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.04481 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.06958 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-102 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.04481 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-164 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.0308 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-165 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.0308 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-177 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.03471 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.06026 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-210 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.03428 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-209 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.03094 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.03433 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build new Double Circuit Crawfish to Seminole 765 kV Line | Build a new Double Circuit Crawfish to Seminole 765 kV line (325 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.07004 | TBD (36-month lead time) | 2104646400 | 2104646400
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build new Potter to Chisholm 765 kV Line | Build new Potter to Chisholm 765 kV Line | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.08946 | TBD (36-month lead time) | 932100000 | 932100000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Build new Potter to Chisholm 765 kV Line | Build new Potter to Chisholm 765 kV Line | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.20191 | TBD (36-month lead time) | 932100000 | 932100000
ASGI-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Potter to Chisholm 765 kV Line | Build new Potter to Chisholm 765 kV Line | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.06979 | TBD (36-month lead time) | 932100000 | 932100000
GEN-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Potter to Chisholm 765 kV Line | Build new Potter to Chisholm 765 kV Line | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.03377 | TBD (36-month lead time) | 932100000 | 932100000
GEN-2023-081 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Potter to Chisholm 765 kV Line | Build new Potter to Chisholm 765 kV Line | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.05852 | TBD (36-month lead time) | 932100000 | 932100000
GEN-2023-086 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Potter to Chisholm 765 kV Line | Build new Potter to Chisholm 765 kV Line | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.03625 | TBD (36-month lead time) | 932100000 | 932100000
GEN-2023-201 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Potter to Chisholm 765 kV Line | Build new Potter to Chisholm 765 kV Line | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.05039 | TBD (36-month lead time) | 932100000 | 932100000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Potter to Chisholm 765 kV Line | Build new Potter to Chisholm 765 kV Line | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.1496 | TBD (36-month lead time) | 932100000 | 932100000
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Potter to Chisholm 765 kV Line | Build new Potter to Chisholm 765 kV Line | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.04202 | TBD (36-month lead time) | 932100000 | 932100000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Potter to Chisholm 765 kV Line | Build new Potter to Chisholm 765 kV Line | Build a new Potter to Chisholm 765 kV line (168 miles) to a minimum rating of 4570 MVA | DISIS-2023-001 | No | Yes | 0.10552 | TBD (36-month lead time) | 932100000 | 932100000
GEN-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Tolk to Needmore 230 kV Line | Build new Tolk to Needmore 230 kV Line | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | DISIS-2023-001 | No | Yes | 0.03103 | TBD (36-month lead time) | 34125000 | 34125000
GEN-2023-005 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Tolk to Needmore 230 kV Line | Build new Tolk to Needmore 230 kV Line | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | DISIS-2023-001 | No | Yes | 0.03332 | TBD (36-month lead time) | 34125000 | 34125000
GEN-2023-060 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Tolk to Needmore 230 kV Line | Build new Tolk to Needmore 230 kV Line | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | DISIS-2023-001 | No | Yes | 0.03332 | TBD (36-month lead time) | 34125000 | 34125000
GEN-2023-142 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Tolk to Needmore 230 kV Line | Build new Tolk to Needmore 230 kV Line | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | DISIS-2023-001 | No | Yes | 0.03332 | TBD (36-month lead time) | 34125000 | 34125000
GEN-2023-143 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Tolk to Needmore 230 kV Line | Build new Tolk to Needmore 230 kV Line | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | DISIS-2023-001 | No | Yes | 0.03332 | TBD (36-month lead time) | 34125000 | 34125000
GEN-2023-158 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Tolk to Needmore 230 kV Line | Build new Tolk to Needmore 230 kV Line | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | DISIS-2023-001 | No | Yes | 0.49155 | TBD (36-month lead time) | 34125000 | 34125000
GEN-2023-159 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Tolk to Needmore 230 kV Line | Build new Tolk to Needmore 230 kV Line | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | DISIS-2023-001 | No | Yes | 0.49155 | TBD (36-month lead time) | 34125000 | 34125000
GEN-2023-178 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Tolk to Needmore 230 kV Line | Build new Tolk to Needmore 230 kV Line | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | DISIS-2023-001 | No | Yes | 0.03479 | TBD (36-month lead time) | 34125000 | 34125000
GEN-2023-195 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Tolk to Needmore 230 kV Line | Build new Tolk to Needmore 230 kV Line | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | DISIS-2023-001 | No | Yes | 0.03855 | TBD (36-month lead time) | 34125000 | 34125000
GEN-2023-203 | 05 SOUTHWEST | NRIS | TBD | TBD | Build new Tolk to Needmore 230 kV Line | Build new Tolk to Needmore 230 kV Line | Build a new Tolk to Needmore 230 kV line (13.65 miles) to a minimum rating of 796 MVA | DISIS-2023-001 | No | Yes | 0.04504 | TBD (36-month lead time) | 34125000 | 34125000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.03441 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-005 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.09327 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-060 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.09327 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-142 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.09327 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-143 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.09327 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-158 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.1116 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-159 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.1116 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-178 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.10782 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-195 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.11678 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-228 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.07242 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line 2 | Build a new TOLK6 to TUCO6 230 kV line CKT2 (54.58 miles) to a minimum rating of 840 MVA | DISIS-2023-001 | No | Yes | 0.07629 | TBD (36-month lead time) | 136450000 | 136450000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the DRYGULCH to G23-028-TAP line Ckt 1 to achieve a rating of 443 MVA | DISIS-2023-001 | No | Yes | 0.04697 | TBD (36-month lead time) | 254602 | 254602
GEN-2023-028 | 04 SOUTHEAST | NRIS | TBD | TBD | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the DRYGULCH to G23-028-TAP line Ckt 1 to achieve a rating of 443 MVA | DISIS-2023-001 | No | Yes | 0.6561 | TBD (36-month lead time) | 254602 | 254602
GEN-2023-049 | 04 SOUTHEAST | NRIS | TBD | TBD | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | DRYGULCH5 to G23-028-TAP 161 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the DRYGULCH to G23-028-TAP line Ckt 1 to achieve a rating of 443 MVA | DISIS-2023-001 | No | Yes | 0.53541 | TBD (36-month lead time) | 254602 | 254602
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | HARRING_WST6 to HARRNG_MID6 230 kV Ckt 1 Terminal Upgrade | HARRING_WST6 to HARRNG_MID6 230 kV Ckt 1 Terminal Upgrade | Upgrade Terminal Equipment on the HARRING_WST6 to HARRNG_MID6 line Ckt 1 to achieve a rating of 650 MVA | DISIS-2023-001 | No | Yes | 0.03134 | TBD (36-month lead time) | 3600000 | 3600000
GEN-2023-132 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line | Rebuild the existing 5HEBER.N# to GREERSF5 161 kV line | Rebuild the 5HEBER.N# to GREERSF5 161 kV line CKT1 (0 miles) to a minimum rating of 229 MVA | DISIS-2023-001 | No | Yes | 0.13854 | TBD (36-month lead time) | 0 | 0
GEN-2023-028 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | DISIS-2023-001 | No | Yes | 0.14531 | TBD (36-month lead time) | 14429000 | 14429000
GEN-2023-049 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | DISIS-2023-001 | No | Yes | 0.18833 | TBD (36-month lead time) | 14429000 | 14429000
GEN-2023-055 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Rebuild the existing AFTON 5 to KETCHUM5 161 kV line | Rebuild the AFTON 5 to KETCHUM5 161 kV line CKT1 (12.8 miles) to a minimum rating of 442 MVA | DISIS-2023-001 | No | Yes | 0.04494 | TBD (36-month lead time) | 14429000 | 14429000
GEN-2023-027 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line | Rebuild the existing BIRDHOL4 to JAY 4 138 kV line | Rebuild the BIRDHOL4 to JAY 4 138 kV line CKT1 (15.58 miles) to a minimum rating of 185 MVA | DISIS-2023-001 | No | Yes | 0.23832 | TBD (36-month lead time) | 230000 | 230000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | DISIS-2023-001 | No | Yes | 0.06176 | TBD (36-month lead time) | 133320000 | 133320000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | DISIS-2023-001 | No | Yes | 0.05909 | TBD (36-month lead time) | 133320000 | 133320000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | DISIS-2023-001 | No | Yes | 0.05909 | TBD (36-month lead time) | 133320000 | 133320000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | DISIS-2023-001 | No | Yes | 0.04161 | TBD (36-month lead time) | 133320000 | 133320000
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | DISIS-2023-001 | No | Yes | 0.03206 | TBD (36-month lead time) | 133320000 | 133320000
GEN-2023-211 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | DISIS-2023-001 | No | Yes | 0.03893 | TBD (36-month lead time) | 133320000 | 133320000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the existing CARPENTER7 to G23-015-TAP 345 kV line | Rebuild the CARPENTER7 to G23-015-TAP 345 kV line CKT1 (60.6 miles) to a minimum rating of 1205 MVA | DISIS-2023-001 | No | Yes | 0.03309 | TBD (36-month lead time) | 133320000 | 133320000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | DISIS-2023-001 | No | Yes | 0.08525 | TBD (36-month lead time) | 44160000 | 44160000
GEN-2023-035 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | DISIS-2023-001 | No | Yes | 0.05729 | TBD (36-month lead time) | 44160000 | 44160000
GEN-2023-069 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | DISIS-2023-001 | No | Yes | 0.08261 | TBD (36-month lead time) | 44160000 | 44160000
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | DISIS-2023-001 | No | Yes | 0.08471 | TBD (36-month lead time) | 44160000 | 44160000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | DISIS-2023-001 | No | Yes | 0.09243 | TBD (36-month lead time) | 44160000 | 44160000
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | DISIS-2023-001 | No | Yes | 0.08944 | TBD (36-month lead time) | 44160000 | 44160000
GEN-2023-210 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the existing ELKCITY6 to CHISHOLM6 230 kV line | Rebuild the ELKCITY6 to CHISHOLM6 230 kV line CKT1 (18.75 miles) to a minimum rating of 501 MVA | DISIS-2023-001 | No | Yes | 0.08192 | TBD (36-month lead time) | 44160000 | 44160000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.06176 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.06176 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.05909 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.05909 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.05909 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.05909 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.51667 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.51667 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.04161 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.04161 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.03206 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.03206 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-211 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.03893 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-211 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.03893 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.03309 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the existing FINNEY7 to G23-015-TAP 345 kV line | Rebuild the FINNEY7 to G23-015-TAP 345 kV line CKT1 (7.36 miles) to a minimum rating of 1341 MVA | DISIS-2023-001 | No | Yes | 0.03309 | TBD (36-month lead time) | 16192000 | 16192000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | DISIS-2023-001 | No | Yes | 0.03172 | TBD (36-month lead time) | 1650000 | 1650000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | DISIS-2023-001 | No | Yes | 0.03172 | TBD (36-month lead time) | 1650000 | 1650000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | DISIS-2023-001 | No | Yes | 0.03034 | TBD (36-month lead time) | 1650000 | 1650000
GEN-2023-222 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | DISIS-2023-001 | No | Yes | 0.03034 | TBD (36-month lead time) | 1650000 | 1650000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | DISIS-2023-001 | No | Yes | 0.03034 | TBD (36-month lead time) | 1650000 | 1650000
GEN-2023-223 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | DISIS-2023-001 | No | Yes | 0.03034 | TBD (36-month lead time) | 1650000 | 1650000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | DISIS-2023-001 | No | Yes | 0.26532 | TBD (36-month lead time) | 1650000 | 1650000
GEN-2023-015 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the existing FINNEY7 to HOLCOMB7 345 kV line | Rebuild the FINNEY7 to HOLCOMB7 345 kV line CKT1 (0.75 miles) to a minimum rating of 1486 MVA | DISIS-2023-001 | No | Yes | 0.26532 | TBD (36-month lead time) | 1650000 | 1650000
GEN-2023-027 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing GROVE 4 to JAY 4 138 kV line | Rebuild the existing GROVE 4 to JAY 4 138 kV line | Rebuild the GROVE 4 to JAY 4 138 kV line CKT1 (13.03 miles) to a minimum rating of 177 MVA | DISIS-2023-001 | No | Yes | 0.23832 | TBD (36-month lead time) | 230000 | 230000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | DISIS-2023-001 | No | Yes | 0.03363 | TBD (36-month lead time) | 149760000 | 149760000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | DISIS-2023-001 | No | Yes | 0.0457 | TBD (36-month lead time) | 149760000 | 149760000
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | DISIS-2023-001 | No | Yes | 0.0385 | TBD (36-month lead time) | 149760000 | 149760000
GEN-2023-135 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | DISIS-2023-001 | No | Yes | 0.09199 | TBD (36-month lead time) | 149760000 | 149760000
GEN-2023-212 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | DISIS-2023-001 | No | Yes | 0.08447 | TBD (36-month lead time) | 149760000 | 149760000
GEN-2023-227 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the existing LONGWD 7 to WILKES 7 345 kV line | Rebuild the LONGWD 7 to WILKES 7 345 kV line CKT1 (38.4 miles) to a minimum rating of 1424 MVA | DISIS-2023-001 | No | Yes | 0.14533 | TBD (36-month lead time) | 149760000 | 149760000
GEN-2023-028 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line | Rebuild the MIAMI 5 to AFTON 5 161 kV line CKT1 (13.5 miles) to a minimum rating of 419 MVA | DISIS-2023-001 | No | Yes | 0.13318 | TBD (36-month lead time) | 15635000 | 15635000
GEN-2023-049 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line | Rebuild the MIAMI 5 to AFTON 5 161 kV line CKT1 (13.5 miles) to a minimum rating of 419 MVA | DISIS-2023-001 | No | Yes | 0.17224 | TBD (36-month lead time) | 15635000 | 15635000
GEN-2023-055 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line | Rebuild the existing MIAMI 5 to AFTON 5 161 kV line | Rebuild the MIAMI 5 to AFTON 5 161 kV line CKT1 (13.5 miles) to a minimum rating of 419 MVA | DISIS-2023-001 | No | Yes | 0.04234 | TBD (36-month lead time) | 15635000 | 15635000
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line | Rebuild the existing NOELSW4 to G23-104-TAP 138 kV line | Rebuild the NOELSW4 to G23-104-TAP 138 kV line CKT1 (7.05 miles) to a minimum rating of 360 MVA | DISIS-2023-001 | No | Yes | 0.67397 | TBD (36-month lead time) | 7857895.85 | 7857895.85
GEN-2023-028 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line | Rebuild the PENSA 5 to G23-049-TAP 161 kV line CKT1 (6.5 miles) to a minimum rating of 449 MVA | DISIS-2023-001 | No | Yes | 0.3439 | TBD (36-month lead time) | 135805 | 135805
GEN-2023-049 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line | Rebuild the existing PENSA 5 to G23-049-TAP 161 kV line | Rebuild the PENSA 5 to G23-049-TAP 161 kV line CKT1 (6.5 miles) to a minimum rating of 449 MVA | DISIS-2023-001 | No | Yes | 0.46459 | TBD (36-month lead time) | 135805 | 135805
GEN-2023-028 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | DISIS-2023-001 | No | Yes | 0.14531 | TBD (36-month lead time) | 5291000 | 5291000
GEN-2023-049 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | DISIS-2023-001 | No | Yes | 0.18833 | TBD (36-month lead time) | 5291000 | 5291000
GEN-2023-055 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Rebuild the existing PENSA 5 to KETCHUM5 161 kV line | Rebuild the PENSA 5 to KETCHUM5 161 kV line CKT1 (4.8 miles) to a minimum rating of 451 MVA | DISIS-2023-001 | No | Yes | 0.04494 | TBD (36-month lead time) | 5291000 | 5291000
GEN-2023-061 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the PITTSB-7 to SEMINOL7 345 kV line CKT1 (51.27 miles) to a minimum rating of 1135 MVA | DISIS-2023-001 | No | Yes | 0.03084 | TBD (36-month lead time) | 112794000 | 112794000
GEN-2023-027 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the PITTSB-7 to SEMINOL7 345 kV line CKT1 (51.27 miles) to a minimum rating of 1135 MVA | DISIS-2023-001 | No | Yes | 0.05169 | TBD (36-month lead time) | 112794000 | 112794000
GEN-2023-035 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the PITTSB-7 to SEMINOL7 345 kV line CKT1 (51.27 miles) to a minimum rating of 1135 MVA | DISIS-2023-001 | No | Yes | 0.08137 | TBD (36-month lead time) | 112794000 | 112794000
GEN-2023-063 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the PITTSB-7 to SEMINOL7 345 kV line CKT1 (51.27 miles) to a minimum rating of 1135 MVA | DISIS-2023-001 | No | Yes | 0.05654 | TBD (36-month lead time) | 112794000 | 112794000
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the PITTSB-7 to SEMINOL7 345 kV line CKT1 (51.27 miles) to a minimum rating of 1135 MVA | DISIS-2023-001 | No | Yes | 0.06754 | TBD (36-month lead time) | 112794000 | 112794000
GEN-2023-188 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the PITTSB-7 to SEMINOL7 345 kV line CKT1 (51.27 miles) to a minimum rating of 1135 MVA | DISIS-2023-001 | No | Yes | 0.10221 | TBD (36-month lead time) | 112794000 | 112794000
GEN-2023-210 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the PITTSB-7 to SEMINOL7 345 kV line CKT1 (51.27 miles) to a minimum rating of 1135 MVA | DISIS-2023-001 | No | Yes | 0.05994 | TBD (36-month lead time) | 112794000 | 112794000
GEN-2023-213 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the PITTSB-7 to SEMINOL7 345 kV line CKT1 (51.27 miles) to a minimum rating of 1135 MVA | DISIS-2023-001 | No | Yes | 0.04455 | TBD (36-month lead time) | 112794000 | 112794000
GEN-2023-134 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the PITTSB-7 to SEMINOL7 345 kV line CKT1 (51.27 miles) to a minimum rating of 1135 MVA | DISIS-2023-001 | No | Yes | 0.06266 | TBD (36-month lead time) | 112794000 | 112794000
GEN-2023-229 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the existing PITTSB-7 to SEMINOL7 345 kV line | Rebuild the PITTSB-7 to SEMINOL7 345 kV line CKT1 (51.27 miles) to a minimum rating of 1135 MVA | DISIS-2023-001 | No | Yes | 0.07929 | TBD (36-month lead time) | 112794000 | 112794000
GEN-2023-005 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | DISIS-2023-001 | No | Yes | 0.11391 | TBD (36-month lead time) | 78679000 | 78679000
GEN-2023-060 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | DISIS-2023-001 | No | Yes | 0.11391 | TBD (36-month lead time) | 78679000 | 78679000
GEN-2023-142 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | DISIS-2023-001 | No | Yes | 0.11391 | TBD (36-month lead time) | 78679000 | 78679000
GEN-2023-143 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | DISIS-2023-001 | No | Yes | 0.11391 | TBD (36-month lead time) | 78679000 | 78679000
GEN-2023-158 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | DISIS-2023-001 | No | Yes | 0.07336 | TBD (36-month lead time) | 78679000 | 78679000
GEN-2023-159 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | DISIS-2023-001 | No | Yes | 0.07336 | TBD (36-month lead time) | 78679000 | 78679000
GEN-2023-178 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | DISIS-2023-001 | No | Yes | 0.04769 | TBD (36-month lead time) | 78679000 | 78679000
GEN-2023-195 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | DISIS-2023-001 | No | Yes | 0.06278 | TBD (36-month lead time) | 78679000 | 78679000
GEN-2023-203 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the existing PLANTX to G17-146-TAP 230 kV line | Rebuild the PLANTX to G17-146-TAP 230 kV line CKT1 (41.41 miles) to a minimum rating of 478 MVA | DISIS-2023-001 | No | Yes | 0.03077 | TBD (36-month lead time) | 78679000 | 78679000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | DISIS-2023-001 | No | Yes | 0.70433 | TBD (36-month lead time) | 12578000 | 12578000
GEN-2023-209 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Rebuild the existing STLN-DEMARCO6 to G23-101-TAP 230 kV line | Rebuild the STLN-DEMARC6 to G23-101-TAP 230 kV line CKT1 (6.62 miles) to a minimum rating of 385 MVA | DISIS-2023-001 | No | Yes | 0.04988 | TBD (36-month lead time) | 12578000 | 12578000
ASGI-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.03377 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.05766 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-005 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.05191 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-060 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.05191 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-081 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.03561 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-142 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.05191 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-143 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.05191 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-158 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.03939 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-159 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.03939 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-178 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.0325 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-195 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.03207 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-201 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.04145 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-203 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.07231 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-236 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.04636 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the existing SUNDOWN6 to WOLFFORTH6 230 kV line | Rebuild the SUNDOWN6 to WOLFFORTH6 230 kV line CKT1 (24.62 miles) to a minimum rating of 502 MVA | DISIS-2023-001 | No | Yes | 0.06075 | TBD (36-month lead time) | 46778000 | 46778000
GEN-2023-034 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | DISIS-2023-001 | No | Yes | 0.05936 | TBD (36-month lead time) | 63860000 | 63860000
GEN-2023-065 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | DISIS-2023-001 | No | Yes | 0.05686 | TBD (36-month lead time) | 63860000 | 63860000
GEN-2023-073 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | DISIS-2023-001 | No | Yes | 0.05874 | TBD (36-month lead time) | 63860000 | 63860000
GEN-2023-219 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | DISIS-2023-001 | No | Yes | 0.0847 | TBD (36-month lead time) | 63860000 | 63860000
GEN-2023-220 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | DISIS-2023-001 | No | Yes | 0.39005 | TBD (36-month lead time) | 63860000 | 63860000
GEN-2023-221 | 03 CENTRAL | NRIS | TBD | TBD | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the existing SWISVAL7 to G23-220-TAP 345 kV line | Rebuild the SWISVAL7 to G23-220-TAP 345 kV line CKT1 (25.07 miles) to a minimum rating of 1167 MVA | DISIS-2023-001 | No | Yes | 0.37871 | TBD (36-month lead time) | 63860000 | 63860000
GEN-2023-001 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line | Rebuild the existing TAYLOR3 to W_BENDER3 115 kV line | Rebuild the TAYLOR3 to W_BENDER3 115 kV line CKT1 (6.4 miles) to a minimum rating of 225 MVA | DISIS-2023-001 | No | Yes | 0.14019 | TBD (36-month lead time) | 6400000 | 6400000
GEN-2023-063 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line | Rebuild the TONECE7 to G23-138-TAP 345 kV line CKT1 (22.5 miles) to a minimum rating of 1317 MVA | DISIS-2023-001 | No | Yes | 0.06369 | TBD (36-month lead time) | 25749990 | 25749990
GEN-2023-064 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line | Rebuild the existing TONECE7 to G23-138-TAP 345 kV line | Rebuild the TONECE7 to G23-138-TAP 345 kV line CKT1 (22.5 miles) to a minimum rating of 1317 MVA | DISIS-2023-001 | No | Yes | 0.03403 | TBD (36-month lead time) | 25749990 | 25749990
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 1 | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT1 (1.53 miles) to a minimum rating of 1385 MVA | DISIS-2023-001 | No | Yes | 0.23075 | TBD (36-month lead time) | 3366000 | 3366000
GEN-2023-237 | 05 SOUTHWEST | NRIS | TBD | TBD | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Rebuild the existing TUCO7 to CRAWFISH 345 kV line 2 | Rebuild the TUCO7 to CRAWFISH 345 kV line CKT2 (1.53 miles) to a minimum rating of 1385 MVA | DISIS-2023-001 | No | Yes | 0.23075 | TBD (36-month lead time) | 3366000 | 3366000
GEN-2023-056 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | DISIS-2023-001 | No | Yes | 0.7688 | TBD (36-month lead time) | 3600000 | 3600000
GEN-2023-064 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | DISIS-2023-001 | No | Yes | 0.34334 | TBD (36-month lead time) | 3600000 | 3600000
GEN-2023-205 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | DISIS-2023-001 | No | Yes | 0.04018 | TBD (36-month lead time) | 3600000 | 3600000
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Rebuild the existing VAN BUR5 to VBI 5 161 kV line | Rebuild the VAN BUR5 to VBI 5 161 kV line CKTZ1 (0.22 miles) to a minimum rating of 383 MVA | DISIS-2023-001 | No | Yes | 0.04305 | TBD (36-month lead time) | 3600000 | 3600000
GEN-2023-205 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 170 MVA | DISIS-2023-001 | No | Yes | 0.1173 | TBD (36-month lead time) | 460000 | 460000
GEN-2023-210 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 170 MVA | DISIS-2023-001 | No | Yes | 0.03353 | TBD (36-month lead time) | 460000 | 460000
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 170 MVA | DISIS-2023-001 | No | Yes | 0.09675 | TBD (36-month lead time) | 460000 | 460000
GEN-2023-134 | 04 SOUTHEAST | NRIS | TBD | TBD | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Rebuild the existing WELETK4 to EC.HEN-4 138 kV line | Rebuild the WELETK4 to EC.HEN-4 138 kV line CKT1 (10.64 miles) to a minimum rating of 170 MVA | DISIS-2023-001 | No | Yes | 0.08069 | TBD (36-month lead time) | 460000 | 460000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1 | Rebuild the MEADOWGROVE4 to FTRANDL4 230kV Line 1 | Rebuild the existing MEADOWGROVE4 to FTRANDL4 230 kV line 1 (84.17 miles) to a minimum rating of 500 MVA | DISIS-2023-001 | No | Yes | 0.03636 | TBD (36-month lead time) | 161923000 | 161923000
GEN-2023-199 | 02 NEBRASKA | NRIS | TBD | TBD | S3458 to S3740 345 kV Ckt 2 New Line | S3458 - S3740 345 kV Ckt 2 New Line | Build an approximately 38 mile 345 kV line from S3458 to S3740 Ckt 2. | DISIS-2023-001 | No | Yes | 0.03783 | TBD (36-month lead time) | 98650000 | 98650000
GEN-2023-009 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | DISIS-2023-001 | No | Yes | 0.08525 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-035 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | DISIS-2023-001 | No | Yes | 0.05729 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-069 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | DISIS-2023-001 | No | Yes | 0.08261 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-092 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | DISIS-2023-001 | No | Yes | 0.08471 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-101 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | DISIS-2023-001 | No | Yes | 0.09243 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-104 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | DISIS-2023-001 | No | Yes | 0.08944 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-210 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the existing ELKCITY6 230/138 kV Transformer | Upgrade the ELKCITY6 230/138 kV Transformer to a minimum rating of 510 MVA | DISIS-2023-001 | No | Yes | 0.08192 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-134 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing FIXICO4 138/69 kV Transformer | Upgrade the existing FIXICO4 138/69 kV Transformer | Upgrade the existing FIXICO 138/69 kV Transformer to a minimum rating of 75 MVA | DISIS-2023-001 | No | Yes | 0.07433 | TBD (36-month lead time) | 7000000 | 7000000
GEN-2023-027 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing GROVE 161/138 kV Transformer | Upgrade the existing GROVE 161/138 kV Transformer | Upgrade the GROVE 161/138 kV Transformer to a minimum rating of 136 MVA | DISIS-2023-001 | No | Yes | 0.20407 | TBD (36-month lead time) | 7000000 | 7000000
GEN-2023-027 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing GROVE 161/138 kV Transformer | Upgrade the existing GROVE 161/138 kV Transformer | Upgrade the GROVE 161/138 kV Transformer to a minimum rating of 136 MVA | DISIS-2023-001 | No | Yes | 0.20407 | TBD (36-month lead time) | 7000000 | 7000000
GEN-2023-005 | 05 SOUTHWEST | NRIS | TBD | TBD | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | DISIS-2023-001 | No | Yes | 0.05761 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-005 | 05 SOUTHWEST | NRIS | TBD | TBD | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | DISIS-2023-001 | No | Yes | 0.05761 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-060 | 05 SOUTHWEST | NRIS | TBD | TBD | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | DISIS-2023-001 | No | Yes | 0.05761 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-060 | 05 SOUTHWEST | NRIS | TBD | TBD | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | DISIS-2023-001 | No | Yes | 0.05761 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-142 | 05 SOUTHWEST | NRIS | TBD | TBD | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | DISIS-2023-001 | No | Yes | 0.05761 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-142 | 05 SOUTHWEST | NRIS | TBD | TBD | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | DISIS-2023-001 | No | Yes | 0.05761 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-143 | 05 SOUTHWEST | NRIS | TBD | TBD | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | DISIS-2023-001 | No | Yes | 0.05761 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-143 | 05 SOUTHWEST | NRIS | TBD | TBD | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer | Upgrade the existing PLANTX 230/115 kV Transformer to a minimum rating of 321 MVA | DISIS-2023-001 | No | Yes | 0.05761 | TBD (36-month lead time) | 8100000 | 8100000
GEN-2023-056 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing VBI2 161/69 kV Transformer | Upgrade the existing VBI2 161/69 kV Transformer | Upgrade the existing VBI2 161/69 kV Transformer to a minimum rating of 123 MVA. | DISIS-2023-001 | No | Yes | 0.03711 | TBD (36-month lead time) | 50000 | 50000
GEN-2023-205 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing WLK X1 161/138 kV Transformer | Upgrade the existing WLK X1 161/138 kV Transformer | Upgrade the existing WLK X1 161/138 kV Transformer to a minimum rating of 129 MVA | DISIS-2023-001 | No | Yes | 0.06669 | TBD (36-month lead time) | 3606166 | 3606166
GEN-2023-210 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing WLK X1 161/138 kV Transformer | Upgrade the existing WLK X1 161/138 kV Transformer | Upgrade the existing WLK X1 161/138 kV Transformer to a minimum rating of 129 MVA | DISIS-2023-001 | No | Yes | 0.031 | TBD (36-month lead time) | 3606166 | 3606166
GEN-2023-088 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing WLK X1 161/138 kV Transformer | Upgrade the existing WLK X1 161/138 kV Transformer | Upgrade the existing WLK X1 161/138 kV Transformer to a minimum rating of 129 MVA | DISIS-2023-001 | No | Yes | 0.08146 | TBD (36-month lead time) | 3606166 | 3606166
GEN-2023-134 | 04 SOUTHEAST | NRIS | TBD | TBD | Upgrade the existing WLK X1 161/138 kV Transformer | Upgrade the existing WLK X1 161/138 kV Transformer | Upgrade the existing WLK X1 161/138 kV Transformer to a minimum rating of 129 MVA | DISIS-2023-001 | No | Yes | 0.04796 | TBD (36-month lead time) | 3606166 | 3606166

## All Thermal
SOLUTIONTYPE | Study Name | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME | Constraint Violation Criteria | Upgrade Name
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 127.42 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 127.42 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 127.42 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 127.42 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 127.42 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 127.42 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 118.41 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 118.41 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 118.41 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 118.41 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 118.41 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 118.41 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 116.98 | POI 763982_1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 116.98 | POI 763982_1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 116.98 | POI 763982_1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 116.72 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 116.72 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 116.72 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 116.67 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 116.67 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 116.67 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07256 | 110.65 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07256 | 110.65 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07256 | 110.65 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | FROM->TO | 640342 SHELCRK3 345 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.10479 | 106 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | FROM->TO | 640342 SHELCRK3 345 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.22941 | 106 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | FROM->TO | 640342 SHELCRK3 345 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.22941 | 106 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | FROM->TO | 640342 SHELCRK3 345 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.22941 | 106 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07256 | 105.27 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07256 | 105.27 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07256 | 105.27 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07256 | 105.26 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07256 | 105.26 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07256 | 105.26 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 640343 SHELCRK4 230 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.10479 | 105.18 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640343 SHELCRK4 230 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.22941 | 105.18 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640343 SHELCRK4 230 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.22941 | 105.18 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640343 SHELCRK4 230 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.22941 | 105.18 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640080 BELDEN 7 115 640228 HOSKINS7 115 1 | 115 | 115 | 0.05169 | 119.97 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640080 BELDEN 7 115 640228 HOSKINS7 115 1 | 115 | 115 | 0.05169 | 119.97 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640080 BELDEN 7 115 640228 HOSKINS7 115 1 | 115 | 115 | 0.05169 | 119.97 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640080 BELDEN 7 115 640228 HOSKINS7 115 1 | 115 | 115 | 0.05169 | 119.97 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640080 BELDEN 7 115 640228 HOSKINS7 115 1 | 115 | 115 | 0.05169 | 119.97 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640080 BELDEN 7 115 640228 HOSKINS7 115 1 | 115 | 115 | 0.05169 | 119.97 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 | 120 | 120 | 0.07233 | 108.87 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 | 120 | 120 | 0.07233 | 108.87 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 | 120 | 120 | 0.07233 | 108.87 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 | 120 | 120 | 0.07233 | 108.87 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 | 120 | 120 | 0.07233 | 108.87 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640136 COLMBUS7 115 640151 CRESTON7 115 1 | 120 | 120 | 0.07233 | 108.87 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 1195 | 1195 | 0.54231 | 108.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 1195 | 1195 | 0.54231 | 108.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 1195 | 1195 | 0.54231 | 108.46 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 1195 | 1195 | 0.54231 | 108.46 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 1195 | 1195 | 0.54231 | 108.46 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | 1195 | 1195 | 0.54231 | 108.46 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 108.06 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 108.06 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 108.06 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 108.06 | POI 763982_2 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 108.06 | POI 763982_2 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07233 | 108.06 | POI 763982_2 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 108 | POI 763982_1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 108 | POI 763982_1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 108 | POI 763982_1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 107.74 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 107.74 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 107.74 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 107.69 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 107.69 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07233 | 107.69 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22999 | 107.13 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22999 | 107.13 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22999 | 107.13 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22999 | 105.94 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22999 | 105.94 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22999 | 105.94 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07531 | 101.06 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07531 | 101.06 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07531 | 101.06 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 110.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 110.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 110.85 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.10462 | 106.16 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22922 | 106.16 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22922 | 106.16 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22922 | 106.16 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.10462 | 105.45 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22922 | 105.45 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22922 | 105.45 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22922 | 105.45 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 105.45 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 105.45 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 105.45 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 105.43 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 105.43 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 105.43 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 100.01 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 100.01 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07235 | 100.01 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 113.8 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 113.8 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 113.8 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 112.49 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 112.49 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 112.49 | POI 763982_4 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 107.71 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 107.71 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 107.71 | POI 763982_3 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 106.39 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 106.39 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 106.39 | POI 763982_0 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 105.48 | POI 763982_1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 105.48 | POI 763982_1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 105.48 | POI 763982_1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.10385 | 101.47 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22845 | 101.47 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22845 | 101.47 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.22845 | 101.47 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 101.18 | POI 763982_2 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 101.18 | POI 763982_2 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 101.18 | POI 763982_2 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07193 | 100.55 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07193 | 100.55 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640151 CRESTON7 115 640263 MADISON7 115 1 | 120 | 120 | 0.07193 | 100.55 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 100.04 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 100.04 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640263 MADISON7 115 640298 NORFOLK7 115 1 | 120 | 120 | 0.07193 | 100.04 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Line - Holt County 345 kV - Antelope 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-116 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.14973 | 107.82 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-117 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.14973 | 107.82 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-133 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.17809 | 107.82 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.08168 | 107.82 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.08168 | 107.82 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.08168 | 107.82 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3001:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-116 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.14973 | 107.77 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-117 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.14973 | 107.77 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-133 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.17809 | 107.77 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.08168 | 107.77 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.08168 | 107.77 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.08168 | 107.77 | P42:345:LES:L3503::103&ROKEBY.MOORE.CB3003:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-116 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.14973 | 107.74 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-117 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.14973 | 107.74 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-133 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.17809 | 107.74 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.08168 | 107.74 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.08168 | 107.74 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.08168 | 107.74 | P42:345:LES:L8589::103&ROKEBY.WAGENER.CB3002:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-116 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.13838 | 100.47 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-117 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.13838 | 100.47 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-133 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.16518 | 100.47 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.06895 | 100.47 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.06895 | 100.47 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | FROM->TO | 640277 MOORE 3 345 640590 MONOLITH 3 345 1 | 956 | 956 | 0.06895 | 100.47 | P12:345:LES:L3503::103&ROKEBY.MOORE.CKT1:: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640277 MOORE 3 345 996822 MOORE T1 115 1 | 336 | 400 | 0.06863 | 103.36 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640277 MOORE 3 345 996822 MOORE T1 115 1 | 336 | 400 | 0.06863 | 103.36 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | FROM->TO | 640277 MOORE 3 345 996822 MOORE T1 115 1 | 336 | 400 | 0.08163 | 103.36 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | FROM->TO | 640277 MOORE 3 345 996822 MOORE T1 115 1 | 336 | 400 | 0.06639 | 103.36 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640278 SHELDON7 115 996822 MOORE T1 115 1 | 336 | 400 | 0.06863 | 100.47 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640278 SHELDON7 115 996822 MOORE T1 115 1 | 336 | 400 | 0.06863 | 100.47 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 640278 SHELDON7 115 996822 MOORE T1 115 1 | 336 | 400 | 0.08163 | 100.47 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 640278 SHELDON7 115 996822 MOORE T1 115 1 | 336 | 400 | 0.06639 | 100.47 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Line - Elm Creek 345 kV - Tobias 345 kV New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-116 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 137 | 165 | 0.06241 | 103.58 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-117 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 137 | 165 | 0.06241 | 103.58 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-116 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 137 | 165 | 0.06243 | 104.3 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-117 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 137 | 165 | 0.06243 | 104.3 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 137 | 165 | 0.06028 | 140.27 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 137 | 165 | 0.06028 | 140.27 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 137 | 165 | 0.05428 | 127.68 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640287 N.PLATT7 115 640365 STOCKVL7 115 1 | 137 | 165 | 0.05428 | 127.68 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640082 BEVERLY7 115 640167 ENDERS 7 115 1 | 160 | 160 | 0.05493 | 122.4 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640082 BEVERLY7 115 640167 ENDERS 7 115 1 | 160 | 160 | 0.05493 | 122.4 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 640082 BEVERLY7 115 640167 ENDERS 7 115 1 | 160 | 160 | 0.19964 | 122.4 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 | 137 | 190 | 0.06018 | 117.4 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 | 137 | 190 | 0.06018 | 117.4 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640082 BEVERLY7 115 640326 REDWILO7 115 1 | 160 | 160 | 0.05493 | 107.8 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640082 BEVERLY7 115 640326 REDWILO7 115 1 | 160 | 160 | 0.05493 | 107.8 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | FROM->TO | 640082 BEVERLY7 115 640326 REDWILO7 115 1 | 160 | 160 | 0.19964 | 107.8 | P42:345:NPPD:BKR-GGS-3322:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.95 | POI 767280_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.95 | POI 767280_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.42285 | 106.95 | POI 767280_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.26916 | 106.95 | POI 767280_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.95 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.95 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.42285 | 106.95 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.26916 | 106.95 | 640325 REDWILO3 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.92 | POI 767280_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.92 | POI 767280_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.42285 | 106.92 | POI 767280_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.26916 | 106.92 | POI 767280_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.8 | POI 767280_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.8 | POI 767280_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.42285 | 106.8 | POI 767280_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.26916 | 106.8 | POI 767280_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.8 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.8 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.42285 | 106.8 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.26916 | 106.8 | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.2866 | 106.72 | POI 531451_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.2866 | 106.72 | POI 531451_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.42273 | 106.72 | POI 531451_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.26905 | 106.72 | POI 531451_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.72 | POI 531451_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.28671 | 106.72 | POI 531451_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.42285 | 106.72 | POI 531451_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.26916 | 106.72 | POI 531451_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 | 137 | 190 | 0.05418 | 106.21 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640326 REDWILO7 115 640365 STOCKVL7 115 1 | 137 | 190 | 0.05418 | 106.21 | 640183 GENTLMN3 345 640325 REDWILO3 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.08513 | 104.14 | POI 640065_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.28782 | 104.14 | POI 640065_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.28782 | 104.14 | POI 640065_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.2352 | 104.14 | POI 640065_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.30582 | 104.14 | POI 640065_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.09329 | 104.14 | POI 640065_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10051 | 104.14 | POI 640065_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10051 | 104.14 | POI 640065_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10051 | 104.14 | POI 640065_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.08366 | 103.56 | POI 640065_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.29113 | 103.56 | POI 640065_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.29113 | 103.56 | POI 640065_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.23401 | 103.56 | POI 640065_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.31003 | 103.56 | POI 640065_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.0929 | 103.56 | POI 640065_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10024 | 103.56 | POI 640065_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10024 | 103.56 | POI 640065_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10024 | 103.56 | POI 640065_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.08366 | 103.56 | P42:345:NPPD:BKR-AXT-3306:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.29113 | 103.56 | P42:345:NPPD:BKR-AXT-3306:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.29113 | 103.56 | P42:345:NPPD:BKR-AXT-3306:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.23401 | 103.56 | P42:345:NPPD:BKR-AXT-3306:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.31003 | 103.56 | P42:345:NPPD:BKR-AXT-3306:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.0929 | 103.56 | P42:345:NPPD:BKR-AXT-3306:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10024 | 103.56 | P42:345:NPPD:BKR-AXT-3306:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10024 | 103.56 | P42:345:NPPD:BKR-AXT-3306:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10024 | 103.56 | P42:345:NPPD:BKR-AXT-3306:::: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.08908 | 103.54 | POI 530583_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27603 | 103.54 | POI 530583_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27603 | 103.54 | POI 530583_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.21204 | 103.54 | POI 530583_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.29572 | 103.54 | POI 530583_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.09451 | 103.54 | POI 530583_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 103.54 | POI 530583_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 103.54 | POI 530583_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 103.54 | POI 530583_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.08908 | 103.54 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27603 | 103.54 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27603 | 103.54 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.21204 | 103.54 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.29572 | 103.54 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.09451 | 103.54 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 103.54 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 103.54 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 103.54 | 530583 POSTROCK7 345 560082 G16-050-TAP 345 1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.08958 | 103.42 | POI 530583_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27601 | 103.42 | POI 530583_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27601 | 103.42 | POI 530583_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.21213 | 103.42 | POI 530583_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.29567 | 103.42 | POI 530583_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.09475 | 103.42 | POI 530583_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10223 | 103.42 | POI 530583_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10223 | 103.42 | POI 530583_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10223 | 103.42 | POI 530583_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.30317 | 103.19 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.30317 | 103.19 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.56185 | 103.19 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | 956 | 956 | 0.26824 | 103.19 | P12:345:UMZW:# 725 #:: GI IN NE. GI-SWEET BRANCH FAULT:EHV: | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.32707 | 102.38 | POI 640374_8 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.32707 | 102.38 | POI 640374_8 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.07847 | 102.38 | POI 640374_8 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.33896 | 102.38 | POI 640374_8 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.06029 | 102.38 | POI 640374_8 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.06351 | 102.38 | POI 640374_8 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.06351 | 102.38 | POI 640374_8 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.06351 | 102.38 | POI 640374_8 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.08908 | 101.38 | POI 560082_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27603 | 101.38 | POI 560082_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27603 | 101.38 | POI 560082_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.21204 | 101.38 | POI 560082_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.29572 | 101.38 | POI 560082_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.09451 | 101.38 | POI 560082_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 101.38 | POI 560082_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 101.38 | POI 560082_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 101.38 | POI 560082_2 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.08908 | 101.2 | POI 560082_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27603 | 101.2 | POI 560082_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27603 | 101.2 | POI 560082_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.21204 | 101.2 | POI 560082_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.29572 | 101.2 | POI 560082_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.09451 | 101.2 | POI 560082_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 101.2 | POI 560082_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 101.2 | POI 560082_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 101.2 | POI 560082_1 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.08908 | 101.13 | POI 560082_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27603 | 101.13 | POI 560082_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.27603 | 101.13 | POI 560082_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.21204 | 101.13 | POI 560082_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.29572 | 101.13 | POI 560082_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.09451 | 101.13 | POI 560082_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 101.13 | POI 560082_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 101.13 | POI 560082_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 531451 MINGO 7 345 767280 G22-015-TAP 345 1 | 956 | 966 | 0.10199 | 101.13 | POI 560082_0 | Cumulative Impact | Line - Holcomb - Sidney 345 kV Ckt 1 New Line
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.14835 | 131.37 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.14835 | 131.37 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.14835 | 131.37 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.14835 | 131.37 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.14835 | 131.37 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.14835 | 131.37 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.53 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.53 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.53 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.89 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.89 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.89 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.89 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.89 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.89 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.05 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.05 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.05 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.69868 | 123.01 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.69914 | 122.07 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.77 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.77 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.77 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.65077 | 111.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15181 | 111.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15181 | 111.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15181 | 111.05 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.65077 | 111.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15181 | 111.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15181 | 111.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15181 | 111.05 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-216_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-216_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-218_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-218_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-217_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-217_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776342 G23-218XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776342 G23-218XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776302 G23-216XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776302 G23-216XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776322 G23-217XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776322 G23-217XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.65175 | 105.71 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.08132 | 105.71 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.08132 | 105.71 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.08132 | 105.71 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.69 | GEN-2016-043_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.69 | GEN-2016-043_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.69 | GEN-2016-043_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | FROM->TO | 640342 SHELCRK3 345 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.07365 | 103.79 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | FROM->TO | 640342 SHELCRK3 345 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.16754 | 103.79 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | FROM->TO | 640342 SHELCRK3 345 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.16754 | 103.79 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | FROM->TO | 640342 SHELCRK3 345 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.16754 | 103.79 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 640343 SHELCRK4 230 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.07365 | 102.99 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 640343 SHELCRK4 230 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.16754 | 102.99 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 640343 SHELCRK4 230 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.16754 | 102.99 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 640343 SHELCRK4 230 996785 SHELLCREEKT1 230 1 | 336 | 360 | 0.16754 | 102.99 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.69462 | 187.41 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.69799 | 163.21 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.59556 | 160.25 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.59556 | 159.84 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.59556 | 153.43 | P12:115:WERE:KELL-SSEN-115:::HV: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.59677 | 148.2 | P12:115:WERE:KNOB-MARS-115:::HV: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.5518 | 145.64 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.5518 | 145.64 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55213 | 144.39 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1:: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55213 | 144.38 | POI 640271_1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55155 | 142.65 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306:::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55155 | 142.65 | P42:345:NPPD:BKR-MOR-3306:::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.54808 | 139.49 | P42:345:NPPD:BKR-MOR-3312:::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.54847 | 138.59 | 640277 MOORE 3 345 640525 TOBIAS 3 345 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.54844 | 138.16 | POI 640525_3 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.54953 | 137.29 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 129.63 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 129.63 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 129.63 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 129.63 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 129.63 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 129.63 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 128.52 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 128.52 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 128.52 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.65 | 640386 TWIN CH4 230 640560 WAKEFIELD 4 230 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.65 | 640386 TWIN CH4 230 640560 WAKEFIELD 4 230 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.65 | 640386 TWIN CH4 230 640560 WAKEFIELD 4 230 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.43 | POI 763982_4 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.43 | POI 763982_4 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.43 | POI 763982_4 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.43 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.43 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.43 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.36 | P12:230:WAPA:TWINCH-SIOUXCY:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.36 | P12:230:WAPA:TWINCH-SIOUXCY:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 127.36 | P12:230:WAPA:TWINCH-SIOUXCY:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.95 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.95 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.95 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55264 | 122.61 | System Intact | TDF Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 114.17 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 114.17 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 114.17 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 114.07 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 114.07 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 114.07 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 114.07 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 114.07 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 114.07 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 110.1 | GEN-2023-216_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 110.1 | GEN-2023-216_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-011 | TO->FROM | 533303 MARSHAL3 115 533332 KNOB HL3 115 1 | 92 | 92 | 0.26016 | 105.87 | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | Cumulative Impact | Rebuild the MARSHAL3 to KNOB HL3 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-116 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.06612 | 105.55 | POI 763982_4 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-117 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.06612 | 105.55 | POI 763982_4 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-133 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.06038 | 105.55 | POI 763982_4 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.39783 | 105.55 | POI 763982_4 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.39783 | 105.55 | POI 763982_4 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.39783 | 105.55 | POI 763982_4 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-116 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.06612 | 105.55 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-117 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.06612 | 105.55 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-133 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.06038 | 105.55 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.39783 | 105.55 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.39783 | 105.55 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 635200 RAUN 3 345 640226 HOSKINS3 345 1 | 956 | 1135 | 0.39783 | 105.55 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.07992 | 105 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.07992 | 105 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.07992 | 105 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16686 | 102.29 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16686 | 102.29 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16686 | 102.29 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16686 | 101.28 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16686 | 101.28 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16686 | 101.28 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.38 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.38 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.38 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.02 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.02 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.02 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.02 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.02 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.02 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.11 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.11 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.11 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.6987 | 123.14 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.69915 | 121.94 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.81 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.81 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.81 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.7 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.7 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.7 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.7 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.7 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.7 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.65053 | 110.23 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15115 | 110.23 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15115 | 110.23 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15115 | 110.23 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.65053 | 110.23 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15115 | 110.23 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15115 | 110.23 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15115 | 110.23 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | GEN-2023-216_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | GEN-2023-216_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | GEN-2023-218_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | GEN-2023-218_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | GEN-2023-217_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | GEN-2023-217_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | 776301 GEN-2023-216 345 776342 G23-218XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | 776301 GEN-2023-216 345 776342 G23-218XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | 776301 GEN-2023-216 345 776302 G23-216XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | 776301 GEN-2023-216 345 776302 G23-216XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | 776301 GEN-2023-216 345 776322 G23-217XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.55 | 776301 GEN-2023-216 345 776322 G23-217XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.75 | GEN-2016-043_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.75 | GEN-2016-043_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.75 | GEN-2016-043_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.71 | 640588 TURTLE.CRK 3 345 643271 PLUMBCR.W 3 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.71 | 640588 TURTLE.CRK 3 345 643271 PLUMBCR.W 3 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.71 | 640588 TURTLE.CRK 3 345 643271 PLUMBCR.W 3 345 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.65157 | 105.24 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.08105 | 105.24 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.08105 | 105.24 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.08105 | 105.24 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.07355 | 104.19 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16747 | 104.19 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16747 | 104.19 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16747 | 104.19 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.07355 | 103.5 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16747 | 103.5 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16747 | 103.5 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 640343 SHELCRK4 230 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16747 | 103.5 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 640163 EMERSON7 115 640387 TWIN CH7 115 1 | 120 | 120 | 0.17093 | 100.8 | P12:230:WAPA:TWINCH-SIOUXCY:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.69731 | 169.46 | P12:115:WERE:KNOB-NPPD-115:::HV: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.69854 | 150.37 | 640208 HARBINE7 115 640426 STEELEC7 115 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.59918 | 133.79 | 533303 MARSHAL3 115 533322 BAILEYV3 115 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.59918 | 133.43 | 533322 BAILEYV3 115 533337 SENECA 3 115 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.51 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.51 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.51 | P42:345:NPPD:BKR-HOS-3308:::: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.28 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.28 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.28 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.28 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.28 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 126.28 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55457 | 125.71 | P42:345:NPPD:BKR-MOR-3310:::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55457 | 125.71 | P42:345:NPPD:L3502A.MOORE.MCCOOL.CB3310:::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.09 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.09 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 125.09 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55491 | 124.62 | P12:345:NPPD:LN004::MOORE.MCCOOL.CKT1:: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55427 | 124.36 | P42:345:NPPD:L3503.MOORE.103&ROKEBY.CB3306:::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55427 | 124.36 | P42:345:NPPD:BKR-MOR-3306:::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.59965 | 124 | P12:115:WERE:KNOB-MARS-115:::HV: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55491 | 123.92 | POI 640271_1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.59918 | 123.83 | P12:115:WERE:KELL-SSEN-115:::HV: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.73612 | 121.4 | 640169 FAIRBRY7 115 640208 HARBINE7 115 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.73612 | 121.14 | P12:115:NPPD:1175B:FAIRBRY7-HARBINE7:BTB:: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.65039 | 119.21 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15098 | 119.21 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15098 | 119.21 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15098 | 119.21 | P12:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.65039 | 119.21 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15098 | 119.21 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15098 | 119.21 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.15098 | 119.21 | P21:345:MEC-NPPD:AUTO-SINGLE:RAUN3:HOSKINS3:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55514 | 118.22 | 640170 FAIRBRYG 34.5 3WXFMR FAIRBURY T1 1 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55483 | 117.47 | POI 640525_5 | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55227 | 117.19 | P42:345:NPPD:BKR-MOR-3308:MONOLITH SUBSTATION ADDITION (2023S+)::: | Cumulative Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.65166 | 112.98 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.08116 | 112.98 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.08116 | 112.98 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 320 | 425 | 0.08116 | 112.98 | System Intact | TDF Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.77 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.77 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.77 | 643250 SHOLES.COL 9 34.5 3WXFMR SHOLES.W T1 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | GEN-2015-007_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 112.66 | P11:1:NPPD:SHOLES.GEN.W:W:178:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-218_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-218_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-216_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-216_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-217_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | GEN-2023-217_POI_640588_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776322 G23-217XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776322 G23-217XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776302 G23-216XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776302 G23-216XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776342 G23-218XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 108.5 | 776301 GEN-2023-216 345 776342 G23-218XFMR1 34.5 1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.26179 | 107.78 | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.26179 | 107.78 | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.53533 | 107.78 | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.23123 | 107.78 | 640065 AXTELL 3 345 640374 SWEET W3 345 1 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.26179 | 107.77 | POI 640065_5 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.26179 | 107.77 | POI 640065_5 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.53533 | 107.77 | POI 640065_5 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.23123 | 107.77 | POI 640065_5 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.26351 | 107.43 | POI 640065_3 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.26351 | 107.43 | POI 640065_3 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.53555 | 107.43 | POI 640065_3 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.23336 | 107.43 | POI 640065_3 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.26351 | 107.43 | P42:345:NPPD:BKR-AXT-3308:::: | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.26351 | 107.43 | P42:345:NPPD:BKR-AXT-3308:::: | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.53555 | 107.43 | P42:345:NPPD:BKR-AXT-3308:::: | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.23336 | 107.43 | P42:345:NPPD:BKR-AXT-3308:::: | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-011 | TO->FROM | 640076 BEATRCE7 115 640208 HARBINE7 115 1 | 99 | 99 | 0.55514 | 107.36 | System Intact | TDF Impact | Rebuild the BEATRCE7 to HARBINE7 115kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.84 | GEN-2016-043_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.84 | GEN-2016-043_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 640226 HOSKINS3 345 640588 TURTLE.CRK 3 345 1 | 1195 | 1195 | 1 | 105.84 | GEN-2016-043_POI_640226_Generator_outage | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.25726 | 105.79 | POI 640065_1 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.25726 | 105.79 | POI 640065_1 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.52932 | 105.79 | POI 640065_1 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.22684 | 105.79 | POI 640065_1 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 640163 EMERSON7 115 640387 TWIN CH7 115 1 | 120 | 120 | 0.17064 | 101.68 | P12:230:WAPA:TWINCH-SIOUXCY:1 | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.07243 | 101.25 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16635 | 101.25 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16635 | 101.25 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | FROM->TO | 640342 SHELCRK3 345 996783 SHELLCREEKT1 230 1 | 336 | 360 | 0.16635 | 101.25 | P12:345:NPPD:LN006::COLUM.E.SHELCRK.CKT1:: | Cumulative Impact | Build new E.HOSKINS3 Substation, Build new TURTLE.CRK 3 to E.HOSKINS3 345kV Line 1&2 Dbl Ckt, Build new E.HOSKINS3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.21531 | 101.14 | P42:345:NPPD:BKR-SW-3304:::: | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.21531 | 101.14 | P42:345:NPPD:BKR-SW-3304:::: | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.61784 | 101.14 | P42:345:NPPD:BKR-SW-3304:::: | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.19017 | 101.14 | P42:345:NPPD:BKR-SW-3304:::: | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-116 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.21531 | 101.14 | POI 640374_4 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-117 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.21531 | 101.14 | POI 640374_4 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-133 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.61784 | 101.14 | POI 640374_4 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-153 | FROM->TO | 640374 SWEET W3 345 653571 GR ISLD3 345 1 | 717 | 717 | 0.19017 | 101.14 | POI 640374_4 | Cumulative Impact | Rebuild the SWEET W3 to GR ISLD3 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23186 | 116.07 | POI 645740_5 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23186 | 116.07 | POI 645740_5 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23186 | 116.07 | POI 645740_5 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 114.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 114.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 114.02 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.24384 | 110.55 | 156260 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.24384 | 110.55 | 156260 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.24384 | 110.55 | 156260 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 110.42 | POI 763982_4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 110.42 | POI 763982_4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 110.42 | POI 763982_4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 110.42 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 110.42 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 110.42 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23708 | 107.98 | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23708 | 107.98 | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23708 | 107.98 | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23697 | 107.64 | 153887 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23697 | 107.64 | 153887 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23697 | 107.64 | 153887 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23697 | 107.64 | 156326 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23697 | 107.64 | 156326 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23697 | 107.64 | 156326 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.27358 | 108.48 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.27358 | 108.48 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.27358 | 108.48 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.22602 | 105.22 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.22602 | 105.22 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.22602 | 105.22 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.26639 | 107.37 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.26639 | 107.37 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.26639 | 107.37 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23708 | 105.76 | 158360 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23708 | 105.76 | 158360 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23708 | 105.76 | 158360 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.2667 | 107.37 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.2667 | 107.37 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.2667 | 107.37 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.26765 | 106.8 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.26765 | 106.8 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.26765 | 106.8 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 114.57 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 114.57 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 114.57 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23178 | 118.17 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 118.17 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 118.17 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 118.17 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-116 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05415 | 115.47 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-117 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05415 | 115.47 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-153 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05239 | 115.47 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.21945 | 115.47 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.25622 | 115.47 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.25622 | 115.47 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.25622 | 115.47 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 113.23 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 113.23 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 113.23 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23188 | 117.26 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 117.26 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 117.26 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 117.26 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-116 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05517 | 114.84 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-117 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05517 | 114.84 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-153 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05343 | 114.84 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.21979 | 114.84 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.25656 | 114.84 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.25656 | 114.84 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.25656 | 114.84 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23188 | 114.75 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 114.75 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 114.75 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 114.75 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23188 | 114.74 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 114.74 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 114.74 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 114.74 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-116 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05711 | 112.82 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-117 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05711 | 112.82 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-153 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05527 | 112.82 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.22546 | 112.82 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.28623 | 112.82 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.28623 | 112.82 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.28623 | 112.82 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 112.68 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 112.68 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 112.68 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23188 | 112.22 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 112.22 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 112.22 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 112.22 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 112.13 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 112.13 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 112.13 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23188 | 111.73 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 111.73 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 111.73 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 111.73 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23188 | 111.72 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 111.72 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 111.72 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30734 | 111.72 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.23188 | 101.09 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.30734 | 101.09 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.30734 | 101.09 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.30734 | 101.09 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-116 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.04859 | 100.79 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-117 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.04859 | 100.79 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-133 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.03629 | 100.79 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-153 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.04703 | 100.79 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.19572 | 100.79 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 100.79 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 100.79 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23737 | 100.79 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.23186 | 100.06 | POI 645740_5 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.23186 | 100.06 | POI 645740_5 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.23186 | 100.06 | POI 645740_5 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 105.69 | POI 763982_3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 105.69 | POI 763982_3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 105.69 | POI 763982_3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 105.69 | POI 763982_0 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 105.69 | POI 763982_0 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 105.69 | POI 763982_0 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 105.66 | POI 763982_1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 105.66 | POI 763982_1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 105.66 | POI 763982_1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 104.68 | POI 763982_2 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 104.68 | POI 763982_2 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 104.68 | POI 763982_2 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 104.68 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 104.68 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.29595 | 104.68 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23178 | 115.63 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 115.63 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 115.63 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 115.63 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23178 | 115.63 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 115.63 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 115.63 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 115.63 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-116 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05619 | 113.6 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-117 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05619 | 113.6 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-153 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.05433 | 113.6 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.22513 | 113.6 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.28598 | 113.6 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.28598 | 113.6 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.28598 | 113.6 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23178 | 113.09 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 113.09 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 113.09 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 113.09 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 112.72 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 112.72 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 112.72 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23178 | 112.59 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 112.59 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 112.59 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 112.59 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23178 | 112.59 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 112.59 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 112.59 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.3074 | 112.59 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.23178 | 101.87 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.3074 | 101.87 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.3074 | 101.87 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645451 S3451 3 345 645551 S3451-RAUN 3 345 Z1 | 1160 | 1160 | 0.3074 | 101.87 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-116 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.04772 | 101.57 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-117 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.04772 | 101.57 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-133 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.03537 | 101.57 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-153 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.04616 | 101.57 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.19556 | 101.57 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 101.57 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 101.57 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.23721 | 101.57 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.21402 | 102.89 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.25081 | 102.89 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.25081 | 102.89 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.25081 | 102.89 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.22629 | 101.99 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30194 | 101.99 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30194 | 101.99 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30194 | 101.99 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.22629 | 101.35 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30194 | 101.35 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30194 | 101.35 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 1000 | 1000 | 0.30194 | 101.35 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.19401 | 121.3 | POI 645740_5 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24088 | 121.3 | POI 645740_5 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24088 | 121.3 | POI 645740_5 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24088 | 121.3 | POI 645740_5 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.19982 | 119.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 119.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 119.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 119.13 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23995 | 123.11 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 123.11 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 123.11 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 123.11 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.22414 | 120.09 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.26648 | 120.09 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.26648 | 120.09 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.26648 | 120.09 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.19982 | 117.73 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 117.73 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 117.73 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 117.73 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.19982 | 117.14 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 117.14 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 117.14 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 117.14 | P11:24:MEC:AUTO-SINGLE:CBLUF33G:3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23995 | 120.35 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 120.35 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 120.35 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 120.35 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23995 | 120.34 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 120.34 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 120.34 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 120.34 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25549 | 112.72 | 156260 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25549 | 112.72 | 156260 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25549 | 112.72 | 156260 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 113.15 | POI 763982_4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 113.15 | POI 763982_4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 113.15 | POI 763982_4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 113.15 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 113.15 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 113.15 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24844 | 109.99 | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24844 | 109.99 | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24844 | 109.99 | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24832 | 109.62 | 153887 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24832 | 109.62 | 153887 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24832 | 109.62 | 153887 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24832 | 109.62 | 156326 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24832 | 109.62 | 156326 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24832 | 109.62 | 156326 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.28801 | 110.27 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.28801 | 110.27 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.28801 | 110.27 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.2801 | 109.11 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.2801 | 109.11 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.2801 | 109.11 | P42:345:LES:L3516::NW68&HOLDREGE.MOORE.CB3005:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.28048 | 109.03 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.28048 | 109.03 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.28048 | 109.03 | P42:345:LES:L1485::NW68&HOLDREGE.WAGENER.CB3006:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23673 | 107.33 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23673 | 107.33 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23673 | 107.33 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24844 | 107.62 | 158360 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24844 | 107.62 | 158360 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24844 | 107.62 | 158360 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.28153 | 108.42 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.28153 | 108.42 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.28153 | 108.42 | P12:345:NPPD:L3521::NW68&HOLDREGE.COLUMBUSEAST.CKT1:: | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 107.99 | POI 763982_3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 107.99 | POI 763982_3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 107.99 | POI 763982_3 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 107.99 | POI 763982_0 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 107.99 | POI 763982_0 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 107.99 | POI 763982_0 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 107.96 | POI 763982_1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 107.96 | POI 763982_1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 107.96 | POI 763982_1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.19295 | 122.92 | POI 645740_5 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23978 | 122.92 | POI 645740_5 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23978 | 122.92 | POI 645740_5 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23978 | 122.92 | POI 645740_5 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23881 | 124.65 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 124.65 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 124.65 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 124.65 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.19862 | 120.48 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24531 | 120.48 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24531 | 120.48 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24531 | 120.48 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.22278 | 121.33 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.26511 | 121.33 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.26511 | 121.33 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.26511 | 121.33 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.19862 | 119.07 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24531 | 119.07 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24531 | 119.07 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24531 | 119.07 | P13:345-26:MEC:AUTO-SINGLE:CBLUFFS3:CBLUF4G:1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23881 | 121.89 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 121.89 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 121.89 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 121.89 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23881 | 121.88 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 121.88 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 121.88 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 121.88 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23256 | 118.12 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.29873 | 118.12 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.29873 | 118.12 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.29873 | 118.12 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23995 | 117.6 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 117.6 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 117.6 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 117.6 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23995 | 117.08 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 117.08 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 117.08 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 117.08 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23995 | 117.08 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 117.08 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 117.08 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32234 | 117.08 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-116 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.03285 | 105.32 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-117 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.03285 | 105.32 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-153 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.03276 | 105.32 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.19982 | 105.32 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 105.32 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 105.32 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 24SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24653 | 105.32 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 106.92 | POI 763982_2 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 106.92 | POI 763982_2 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 106.92 | POI 763982_2 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 106.92 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 106.92 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27L | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31289 | 106.92 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23116 | 119.56 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.29738 | 119.56 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.29738 | 119.56 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.29738 | 119.56 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23881 | 119.11 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 119.11 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 119.11 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 119.11 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23881 | 118.57 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 118.57 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 118.57 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 118.57 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23881 | 118.57 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 118.57 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 118.57 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.32132 | 118.57 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-116 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.03144 | 106.81 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-117 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.03144 | 106.81 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-153 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.03135 | 106.81 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.19862 | 106.81 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24531 | 106.81 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24531 | 106.81 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27SP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24531 | 106.81 | System Intact | TDF Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.21713 | 109.04 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25948 | 109.04 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25948 | 109.04 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25948 | 109.04 | 156260 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23311 | 108.29 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 108.29 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 108.29 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 108.29 | 640342 SHELCRK3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23311 | 107.6 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 107.6 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 107.6 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 107.6 | POI 763982_4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 460 | 320 | 0.59729 | 106.03 | 635200 RAUN 3 345 640999 E.HOSKINS3 345 1 | Cumulative Impact | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 460 | 320 | 0.08747 | 106.03 | 635200 RAUN 3 345 640999 E.HOSKINS3 345 1 | Cumulative Impact | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 460 | 320 | 0.08747 | 106.03 | 635200 RAUN 3 345 640999 E.HOSKINS3 345 1 | Cumulative Impact | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | FROM->TO | 640386 TWIN CH4 230 652565 SIOUXCY4 230 1 | 460 | 320 | 0.08747 | 106.03 | 635200 RAUN 3 345 640999 E.HOSKINS3 345 1 | Cumulative Impact | Rebuild the TWIN CH4 to SIOUXCY4 230kV Line 1
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.21072 | 105.37 | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25226 | 105.37 | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25226 | 105.37 | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25226 | 105.37 | 635600 GRIMES 3 345 636003 BEAVER CRK 3 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23311 | 105.19 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 105.19 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 105.19 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 105.19 | POI 763982_3 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.21068 | 104.91 | 153887 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25214 | 104.91 | 153887 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25214 | 104.91 | 153887 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25214 | 104.91 | 153887 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.21068 | 104.91 | 156326 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25214 | 104.91 | 156326 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25214 | 104.91 | 156326 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.25214 | 104.91 | 156326 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.19363 | 104.74 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24034 | 104.74 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24034 | 104.74 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.24034 | 104.74 | P11:26:MEC:AUTO-SINGLE:CBLUF4G:4 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.22523 | 104.68 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.29149 | 104.68 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.29149 | 104.68 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.29149 | 104.68 | P42:345:NPPD:LXXXX.COLMB E.SHELCRK.CB3306:::: | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23311 | 104.49 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 104.49 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 104.49 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 104.49 | POI 763982_0 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23311 | 104.28 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 104.28 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 104.28 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 104.28 | POI 763982_1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23311 | 103.83 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 103.83 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 103.83 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 103.83 | POI 763982_2 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-199 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.23311 | 103.67 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-216 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 103.67 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-217 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 103.67 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Thermal | DISIS-2023-001 CF | 02ALL | 1 | 27WP | GEN-2023-218 | TO->FROM | 645551 S3451-RAUN 3 345 762779 G18-043 TAP 345 1 | 956 | 956 | 0.31564 | 103.67 | 640226 HOSKINS3 345 763982 G19-069TAP 345 1 | Cumulative Impact | Rebuild the S3451-RAUN 3 to G18-043 TAP 345kV Line 1 (Conductor uprate)
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 24SP | GEN-2023-116 |  | Non-Converged |  |  | 0.68264 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 24SP | GEN-2023-117 |  | Non-Converged |  |  | 0.68264 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 24SP | GEN-2023-153 |  | Non-Converged |  |  | 0.28907 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 27L | GEN-2023-116 |  | Non-Converged |  |  | 0.6777 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 27L | GEN-2023-117 |  | Non-Converged |  |  | 0.6777 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 27SP | GEN-2023-116 |  | Non-Converged |  |  | 0.68251 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 27SP | GEN-2023-117 |  | Non-Converged |  |  | 0.68251 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 27SP | GEN-2023-153 |  | Non-Converged |  |  | 0.28897 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 27WP | GEN-2023-116 |  | Non-Converged |  |  | 0.68317 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 27WP | GEN-2023-117 |  | Non-Converged |  |  | 0.68317 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 02ALL | 0 | 27WP | GEN-2023-153 |  | Non-Converged |  |  | 0.28963 |  | POI 640252_0 | TDF Impact | Build new Gerald Gentleman 345 kV Satellite Substation (GNTLMNS3) and build new KEYSTON3 to GNTLMNS3 345kV Line 1
Non-Converged | DISIS-2023-001 | 03ALL | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 03ALL | 0 | 27WP | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 03ALL | 0 | 24SP | GEN-2023-219 | '' | Non-Converged |  |  | 0.66759 |  | 533304 LANG 3 115 767120 G22-007-TAP 115 1 | TDF Impact | Build 2nd LANG 3 to G22-007-TAP 115 kV Line
Non-Converged | DISIS-2023-001 | 03ALL | 0 | 27SP | GEN-2023-219 | '' | Non-Converged |  |  | 0.66805 |  | 533304 LANG 3 115 767120 G22-007-TAP 115 1 | TDF Impact | Build 2nd LANG 3 to G22-007-TAP 115 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-061 | FROM->TO | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 294 | 294 | 0.2693 | 107.32 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-061 | FROM->TO | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 294 | 294 | 0.2693 | 107.29 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-061 | FROM->TO | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 294 | 294 | 0.26817 | 106.96 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-006 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.05608 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-023 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.12747 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-032 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.0636 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-033 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.08885 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-034 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.056 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-036 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.0663 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-037 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.13083 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-050 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.05548 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-065 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.06092 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-073 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.05933 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-087 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.07549 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-099 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.13537 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-149 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.0933 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-169 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.05498 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-171 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.09342 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-219 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.10325 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-220 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.10051 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-221 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.10007 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-231 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1248 | 1248 | 0.06206 | 100.56 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.67674 | 131.96 | 300042 7HUBEN 345 300045 7MORGAN 345 1 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68228 | 122.62 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68228 | 122.62 | POI 337957_4 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68229 | 122.52 | POI 337957_12 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68229 | 122.52 | P23:500:EES-EAI:KEO:B4921 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.6852 | 119.82 | 300042 7HUBEN 345 300051 7FRANKSRCTP 345 1 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.6852 | 119.79 | 300041 7FRANKS 345 300051 7FRANKSRCTP 345 1 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.67101 | 118.81 | 300072 5COFFMN 161 300088 5HUBEN 161 1 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68239 | 118.55 | 300041 7FRANKS 345 300472 7SALEMTP 345 1 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68321 | 118.44 | P12:HV:EES::5HILLTOP%:NORFORK5!:TABLE R5!:1 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.67082 | 117.85 | 300072 5COFFMN 161 300092 5LEBANN 161 1 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68294 | 117.78 | 300040 7FLETCH 345 300472 7SALEMTP 345 1 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68232 | 117.73 | POI 508359_4 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68238 | 117.71 | P23:345:AEPW:VALLIANT CB 3421A NBTB:::: | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68238 | 117.71 | P42:345:AEPW:VALLIANT CB 3421A NBTB+FAULT:::: | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27L | GEN-2023-085 | TO->FROM | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.68313 | 112.61 | System Intact | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1 (SWPA) Upgrade Terminal Equipment limiting 5MANSFDMN to G23-085-TAP 161 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 187 | 211 | 0.884 | 120.73 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 187 | 211 | 0.9454 | 120.73 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 187 | 211 | 0.34445 | 107.48 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-033 | TO->FROM | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 187 | 211 | 0.88391 | 121.14 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-169 | TO->FROM | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 187 | 211 | 0.94532 | 121.14 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-169 | TO->FROM | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 187 | 211 | 0.34366 | 112.25 | P12:161:AECI-INDN:ECKLES-5MOCITYB1:::HV: | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | TO->FROM | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 266 | 266 | 0.88397 | 100.45 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | TO->FROM | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | 266 | 266 | 0.94538 | 100.45 | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | TDF Impact | Rebuild the 5MOCITYB2 to G23-169-TAP 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-034 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.04456 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.30083 | 128.8 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.30083 | 128.74 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.30444 | 128.35 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.30444 | 128.35 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.30083 | 126.68 | POI 773480_1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.30083 | 126.67 | POI 773480_0 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.30083 | 126.63 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.30083 | 126.6 | POI 773480_2 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.29594 | 123.26 | POI 770500_2 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.29594 | 123.26 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.29594 | 123.25 | POI 770500_1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.29594 | 123.25 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.29594 | 123.24 | POI 770500_0 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.23016 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-065 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.04307 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-073 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.06262 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.03137 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.06368 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.06406 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.03961 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.04086 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.041 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.26374 | 128.8 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.26374 | 128.74 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.26706 | 128.35 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.26706 | 128.35 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.26374 | 126.68 | POI 773480_1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.26374 | 126.67 | POI 773480_0 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.26374 | 126.63 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.26374 | 126.6 | POI 773480_2 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.25951 | 123.26 | POI 770500_2 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.25951 | 123.26 | 510406 N.E.S.-7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.25951 | 123.25 | POI 770500_1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.25951 | 123.25 | 510380 DELWARE7 345 770500 G22-176-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.25951 | 123.24 | POI 770500_0 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.20013 | 104.7 | System Intact | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.23117 | 107.17 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.23117 | 105.35 | POI 772100_2 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.23117 | 105.22 | POI 772100_1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.23117 | 105.21 | POI 772100_0 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.20101 | 107.17 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.20101 | 105.35 | POI 772100_2 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.20101 | 105.22 | POI 772100_1 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 870 | 870 | 0.20101 | 105.21 | POI 772100_0 | TDF Impact | Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (WERE) Rebuild the 7BLACKBERRY to NEOSHO 7 345 kV Line 1 (Owned by AECI)
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-061 | FROM->TO | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 223 | 223 | 0.24393 | 127.36 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-061 | FROM->TO | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 223 | 223 | 0.24393 | 127.34 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-061 | FROM->TO | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 223 | 223 | 0.24283 | 126.99 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-061 | FROM->TO | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 223 | 223 | 0.25406 | 116.13 | 547472 TIP292 5 161 547480 MON383 5 161 1 | TDF Impact | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-061 | FROM->TO | 505488 CARTHAG5 161 547479 LAR382 5 161 1 | 223 | 223 | 0.24853 | 101.26 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Upgrade Terminal Equipment limiting CARTHAG5 to LAR382 5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09679 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07034 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08162 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07606 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09725 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.06567 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08731 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07626 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08295 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09053 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10228 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10179 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09761 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07623 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08561 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08141 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09792 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07259 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08554 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08086 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08709 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0878 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09879 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09834 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10064 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11234 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09281 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10111 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09749 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11242 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09304 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08453 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09605 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10321 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08177 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09205 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09135 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11234 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09281 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10111 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09749 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11242 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09304 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08453 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09605 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10321 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08177 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09205 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09135 | 111.83 | POI 772100_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11234 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09281 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10111 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09749 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11242 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09304 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08453 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09605 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10321 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08177 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09205 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09135 | 111.81 | POI 772100_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11234 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09281 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10111 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09749 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11242 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09304 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08453 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09605 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10321 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08177 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09205 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09135 | 111.8 | POI 772100_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09761 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07623 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08561 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08141 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09792 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07259 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08554 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.1118 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08086 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08709 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0878 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09879 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09834 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11234 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09281 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10111 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09749 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11242 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09304 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.29127 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.28681 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08453 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22897 | 106.07 | POI 532793_12 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22897 | 105.88 | POI 532793_15 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.27553 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.27553 | 105.05 | POI 542965_7 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22897 | 103.98 | POI 532793_11 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.2611 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22239 | 103.41 | POI 532793_8 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.28873 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09605 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10321 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08177 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09205 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09135 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11234 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09281 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10111 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09749 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11242 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09304 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08453 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09605 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10321 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08177 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09205 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09135 | 107.05 | POI 765200_5 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11234 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09281 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10111 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09749 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11242 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09304 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08453 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09605 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10321 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08177 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09205 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09135 | 107.01 | POI 765200_4 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11884 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09912 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.1076 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.1039 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11891 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09914 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09148 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10248 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-170 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0525 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10965 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08879 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0991 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0984 | 106.07 | POI 532793_12 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09761 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07623 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08561 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08141 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09792 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07259 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08554 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08086 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08709 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0878 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09879 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09834 | 106.06 | POI 774960_1 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09761 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07623 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.72136 | 116.72 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.71949 | 114.22 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.71949 | 108.98 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69877 | 106.07 | POI 532793_12 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.71949 | 106.06 | POI 774960_1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.71949 | 106.04 | POI 774960_2 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.71949 | 106.03 | POI 774960_0 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69877 | 105.88 | POI 532793_15 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.7195 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.7195 | 105.05 | POI 542965_7 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69877 | 103.98 | POI 532793_11 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.71339 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.65635 | 103.41 | POI 532793_8 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.72141 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08561 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08141 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09792 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07259 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08554 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08086 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08709 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0878 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09879 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09834 | 106.04 | POI 774960_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09761 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07623 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08561 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08141 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09792 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.27408 | 101.96 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07259 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08554 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08086 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08709 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0878 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.73601 | 101.96 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09879 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09834 | 106.03 | POI 774960_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11884 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09912 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.1076 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.1039 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11891 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09914 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09148 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10248 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-170 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0525 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10965 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08879 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0991 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0984 | 105.88 | POI 532793_15 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11234 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09281 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10111 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09749 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11242 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09304 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08453 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09605 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10321 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08177 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09205 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09135 | 105.22 | POI 765200_2 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10183 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10183 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09515 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09515 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09846 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09846 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09741 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09741 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10137 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10137 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10198 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10198 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07436 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07436 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09484 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09484 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10075 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10075 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0733 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0733 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08014 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08014 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07999 | 105.05 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07999 | 105.05 | POI 542965_7 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11884 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09912 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.1076 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.1039 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11891 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09914 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09148 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10248 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-170 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0525 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10965 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08879 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0991 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0984 | 103.98 | POI 532793_11 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10554 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09048 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09718 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09439 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10547 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09208 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08285 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09278 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09915 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08233 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09148 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09107 | 103.52 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11547 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09356 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10349 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0992 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11562 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-065 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.05156 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09166 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.0979 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09799 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10552 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09737 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10786 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10735 | 103.41 | POI 532793_8 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09953 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07815 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08753 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08333 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09984 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.07451 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08746 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08278 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08901 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08972 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10072 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10026 | 102.94 | P23:345:KCPL:LACYGNE-R2-5:::EHV: | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-023 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11234 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-032 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09281 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10111 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-036 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09749 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-037 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.11242 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-087 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09304 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-099 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08453 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09605 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-171 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.10321 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-219 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.08177 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-220 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09205 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-221 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.09135 | 102.29 | POI 765200_0 | Cumulative Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22265 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22265 | 111.83 | POI 772100_2 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.26811 | 111.82 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22265 | 111.81 | POI 772100_1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22265 | 111.8 | POI 772100_0 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.26429 | 109.83 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22265 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22265 | 107.05 | POI 765200_5 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22265 | 107.01 | POI 765200_4 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22265 | 105.22 | POI 765200_2 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.20913 | 104.16 | POI 532793_12 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.20913 | 103.98 | POI 532793_15 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-149 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.22265 | 102.29 | POI 765200_0 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69383 | 113.6 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69383 | 111.83 | POI 772100_2 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.73018 | 111.82 | P23:345:KCPL-GMO:STILWELL-R2-5:::EHV: | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69383 | 111.81 | POI 772100_1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69383 | 111.8 | POI 772100_0 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.72832 | 109.83 | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69383 | 108.82 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69383 | 107.05 | POI 765200_5 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69383 | 107.01 | POI 765200_4 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69383 | 105.22 | POI 765200_2 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.72832 | 104.83 | 765571 G21-029-TAP 345 774960 G23-149-TAP 345 1 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.70739 | 104.16 | POI 532793_12 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.70739 | 103.98 | POI 532793_15 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.69383 | 102.29 | POI 765200_0 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | 1015 | 1015 | 0.72832 | 102.25 | POI 774960_0 | TDF Impact | Rebuild the NEOSHO 7 to G23-231-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05245 | 120.47 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.13315 | 120.47 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.11563 | 120.47 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.05245 | 120.25 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.13315 | 120.25 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997417 N345 TX-1 138 1 | 400 | 440 | 0.11563 | 120.25 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.06289 | 112.07 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.1607 | 112.07 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.13955 | 112.07 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.06289 | 111.77 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.1607 | 111.77 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.13955 | 111.77 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 105.57 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 105.57 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 105.57 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 105.55 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 105.55 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 105.55 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.06226 | 105.39 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.06226 | 105.39 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.14934 | 105.39 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.14934 | 105.39 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.13079 | 105.39 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.13079 | 105.39 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 103.77 | POI 773480_2 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 103.77 | POI 773480_2 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 103.77 | POI 773480_2 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 103.67 | POI 773480_1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 103.67 | POI 773480_1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 103.67 | POI 773480_1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 103.66 | POI 773480_0 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 103.66 | POI 773480_0 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 103.66 | POI 773480_0 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 103.3 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 103.3 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 532793 NEOSHO 7 345 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 103.3 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.06289 | 110.29 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.1607 | 110.29 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.13955 | 110.29 | 532793 NEOSHO 7 345 3WXFMR N345 TX-1 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.06289 | 110.19 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.1607 | 110.19 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.13955 | 110.19 | 533021 NEOSHO 4 138 533023 N345 3 4 138 Z1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 104.73 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 104.73 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 104.73 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.06226 | 104.65 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.06226 | 104.65 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.14934 | 104.65 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.14934 | 104.65 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.13079 | 104.65 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.13079 | 104.65 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 104.47 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 104.47 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 104.47 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 103.01 | POI 773480_2 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 103.01 | POI 773480_2 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 103.01 | POI 773480_2 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 102.98 | POI 773480_1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 102.98 | POI 773480_1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 102.98 | POI 773480_1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 102.96 | POI 773480_0 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 102.96 | POI 773480_0 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 102.96 | POI 773480_0 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.06398 | 102.63 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.15236 | 102.63 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 532939 N345 4 5 161 997416 N345 TX-2 161 1 | 500 | 550 | 0.13357 | 102.63 | 532793 NEOSHO 7 345 773480 G23-075-TAP 345 1 | Cumulative Impact | Upgrade the Neosho 345/161 kV Transformer Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05245 | 114.96 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.13315 | 114.96 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.11563 | 114.96 | 532793 NEOSHO 7 345 3WXFMR N345 TX-2 1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-006 | TO->FROM | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.05245 | 114.89 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.13315 | 114.89 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 533023 N345 3 4 138 997417 N345 TX-1 138 1 | 400 | 440 | 0.11563 | 114.89 | 532937 NEOSHO 5 161 532939 N345 4 5 161 Z1 | Cumulative Impact | Reconfigure the Neosho Transformers
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-065 | FROM->TO | 533745 NEWTON 2 69.0 533746 ADAMS 2 69.0 1 | 55 | 65 | 0.51782 | 109.64 | 533011 HALSTD 4 138 3WXFMR HALS TX-4 1 | TDF Impact | Rebuild the NEWTON 2 to ADAMS 2 69 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-033 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 199 | 223 | 0.942 | 115.94 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-169 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 199 | 223 | 0.942 | 115.94 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-033 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 199 | 223 | 0.94208 | 115.75 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-169 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 199 | 223 | 0.94208 | 115.75 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-033 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 233 | 254 | 0.94208 | 104.1 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-169 | FROM->TO | 541248 LBRTYST5 161 543020 BRMGHAM5 161 1 | 233 | 254 | 0.94208 | 104.1 | 300098 5MOCITYB2 161 775360 G23-169-TAP 161 1 | TDF Impact | Rebuild the LBRTYST5 to BRMGHAM5 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-006 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.05508 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-023 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.12646 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-032 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.0628 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-033 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.08448 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-034 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.05522 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-036 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.06496 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-037 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.12975 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-050 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.05466 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-065 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.06011 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-073 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.05847 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-087 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.07495 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-099 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.13383 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-149 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.09143 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-169 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.05307 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-171 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.09262 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-219 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.10204 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-220 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.09933 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-221 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.09889 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-231 | TO->FROM | 541400 EASTOWN7 345 542982 IATAN 7 345 1 | 1074 | 1195 | 0.06133 | 103.58 | 541199 ST JOE 7 345 761383 G17-183-TAP 345 1 | Cumulative Impact | Rebuild the EASTOWN7 to IATAN 7 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | 1792 | 1792 | 0.47227 | 105.6 | POI 542965_9 | TDF Impact | Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | 1792 | 1792 | 0.47227 | 103.82 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | 1792 | 1792 | 0.42993 | 101.78 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | 1792 | 1792 | 0.42993 | 101.78 | POI 542965_7 | TDF Impact | Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-149 | TO->FROM | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | 1792 | 1792 | 0.46747 | 105.53 | POI 542965_9 | TDF Impact | Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-149 | TO->FROM | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | 1792 | 1792 | 0.46747 | 103.7 | P23:345:KCPL-WERE:239LACYGNE-R9-10:::EHV: | TDF Impact | Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-149 | TO->FROM | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | 1792 | 1792 | 0.42488 | 101.16 | POI 542965_7 | TDF Impact | Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-149 | TO->FROM | 542968 STILWEL7 345 774960 G23-149-TAP 345 1 | 1792 | 1792 | 0.42488 | 101.16 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | Build STILWEL7 to G21-029-TAP 345 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547467 ORO110 5 161 547469 RIV4525 161 1 | 279 | 279 | 0.24115 | 143.37 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547467 ORO110 5 161 547469 RIV4525 161 1 | 404 | 420 | 0.24578 | 115.19 | 547469 RIV4525 161 547498 STL439 5 161 1 | TDF Impact | Rebuild the ORO110 5 to RIV4525 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66928 | 113.34 | P12:345:WERE:N345-AECI-345:::EHV: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.59199 | 110.31 | 532937 NEOSHO 5 161 547469 RIV4525 161 2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66928 | 108.72 | POI 532793_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66928 | 107.38 | POI 532793_3 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66459 | 105.59 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.6693 | 103.14 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.6693 | 103.13 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67076 | 102.85 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67076 | 102.85 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66403 | 102.54 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.59407 | 112.73 | 532937 NEOSHO 5 161 547469 RIV4525 161 2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.6641 | 109.94 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67173 | 106.22 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67173 | 106.22 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67031 | 106.21 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05084 | 138.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05681 | 138.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05239 | 138.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.1525 | 138.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06032 | 138.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07202 | 138.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07155 | 138.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07265 | 138.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-034 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0502 | 136.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05227 | 136.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-065 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05 | 136.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05795 | 136.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-099 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05479 | 136.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.15711 | 136.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06512 | 136.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0767 | 136.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07623 | 136.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06974 | 136.96 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05285 | 129.37 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.18464 | 129.37 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67031 | 106.2 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66421 | 106.17 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66421 | 106.13 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67031 | 105.52 | POI 773480_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67031 | 105.52 | POI 773480_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67031 | 105.49 | POI 773480_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.05084 | 107.62 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.59579 | 128.83 | 532937 NEOSHO 5 161 547469 RIV4525 161 2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66516 | 123.16 | 300739 7BLACKBERRY 345 300949 7JASPER 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66517 | 119.02 | 300949 7JASPER 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66517 | 119.01 | 300045 7MORGAN 345 709500 GI-95_POI 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.6722 | 117.66 | P42:345:AEPW:DELAWARE CB 3405A NBTB+FAULT:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.6722 | 117.66 | P23:345:AEPW:DELAWARE CB 3405A NBTB:::: | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67083 | 117.57 | 510380 DELWARE7 345 768820 G22-092-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67083 | 117.55 | 768820 G22-092-TAP 345 773480 G23-075-TAP 345 1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67083 | 116.82 | POI 773480_0 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67083 | 116.82 | POI 773480_1 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.67083 | 116.8 | POI 773480_2 | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.66435 | 107.62 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Thermal | DISIS-2023-001 | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 558 | 558 | 0.04513 | 107.62 | System Intact | TDF Impact | Build RIV4525 to G20-079-TAP 161 kV Line 2 Upgrade Terminal Equipment limiting RIV4525 to G20-079-TAP 161 kV Line
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 24SP | GEN-2023-015 | '' | Non-Converged |  |  | 0.42612 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 24SP | GEN-2023-107 | '' | Non-Converged |  |  | 0.37344 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 24SP | GEN-2023-172 | '' | Non-Converged |  |  | 0.44918 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 24SP | GEN-2023-173 | '' | Non-Converged |  |  | 0.44918 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27L | GEN-2023-107 | '' | Non-Converged |  |  | 0.38112 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27L | GEN-2023-107 | '' | Non-Converged |  |  | 0.38112 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27L | GEN-2023-107 | '' | Non-Converged |  |  | 0.38112 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27L | GEN-2023-172 | '' | Non-Converged |  |  | 0.45677 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27L | GEN-2023-172 | '' | Non-Converged |  |  | 0.45677 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27L | GEN-2023-172 | '' | Non-Converged |  |  | 0.45677 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27L | GEN-2023-173 | '' | Non-Converged |  |  | 0.45677 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27L | GEN-2023-173 | '' | Non-Converged |  |  | 0.45677 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27L | GEN-2023-173 | '' | Non-Converged |  |  | 0.45677 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-015 | '' | Non-Converged |  |  | 0.42525 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-015 | '' | Non-Converged |  |  | 0.42525 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-015 | '' | Non-Converged |  |  | 0.42525 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-107 | '' | Non-Converged |  |  | 0.37259 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-107 | '' | Non-Converged |  |  | 0.37259 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-107 | '' | Non-Converged |  |  | 0.37259 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-172 | '' | Non-Converged |  |  | 0.44834 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-172 | '' | Non-Converged |  |  | 0.44834 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-172 | '' | Non-Converged |  |  | 0.44834 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-173 | '' | Non-Converged |  |  | 0.44834 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-173 | '' | Non-Converged |  |  | 0.44834 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27SP | GEN-2023-173 | '' | Non-Converged |  |  | 0.44834 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-015 | '' | Non-Converged |  |  | 0.42589 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-015 | '' | Non-Converged |  |  | 0.42589 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-015 | '' | Non-Converged |  |  | 0.42589 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-107 | '' | Non-Converged |  |  | 0.37324 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-107 | '' | Non-Converged |  |  | 0.37324 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-107 | '' | Non-Converged |  |  | 0.37324 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-172 | '' | Non-Converged |  |  | 0.44898 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-172 | '' | Non-Converged |  |  | 0.44898 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-172 | '' | Non-Converged |  |  | 0.44898 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-173 | '' | Non-Converged |  |  | 0.44898 |  | POI 765911_2 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-173 | '' | Non-Converged |  |  | 0.44898 |  | POI 765911_3 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Non-Converged | DISIS-2023-001 CF | 03ALL | 0 | 27WP | GEN-2023-173 | '' | Non-Converged |  |  | 0.44898 |  | 531469 SPERVIL7 345 765911 G21-068-TAP 345 1 | TDF Impact | Build a new SPERVIL7 to G21-068-TAP 345 kV line 2
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05639 | 129.37 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07189 | 129.37 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07129 | 129.37 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.18014 | 129.37 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05039 | 125.97 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.18494 | 125.97 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05611 | 125.97 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07175 | 125.97 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07114 | 125.97 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.18041 | 125.97 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05014 | 125.76 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.1847 | 125.76 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0559 | 125.76 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07154 | 125.76 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07093 | 125.76 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.18017 | 125.76 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05374 | 125.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05374 | 125.11 | POI 542940_4 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05965 | 125.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05965 | 125.11 | POI 542940_4 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05037 | 125.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05037 | 125.11 | POI 542940_4 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.16143 | 125.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.16143 | 125.11 | POI 542940_4 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05993 | 125.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05993 | 125.11 | POI 542940_4 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05926 | 125.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05926 | 125.11 | POI 542940_4 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07657 | 125.11 | 542940 ATLNTIC7 345 542977 CRAIG 7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07657 | 125.11 | POI 542940_4 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.21491 | 123.75 | POI 542965_7 | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.21491 | 123.75 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05014 | 123.51 | POI 532793_17 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.1847 | 123.51 | POI 532793_17 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0559 | 123.51 | POI 532793_17 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07154 | 123.51 | POI 532793_17 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07093 | 123.51 | POI 532793_17 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.18017 | 123.51 | POI 532793_17 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05254 | 123.49 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05863 | 123.49 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05532 | 123.49 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-099 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06045 | 123.49 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.15485 | 123.49 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06766 | 123.49 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0786 | 123.49 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07813 | 123.49 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07457 | 123.49 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05014 | 123.44 | POI 532793_14 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 2 | 583 | 607 | 0.61635 | 102.6 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build new NEOSHO 5 to RIV4525 161kV Line 2
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 583 | 607 | 0.61554 | 102.53 | 547469 RIV4525 161 764310 G20-079-TAP 161 2 | TDF Impact | Build new NEOSHO 5 to RIV4525 161kV Line 2
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-194 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 | 222 | 222 | 0.12369 | 100.71 | System Intact | TDF Impact | Rebuild the NEO SPA5 to TIP292 5 161kV Line 1 (EMDE)
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.1847 | 123.44 | POI 532793_14 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0559 | 123.44 | POI 532793_14 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07154 | 123.44 | POI 532793_14 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07093 | 123.44 | POI 532793_14 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.18017 | 123.44 | POI 532793_14 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05014 | 122.75 | POI 532793_19 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.1847 | 122.75 | POI 532793_19 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0559 | 122.75 | POI 532793_19 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07154 | 122.75 | POI 532793_19 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07093 | 122.75 | POI 532793_19 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.18017 | 122.75 | POI 532793_19 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.22005 | 122.58 | POI 542965_7 | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.22005 | 122.58 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-034 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05379 | 121.94 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05407 | 121.94 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-065 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05436 | 121.94 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0612 | 121.94 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-099 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06606 | 121.94 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.15968 | 121.94 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07308 | 121.94 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.08383 | 121.94 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.08336 | 121.94 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07169 | 121.94 | POI 532772_9 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05193 | 121.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.13616 | 121.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.12847 | 121.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-219 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05416 | 121.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06401 | 121.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06359 | 121.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06461 | 121.21 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05374 | 121.16 | POI 542940_2 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05374 | 121.16 | 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05965 | 121.16 | POI 542940_2 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05965 | 121.16 | 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05037 | 121.16 | POI 542940_2 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05037 | 121.16 | 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.16143 | 121.16 | POI 542940_2 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.16143 | 121.16 | 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05993 | 121.16 | POI 542940_2 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05993 | 121.16 | 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05926 | 121.16 | POI 542940_2 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05926 | 121.16 | 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07657 | 121.16 | POI 542940_2 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07657 | 121.16 | 542940 ATLNTIC7 345 542965 W.GRDNR7 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05374 | 120.81 | POI 542940_0 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05965 | 120.81 | POI 542940_0 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05037 | 120.81 | POI 542940_0 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.16143 | 120.81 | POI 542940_0 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05993 | 120.81 | POI 542940_0 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05926 | 120.81 | POI 542940_0 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07657 | 120.81 | POI 542940_0 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05374 | 120.79 | POI 542940_3 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05965 | 120.79 | POI 542940_3 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05037 | 120.79 | POI 542940_3 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.16143 | 120.79 | POI 542940_3 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05993 | 120.79 | POI 542940_3 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05926 | 120.79 | POI 542940_3 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07657 | 120.79 | POI 542940_3 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-006 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05537 | 111.65 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-034 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05017 | 111.65 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06131 | 111.65 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05692 | 111.65 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-099 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05449 | 111.65 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.15705 | 111.65 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06486 | 111.65 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07657 | 111.65 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07609 | 111.65 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.07715 | 111.65 | P23:345:KCPL-GMO:IATAN-R7-9:::EHV: | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.04725 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-034 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.03735 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05273 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-065 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0347 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.04503 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.14502 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-194 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.03078 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.03771 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05158 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05109 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06794 | 106.54 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05359 | 106.2 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.13577 | 106.2 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-099 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05551 | 106.2 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.13054 | 106.2 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-219 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06076 | 106.2 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06991 | 106.2 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.0695 | 106.2 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06635 | 106.2 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15162 | 105.88 | POI 532793_5 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15168 | 105.88 | POI 532793_5 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05891 | 105.88 | POI 532793_5 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05839 | 105.88 | POI 532793_5 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.14812 | 105.88 | POI 532793_5 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-034 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.04105 | 105.64 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-050 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.04839 | 105.64 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-065 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.03847 | 105.64 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-073 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.04968 | 105.64 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.14889 | 105.64 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0411 | 105.64 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-087 | FROM->TO | 541207 ARCHIE 5 161 541239 HSNVL 5 161 1 | 223 | 223 | 0.40305 | 101.63 | 541198 PECULR 7 345 541200 PHILL 7 345 1 | TDF Impact | ARCHIE 5 to HSNVL 5 161 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05496 | 105.64 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05448 | 105.64 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06506 | 105.64 | System Intact | TDF Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15308 | 104.13 | POI 532793_20 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15215 | 104.13 | POI 532793_20 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05905 | 104.13 | POI 532793_20 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05853 | 104.13 | POI 532793_20 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.14855 | 104.13 | POI 532793_20 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-050 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05004 | 104.02 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-073 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05309 | 104.02 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.13649 | 104.02 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-099 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05977 | 104.02 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.1341 | 104.02 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-219 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06487 | 104.02 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.07385 | 104.02 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.07345 | 104.02 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06407 | 104.02 | POI 532772_9 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15262 | 103.73 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15173 | 103.73 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 2 | 583 | 607 | 0.61668 | 105.41 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build new NEOSHO 5 to RIV4525 161kV Line 2
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 583 | 607 | 0.61587 | 105.34 | 547469 RIV4525 161 764310 G20-079-TAP 161 2 | TDF Impact | Build new NEOSHO 5 to RIV4525 161kV Line 2
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 505486 NEO SPA5 161 547472 TIP292 5 161 1 | 222 | 222 | 0.12349 | 103.99 | System Intact | TDF Impact | Rebuild the NEO SPA5 to TIP292 5 161kV Line 1 (EMDE)
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05868 | 103.73 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05816 | 103.73 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.14813 | 103.73 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06294 | 102.74 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-006 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06294 | 102.74 | POI 542965_7 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06712 | 102.74 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-050 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.06712 | 102.74 | POI 542965_7 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.16123 | 102.74 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.16123 | 102.74 | POI 542965_7 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.17539 | 102.74 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.17539 | 102.74 | POI 542965_7 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.08522 | 102.74 | P23:345:KCPL:WGARDNER-R10-12:::EHV: | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.08522 | 102.74 | POI 542965_7 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15043 | 102.43 | POI 532793_20 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.14478 | 102.43 | POI 532793_20 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-220 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05439 | 102.43 | POI 532793_20 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-221 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05388 | 102.43 | POI 532793_20 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.14092 | 102.43 | POI 532793_20 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-006 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.04217 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-034 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.03475 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-050 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.0486 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-065 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.03311 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-073 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.04103 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-149 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.14241 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-194 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.0301 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-219 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.04212 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-220 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.05626 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-221 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.05589 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-231 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.06403 | 101.91 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.17806 | 101.46 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05308 | 101.46 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06841 | 101.46 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06781 | 101.46 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.17317 | 101.46 | POI 532793_20 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15262 | 101.4 | POI 532793_17 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15173 | 101.4 | POI 532793_17 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05868 | 101.4 | POI 532793_17 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05816 | 101.4 | POI 532793_17 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.14813 | 101.4 | POI 532793_17 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15262 | 101.32 | POI 532793_14 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15173 | 101.32 | POI 532793_14 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05868 | 101.32 | POI 532793_14 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05816 | 101.32 | POI 532793_14 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.14813 | 101.32 | POI 532793_14 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-034 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.038 | 100.83 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.23896 | 113.76 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.23896 | 111.83 | POI 772100_2 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.23896 | 111.71 | POI 772100_1 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.23896 | 111.69 | POI 772100_0 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-050 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.04451 | 100.83 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.23896 | 102.3 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.23896 | 100.28 | POI 765200_5 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-050 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.23896 | 100.24 | POI 765200_4 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-065 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.03668 | 100.83 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-073 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.04467 | 100.83 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-149 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.1458 | 100.83 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-219 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.04729 | 100.83 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-220 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.06179 | 100.83 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-221 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.06145 | 100.83 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 2 | 583 | 607 | 0.61715 | 118.78 | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | TDF Impact | Build new NEOSHO 5 to RIV4525 161kV Line 2
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-194 | TO->FROM | 547469 RIV4525 161 764310 G20-079-TAP 161 1 | 583 | 607 | 0.61633 | 118.69 | 547469 RIV4525 161 764310 G20-079-TAP 161 2 | TDF Impact | Build new NEOSHO 5 to RIV4525 161kV Line 2
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-231 | TO->FROM | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 875 | 0.06127 | 100.83 | System Intact | System Intact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-087 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15262 | 100.61 | POI 532793_19 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-149 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.15173 | 100.61 | POI 532793_19 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-220 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05868 | 100.61 | POI 532793_19 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-221 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.05816 | 100.61 | POI 532793_19 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 24SP | GEN-2023-231 | FROM->TO | 541200 PHILL 7 345 541201 SIBLEY 7 345 1 | 717 | 717 | 0.14813 | 100.61 | POI 532793_19 | Cumulative Impact | PHILL 7 to SIBLEY 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.17717 | 100.46 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05244 | 100.46 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06775 | 100.46 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.06715 | 100.46 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.17228 | 100.46 | POI 532793_5 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-149 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.1773 | 100.38 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.20861 | 113.76 | 300739 7BLACKBERRY 345 772100 G23-006-TAP 345 1 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.20861 | 111.83 | POI 772100_2 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.20861 | 111.71 | POI 772100_1 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.20861 | 111.69 | POI 772100_0 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-219 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.05247 | 100.38 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.20861 | 102.3 | 765200 G20-090-TAP 345 772100 G23-006-TAP 345 1 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-220 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0678 | 100.38 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-221 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.0672 | 100.38 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | FROM->TO | 541198 PECULR 7 345 541200 PHILL 7 345 1 | 717 | 717 | 0.17241 | 100.38 | 532793 NEOSHO 7 345 776600 G23-231-TAP 345 1 | Cumulative Impact | PECULR 7 to PHILL 7 345 kV Ckt 1 Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.20861 | 100.28 | POI 765200_5 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03ALL | 1 | 27WP | GEN-2023-231 | TO->FROM | 300739 7BLACKBERRY 345 532793 NEOSHO 7 345 1 | 956 | 956 | 0.20861 | 100.24 | POI 765200_4 | TDF Impact | Neosho 345 kV Terminal Upgrade
Thermal | DISIS-2023-001 CF | 03NR | 1 | 27L | GEN-2023-085 | FROM->TO | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.70522 | 115.33 | 300042 7HUBEN 345 300045 7MORGAN 345 1 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1
Thermal | DISIS-2023-001 CF | 03NR | 1 | 27L | GEN-2023-085 | FROM->TO | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.70429 | 111.8 | POI 337957_4 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1
Thermal | DISIS-2023-001 CF | 03NR | 1 | 27L | GEN-2023-085 | FROM->TO | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.70429 | 111.8 | P23:500:EES-EAI:KEO:B4941 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1
Thermal | DISIS-2023-001 CF | 03NR | 1 | 27L | GEN-2023-085 | FROM->TO | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.70431 | 111.71 | P23:500:EES-EAI:KEO:B4921 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1
Thermal | DISIS-2023-001 CF | 03NR | 1 | 27L | GEN-2023-085 | FROM->TO | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.70431 | 111.71 | POI 337957_12 | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1
Thermal | DISIS-2023-001 CF | 03NR | 1 | 27L | GEN-2023-085 | FROM->TO | 300095 5MANSFDMN 161 773680 G23-085-TAP 161 1 | 167 | 167 | 0.70333 | 101.84 | System Intact | TDF Impact | Rebuild the 5MANSFDMN to G23-085-TAP 161 kV Line 1
Thermal | DISIS-2023-001 | 03ALL | 1 | 27SP | GEN-2023-087 | TO->FROM | 300117 5SEDALA 161 541209 SEDALIA5 161 1 | 111 | 111 | 0.03792 | 125.02 | System Intact | TDF Impact | SEDALA to SEDALIA5 161 kV Line 1 Rating Update
Thermal | DISIS-2023-001 | 03ALL | 1 | 24SP | GEN-2023-087 | TO->FROM | 300117 5SEDALA 161 541209 SEDALIA5 161 1 | 111 | 111 | 0.03782 | 116.91 | System Intact | TDF Impact | SEDALA to SEDALIA5 161 kV Line 1 Rating Update
Non-Converged | DISIS-2023-001 | 03NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2023-001 | 03NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 | 02NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2023-001 | 02NR | 1 | 27L | N/A | " | None |  |  |  |  | None |  | None
Non-Converged | DISIS-2023-001 CF | 03NR | 0 | 27L | N/A | " | None |  |  |  |  | None |  | None
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652507 FTTHOMP4 230 1 | 352 | 352 | 1 | 107.79 | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652507 FTTHOMP4 230 1 | 352 | 352 | 1 | 107.17 | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.11243 | 111.05 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.56534 | 111.05 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.11249 | 109.79 | POI 652532_1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.56541 | 109.79 | POI 652532_1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.11243 | 109.6 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.56534 | 109.6 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.1124 | 109.53 | POI 652532_2 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.56531 | 109.53 | POI 652532_2 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.11243 | 109.31 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.56534 | 109.31 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 1 | 106.32 | 589324 G17-094-TAP 230 652507 FTTHOMP4 230 1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.11191 | 112.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.5658 | 112.28 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.11197 | 111.42 | POI 652532_1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.56586 | 111.42 | POI 652532_1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.11191 | 111.35 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.5658 | 111.35 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.11188 | 111.3 | POI 652532_2 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.56576 | 111.3 | POI 652532_2 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.11191 | 111.08 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 0.5658 | 111.08 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 589324 G17-094-TAP 230 652514 HURON 4 230 1 | 352 | 352 | 1 | 105.98 | 589324 G17-094-TAP 230 652507 FTTHOMP4 230 1 | Cumulative Impact | Route second Ft. Thompson – Huron 230 kV circuit into G17-094-TAP
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-012 | TO->FROM | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 387 | 387 | 0.03699 | 106.94 | System Intact | TDF Impact | Rebuild the COLMBUS4 to MEADOWGROVE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 387 | 387 | 0.04752 | 106.94 | System Intact | TDF Impact | Rebuild the COLMBUS4 to MEADOWGROVE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | TO->FROM | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | 387 | 387 | 0.03271 | 106.94 | System Intact | TDF Impact | Rebuild the COLMBUS4 to MEADOWGROVE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.13649 | 111.63 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.84207 | 111.63 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.11444 | 111.63 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.83704 | 119.71 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.10739 | 119.71 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.14524 | 106.71 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.84088 | 106.71 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652506 FTTHOMP3 345 652806 FTTHOM1-LNX3 345 Z | 760 | 760 | 0.11122 | 106.71 | 652506 FTTHOMP3 345 659130 CHAPELLE-BE3 345 2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13285 | 124.26 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10571 | 124.26 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15755 | 124.26 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32408 | 124.26 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22205 | 124.26 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15161 | 124.26 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12391 | 123.4 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.09721 | 123.4 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15336 | 123.4 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32545 | 123.4 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21826 | 123.4 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14592 | 123.4 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12505 | 123.61 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.09757 | 123.61 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15486 | 123.61 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32743 | 123.61 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22125 | 123.61 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14747 | 123.61 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13062 | 123.44 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10275 | 123.44 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15768 | 123.44 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32868 | 123.44 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22454 | 123.44 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15107 | 123.44 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13075 | 123.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10283 | 123.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15787 | 123.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32905 | 123.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22487 | 123.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15124 | 123.44 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14192 | 123.75 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11917 | 123.75 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16072 | 123.75 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32202 | 123.75 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22287 | 123.75 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15774 | 123.75 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13062 | 123.08 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10275 | 123.08 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15768 | 123.08 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32868 | 123.08 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22454 | 123.08 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15107 | 123.08 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12587 | 122.52 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.09814 | 122.52 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.1543 | 122.52 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32318 | 122.52 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22055 | 122.52 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14768 | 122.52 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13386 | 123.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10691 | 123.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16502 | 123.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32477 | 123.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22275 | 123.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15528 | 123.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13285 | 122.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10571 | 122.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15755 | 122.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32408 | 122.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22205 | 122.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15161 | 122.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13513 | 122.86 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11438 | 122.86 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15656 | 122.86 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31609 | 122.86 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21643 | 122.86 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15341 | 122.86 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13512 | 122.85 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11435 | 122.85 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15655 | 122.85 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31608 | 122.85 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21642 | 122.85 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.1534 | 122.85 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13512 | 122.85 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11435 | 122.85 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15655 | 122.85 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31608 | 122.85 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21642 | 122.85 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.1534 | 122.85 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12747 | 120.91 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10116 | 120.91 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15406 | 120.91 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31674 | 120.91 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21463 | 120.91 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.1471 | 120.91 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12675 | 120.93 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10053 | 120.93 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15281 | 120.93 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31576 | 120.93 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21365 | 120.93 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14616 | 120.93 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12551 | 116.2 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.09949 | 116.2 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15047 | 116.2 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31401 | 116.2 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21187 | 116.2 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14449 | 116.2 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.30283 | 111.21 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31759 | 113.52 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31553 | 111.02 | P23:345:XEL:396 BKR SPK | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31867 | 110.03 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31844 | 109.95 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32128 | 110.08 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32241 | 109.86 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31621 | 109.23 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32277 | 109.91 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32241 | 109.62 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31064 | 109.06 | 156784 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.30904 | 108.64 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.30904 | 108.64 | P12:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.30956 | 108.42 | P23:345:MPC:BISON 3:6720 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.30956 | 108.42 | 151341 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12372 | 103.52 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.30821 | 103.52 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13842 | 103.52 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.1365 | 122.09 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10572 | 122.09 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16076 | 122.09 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32305 | 122.09 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22116 | 122.09 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15034 | 122.09 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12201 | 120.83 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.09645 | 120.83 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15636 | 120.83 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32419 | 120.83 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21705 | 120.83 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14436 | 120.83 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11988 | 121.09 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.09627 | 121.09 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15798 | 121.09 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32656 | 121.09 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22034 | 121.09 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.1459 | 121.09 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13343 | 121.09 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10267 | 121.09 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16115 | 121.09 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32805 | 121.09 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22398 | 121.09 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14992 | 121.09 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13331 | 121.08 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10258 | 121.08 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16097 | 121.08 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32768 | 121.08 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22365 | 121.08 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14976 | 121.08 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14477 | 121.34 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11899 | 121.34 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16396 | 121.34 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32101 | 121.34 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22198 | 121.34 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15642 | 121.34 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13331 | 120.75 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10258 | 120.75 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16097 | 120.75 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32768 | 120.75 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22365 | 120.75 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14976 | 120.75 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12183 | 119.79 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.09709 | 119.79 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15713 | 119.79 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32174 | 119.79 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21899 | 119.79 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14588 | 119.79 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.1365 | 119.96 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10572 | 119.96 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16076 | 119.96 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32305 | 119.96 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22116 | 119.96 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15034 | 119.96 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13049 | 118.71 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10107 | 118.71 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15711 | 118.71 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31577 | 118.71 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21378 | 118.71 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14586 | 118.71 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13497 | 120.25 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11379 | 120.25 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15966 | 120.25 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31516 | 120.25 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21551 | 120.25 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15201 | 120.25 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13496 | 120.24 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11375 | 120.24 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15966 | 120.24 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31516 | 120.24 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21551 | 120.24 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15199 | 120.24 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13496 | 120.24 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11375 | 120.24 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15966 | 120.24 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31516 | 120.24 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21551 | 120.24 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15199 | 120.24 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13683 | 120.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10683 | 120.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16783 | 120.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.32382 | 120.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.22191 | 120.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15409 | 120.35 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12856 | 114.1 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.09942 | 114.1 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15362 | 114.1 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31305 | 114.1 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21105 | 114.1 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14327 | 114.1 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.1352 | 121 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.1113 | 121 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15717 | 121 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31799 | 121 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21793 | 121 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15278 | 121 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13507 | 120.91 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11118 | 120.91 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15706 | 120.91 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31784 | 120.91 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21779 | 120.91 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15266 | 120.91 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13507 | 120.91 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11118 | 120.91 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15706 | 120.91 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31784 | 120.91 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21779 | 120.91 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15266 | 120.91 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13507 | 120.85 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11118 | 120.85 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15706 | 120.85 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31784 | 120.85 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21779 | 120.85 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15266 | 120.85 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13507 | 120.82 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11118 | 120.82 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15706 | 120.82 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31784 | 120.82 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21779 | 120.82 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15266 | 120.82 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.30949 | 110.48 | POI 640252_2 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.30907 | 109.27 | POI 640252_1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31016 | 108.82 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31016 | 108.81 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31016 | 108.81 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.12978 | 118.87 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.10045 | 118.87 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15588 | 118.87 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31479 | 118.87 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.2128 | 118.87 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.14493 | 118.87 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13769 | 118.74 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.11112 | 118.74 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16032 | 118.74 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31703 | 118.74 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21707 | 118.74 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.1515 | 118.74 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13755 | 118.64 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.111 | 118.64 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16021 | 118.64 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31688 | 118.64 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21694 | 118.64 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15139 | 118.64 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13755 | 118.64 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.111 | 118.64 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16021 | 118.64 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31688 | 118.64 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21694 | 118.64 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15139 | 118.64 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13755 | 118.59 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.111 | 118.59 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16021 | 118.59 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31688 | 118.59 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21694 | 118.59 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15139 | 118.59 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.13755 | 118.57 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.111 | 118.57 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.16021 | 118.57 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.31688 | 118.57 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.21694 | 118.57 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652506 FTTHOMP3 345 652807 FTTHOM2-LNX3 345 Z | 844 | 844 | 0.15139 | 118.57 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05943 | 134.18 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.12216 | 134.18 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09718 | 134.18 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05524 | 134.18 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05953 | 133.71 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.12226 | 133.71 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09728 | 133.71 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05535 | 133.71 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05953 | 133.38 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.12226 | 133.38 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09728 | 133.38 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05535 | 133.38 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05953 | 133.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.12226 | 133.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09728 | 133.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05535 | 133.28 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05899 | 133.06 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.12165 | 133.06 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09666 | 133.06 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05476 | 133.06 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.06064 | 131.38 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.1218 | 131.38 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09678 | 131.38 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05462 | 131.38 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.06074 | 130.78 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.1219 | 130.78 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09688 | 130.78 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05472 | 130.78 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.06074 | 130.58 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.1219 | 130.58 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09688 | 130.58 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05472 | 130.58 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.06074 | 130.51 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.1219 | 130.51 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09688 | 130.51 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05472 | 130.51 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.0602 | 130.35 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.12129 | 130.35 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09626 | 130.35 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05413 | 130.35 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.06332 | 108.37 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.121 | 108.37 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.0959 | 108.37 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.0547 | 108.37 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.0635 | 107.24 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.12119 | 107.24 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09608 | 107.24 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05489 | 107.24 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.0635 | 107.1 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.12119 | 107.1 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09608 | 107.1 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05489 | 107.1 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.0635 | 107.02 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.12119 | 107.02 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09608 | 107.02 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05489 | 107.02 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.063 | 106.76 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.12063 | 106.76 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.09551 | 106.76 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 652509 FTRANDL4 230 1 | 318 | 318 | 0.05435 | 106.76 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to FTRANDL4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05831 | 121.44 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.11987 | 121.44 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.09535 | 121.44 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05421 | 121.44 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05841 | 121.08 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.11997 | 121.08 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.09546 | 121.08 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05431 | 121.08 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05841 | 120.73 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.11997 | 120.73 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.09546 | 120.73 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05431 | 120.73 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05841 | 120.63 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.11997 | 120.63 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.09546 | 120.63 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05431 | 120.63 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05789 | 120.45 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.11937 | 120.45 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.09485 | 120.45 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05374 | 120.45 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.0595 | 118.94 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.11952 | 118.94 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.09496 | 118.94 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05359 | 118.94 | POI 652532_1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.0596 | 118.45 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.11961 | 118.45 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.09506 | 118.45 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05369 | 118.45 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.0596 | 118.23 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.11961 | 118.23 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.09506 | 118.23 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05369 | 118.23 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.0596 | 118.16 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.11961 | 118.16 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.09506 | 118.16 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05369 | 118.16 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05907 | 118.03 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.11902 | 118.03 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.09446 | 118.03 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652507 FTTHOMP4 230 655475 LAKPLAT-ER4 230 1 | 352 | 352 | 0.05312 | 118.03 | POI 652532_2 | Cumulative Impact | Rebuild the FTTHOMP4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05831 | 128.67 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11987 | 128.67 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09535 | 128.67 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05421 | 128.67 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05841 | 128.23 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11997 | 128.23 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09546 | 128.23 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05431 | 128.23 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05841 | 127.92 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11997 | 127.92 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09546 | 127.92 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05431 | 127.92 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05841 | 127.82 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11997 | 127.82 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09546 | 127.82 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05431 | 127.82 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05789 | 127.61 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11937 | 127.61 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09485 | 127.61 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05374 | 127.61 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.0595 | 125.89 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11952 | 125.89 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09496 | 125.89 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05359 | 125.89 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.0596 | 125.33 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11961 | 125.33 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09506 | 125.33 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05369 | 125.33 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.0596 | 125.14 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11961 | 125.14 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09506 | 125.14 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05369 | 125.14 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.0596 | 125.07 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11961 | 125.07 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09506 | 125.07 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05369 | 125.07 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05907 | 124.92 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11902 | 124.92 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09446 | 124.92 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05312 | 124.92 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.06213 | 103.12 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11873 | 103.12 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.0941 | 103.12 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05368 | 103.12 | POI 652532_1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.06231 | 101.97 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11892 | 101.97 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09428 | 101.97 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05386 | 101.97 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.06231 | 101.85 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11892 | 101.85 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09428 | 101.85 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05386 | 101.85 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.06231 | 101.8 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11892 | 101.8 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09428 | 101.8 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05386 | 101.8 | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W/O A FAULT:EHV: | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-097 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.06182 | 101.53 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-105 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.11837 | 101.53 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-154 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.09372 | 101.53 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27WP | GEN-2023-182 | TO->FROM | 652509 FTRANDL4 230 655475 LAKPLAT-ER4 230 1 | 320 | 320 | 0.05333 | 101.53 | POI 652532_2 | Cumulative Impact | Rebuild the FTRANDL4 to LAKPLAT-ER4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08679 | 110.65 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV: | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08567 | 119.89 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV: | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08567 | 102.93 | POI 659165_1 | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08567 | 102.97 | POI 659165_2 | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08567 | 102.9 | POI 659165_0 | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08567 | 102.9 | P23:345:UMZB:# 7110 #:: CKE IN SD. CKE BREAKER FAULT (192):EHV: | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08641 | 106.95 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV: | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08679 | 101.61 | POI 659165_2 | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08679 | 101.6 | P23:345:UMZB:# 7110 #:: CKE IN SD. CKE BREAKER FAULT (192):EHV: | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08679 | 101.6 | POI 659165_0 | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08679 | 101.58 | POI 659165_1 | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08679 | 100.69 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1 | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | FROM->TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08567 | 101.32 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1 | Cumulative Impact | Rebuild the GROTON 7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08679 | 107.56 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV: | Cumulative Impact | Rebuild the SUMMIT-7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | TO->FROM | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08567 | 116.21 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV: | Cumulative Impact | Rebuild the SUMMIT-7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.08641 | 103.76 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV: | Cumulative Impact | Rebuild the SUMMIT-7 to BRISTOL-ER7 115kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.09465 | 116.54 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.0915 | 116.54 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.05659 | 116.54 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.06048 | 116.54 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.07201 | 116.54 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.06668 | 116.54 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.11267 | 115.67 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.09357 | 115.67 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.0577 | 115.67 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.05998 | 115.67 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.07217 | 115.67 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652523 SIOUXFL4 230 659311 PAHOJA__-BE4 230 1 | 342 | 343 | 0.06696 | 115.67 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the SIOUXFL4 to PAHOJA__-BE4 230kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13285 | 123.39 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10571 | 123.39 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15755 | 123.39 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32408 | 123.39 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22205 | 123.39 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15161 | 123.39 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12391 | 122.57 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.09721 | 122.57 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15336 | 122.57 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32545 | 122.57 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21826 | 122.57 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14592 | 122.57 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12505 | 122.78 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.09757 | 122.78 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15486 | 122.78 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32743 | 122.78 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22125 | 122.78 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14747 | 122.78 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13062 | 122.63 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10275 | 122.63 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15768 | 122.63 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32868 | 122.63 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22454 | 122.63 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15107 | 122.63 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13075 | 122.62 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10283 | 122.62 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15787 | 122.62 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32905 | 122.62 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22487 | 122.62 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15124 | 122.62 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14192 | 122.91 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11917 | 122.91 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16072 | 122.91 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32202 | 122.91 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22287 | 122.91 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15774 | 122.91 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13062 | 122.26 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10275 | 122.26 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15768 | 122.26 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32868 | 122.26 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22454 | 122.26 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15107 | 122.26 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12587 | 121.69 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.09814 | 121.69 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.1543 | 121.69 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32318 | 121.69 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22055 | 121.69 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14768 | 121.69 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13386 | 122.54 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10691 | 122.54 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16502 | 122.54 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32477 | 122.54 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22275 | 122.54 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15528 | 122.54 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13285 | 121.32 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10571 | 121.32 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15755 | 121.32 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32408 | 121.32 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22205 | 121.32 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15161 | 121.32 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13513 | 122.07 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11438 | 122.07 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15656 | 122.07 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31609 | 122.07 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21643 | 122.07 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15341 | 122.07 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13512 | 122.07 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11435 | 122.07 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15655 | 122.07 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31608 | 122.07 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21642 | 122.07 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.1534 | 122.07 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13512 | 122.07 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11435 | 122.07 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15655 | 122.07 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31608 | 122.07 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21642 | 122.07 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.1534 | 122.07 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12747 | 120.11 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10116 | 120.11 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15406 | 120.11 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31674 | 120.11 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21463 | 120.11 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.1471 | 120.11 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12675 | 120.12 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10053 | 120.12 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15281 | 120.12 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31576 | 120.12 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21365 | 120.12 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14616 | 120.12 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12551 | 115.42 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.09949 | 115.42 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15047 | 115.42 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31401 | 115.42 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21187 | 115.42 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14449 | 115.42 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.30283 | 110.4 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31759 | 112.65 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31867 | 109.25 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31553 | 110.19 | P23:345:XEL:396 BKR SPK | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31844 | 109.15 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32128 | 109.27 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32241 | 109.07 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31621 | 108.43 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32277 | 109.12 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32241 | 108.82 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31064 | 108.26 | 156784 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.30956 | 107.7 | 151341 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.30956 | 107.7 | P23:345:MPC:BISON 3:6720 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.30904 | 107.9 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.30904 | 107.9 | P12:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12372 | 102.76 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.30821 | 102.76 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13842 | 102.76 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.1365 | 121.25 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10572 | 121.25 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16076 | 121.25 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32305 | 121.25 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22116 | 121.25 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15034 | 121.25 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12201 | 120.02 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.09645 | 120.02 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15636 | 120.02 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32419 | 120.02 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21705 | 120.02 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14436 | 120.02 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11988 | 120.28 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.09627 | 120.28 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15798 | 120.28 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32656 | 120.28 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22034 | 120.28 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.1459 | 120.28 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13343 | 120.29 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10267 | 120.29 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16115 | 120.29 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32805 | 120.29 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22398 | 120.29 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14992 | 120.29 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13331 | 120.28 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10258 | 120.28 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16097 | 120.28 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32768 | 120.28 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22365 | 120.28 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14976 | 120.28 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14477 | 120.53 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11899 | 120.53 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16396 | 120.53 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32101 | 120.53 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22198 | 120.53 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15642 | 120.53 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13331 | 119.95 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10258 | 119.95 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16097 | 119.95 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32768 | 119.95 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22365 | 119.95 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14976 | 119.95 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12183 | 118.99 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.09709 | 118.99 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15713 | 118.99 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32174 | 118.99 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21899 | 118.99 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14588 | 118.99 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.1365 | 119.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10572 | 119.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16076 | 119.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32305 | 119.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22116 | 119.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15034 | 119.16 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13049 | 117.93 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10107 | 117.93 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15711 | 117.93 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31577 | 117.93 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21378 | 117.93 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14586 | 117.93 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13497 | 119.47 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11379 | 119.47 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15966 | 119.47 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31516 | 119.47 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21551 | 119.47 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15201 | 119.47 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13496 | 119.46 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11375 | 119.46 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15966 | 119.46 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31516 | 119.46 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21551 | 119.46 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15199 | 119.46 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13496 | 119.46 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11375 | 119.46 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15966 | 119.46 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31516 | 119.46 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21551 | 119.46 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15199 | 119.46 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13683 | 119.56 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10683 | 119.56 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16783 | 119.56 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.32382 | 119.56 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.22191 | 119.56 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15409 | 119.56 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12856 | 113.36 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.09942 | 113.36 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15362 | 113.36 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31305 | 113.36 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21105 | 113.36 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14327 | 113.36 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.1352 | 120.19 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.1113 | 120.19 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15717 | 120.19 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31799 | 120.19 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21793 | 120.19 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15278 | 120.19 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13507 | 120.1 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11118 | 120.1 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15706 | 120.1 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31784 | 120.1 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21779 | 120.1 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15266 | 120.1 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13507 | 120.1 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11118 | 120.1 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15706 | 120.1 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31784 | 120.1 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21779 | 120.1 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15266 | 120.1 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13507 | 120.04 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11118 | 120.04 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15706 | 120.04 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31784 | 120.04 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21779 | 120.04 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15266 | 120.04 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13507 | 120.01 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11118 | 120.01 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15706 | 120.01 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31784 | 120.01 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21779 | 120.01 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15266 | 120.01 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.30949 | 109.68 | POI 640252_2 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.30907 | 108.48 | POI 640252_1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31016 | 108.06 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31016 | 108.06 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31016 | 108.06 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.12978 | 118.09 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.10045 | 118.09 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15588 | 118.09 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31479 | 118.09 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.2128 | 118.09 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.14493 | 118.09 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13769 | 117.95 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.11112 | 117.95 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16032 | 117.95 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31703 | 117.95 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21707 | 117.95 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.1515 | 117.95 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13755 | 117.86 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.111 | 117.86 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16021 | 117.86 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31688 | 117.86 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21694 | 117.86 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15139 | 117.86 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13755 | 117.86 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.111 | 117.86 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16021 | 117.86 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31688 | 117.86 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21694 | 117.86 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15139 | 117.86 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13755 | 117.8 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.111 | 117.8 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16021 | 117.8 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31688 | 117.8 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21694 | 117.8 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15139 | 117.8 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.13755 | 117.78 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.111 | 117.78 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.16021 | 117.78 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.31688 | 117.78 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.21694 | 117.78 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | TO->FROM | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | 844 | 844 | 0.15139 | 117.78 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13285 | 121.89 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10571 | 121.89 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15755 | 121.89 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32408 | 121.89 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22205 | 121.89 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15161 | 121.89 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12391 | 121.16 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.09721 | 121.16 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15336 | 121.16 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32545 | 121.16 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21826 | 121.16 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14592 | 121.16 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12505 | 121.34 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.09757 | 121.34 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15486 | 121.34 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32743 | 121.34 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22125 | 121.34 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14747 | 121.34 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13062 | 121.24 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10275 | 121.24 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15768 | 121.24 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32868 | 121.24 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22454 | 121.24 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15107 | 121.24 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13075 | 121.22 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10283 | 121.22 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15787 | 121.22 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32905 | 121.22 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22487 | 121.22 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15124 | 121.22 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13062 | 120.86 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10275 | 120.86 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15768 | 120.86 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32868 | 120.86 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22454 | 120.86 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15107 | 120.86 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14192 | 121.5 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11917 | 121.5 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16072 | 121.5 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32202 | 121.5 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22287 | 121.5 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15774 | 121.5 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12587 | 120.29 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.09814 | 120.29 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.1543 | 120.29 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32318 | 120.29 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22055 | 120.29 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14768 | 120.29 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13386 | 121.2 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10691 | 121.2 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16502 | 121.2 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32477 | 121.2 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22275 | 121.2 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15528 | 121.2 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13285 | 119.91 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10571 | 119.91 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15755 | 119.91 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32408 | 119.91 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22205 | 119.91 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15161 | 119.91 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13513 | 120.79 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11438 | 120.79 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15656 | 120.79 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31609 | 120.79 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21643 | 120.79 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15341 | 120.79 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13512 | 120.79 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11435 | 120.79 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15655 | 120.79 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31608 | 120.79 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21642 | 120.79 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.1534 | 120.79 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13512 | 120.79 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11435 | 120.79 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15655 | 120.79 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31608 | 120.79 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21642 | 120.79 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.1534 | 120.79 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12747 | 118.78 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10116 | 118.78 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15406 | 118.78 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31674 | 118.78 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21463 | 118.78 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.1471 | 118.78 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12675 | 118.78 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10053 | 118.78 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15281 | 118.78 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31576 | 118.78 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21365 | 118.78 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14616 | 118.78 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12551 | 114.16 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.09949 | 114.16 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15047 | 114.16 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31401 | 114.16 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21187 | 114.16 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14449 | 114.16 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.30283 | 109.01 | 648513 GRPR1 3 345 652532 GR PRAIRIE 3 345 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31759 | 111.12 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31867 | 107.95 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31553 | 108.76 | P23:345:XEL:396 BKR SPK | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31844 | 107.79 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32128 | 107.88 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32241 | 107.72 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32277 | 107.76 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31621 | 107.06 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32241 | 107.46 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.30956 | 106.51 | P23:345:MPC:BISON 3:6720 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.30956 | 106.51 | 151341 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.30904 | 106.67 | P12:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.30904 | 106.67 | P21:500:XEL:AUTO-SINGLE:CHISCO2:CHIS-N2:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31064 | 106.89 | 156784 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12372 | 101.5 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.30821 | 101.5 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13842 | 101.5 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.1365 | 119.84 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10572 | 119.84 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16076 | 119.84 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32305 | 119.84 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22116 | 119.84 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15034 | 119.84 | 640133 COLMBUS4 230 640540 MEADOWGROVE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12201 | 118.7 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.09645 | 118.7 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15636 | 118.7 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32419 | 118.7 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21705 | 118.7 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14436 | 118.7 | 652607 WESSINGTON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11988 | 118.93 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.09627 | 118.93 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15798 | 118.93 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32656 | 118.93 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22034 | 118.93 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.1459 | 118.93 | P12:230:UMZW:# 692 #:: FT IN SD. FT-LET BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13331 | 118.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10258 | 118.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16097 | 118.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32768 | 118.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22365 | 118.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14976 | 118.96 | P12:230:UMZW:# 694 #:: FT IN SD. FT-LP BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13343 | 118.97 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10267 | 118.97 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16115 | 118.97 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32805 | 118.97 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22398 | 118.97 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14992 | 118.97 | P12:230:UMZW:# 693 #:: FT IN SD. FT-FR BRANCH FAULT:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14477 | 119.18 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11899 | 119.18 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16396 | 119.18 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32101 | 119.18 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22198 | 119.18 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15642 | 119.18 | P23:345:XEL:396 BKR SPK | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13331 | 118.63 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10258 | 118.63 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16097 | 118.63 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32768 | 118.63 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22365 | 118.63 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14976 | 118.63 | P12:230:UMZW:# 4042 #:: FR-LP IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-LP).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12183 | 117.68 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.09709 | 117.68 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15713 | 117.68 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32174 | 117.68 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21899 | 117.68 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14588 | 117.68 | 652513 HANLON 4 230 659122 STORLA__-BE4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.1365 | 117.82 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10572 | 117.82 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16076 | 117.82 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32305 | 117.82 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22116 | 117.82 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15034 | 117.82 | P12:230:UMZW:# 3863 #:: FR-MG IN SD. FAULT FOR TRANSMISSION CIRCUIT (FR-MG).:HV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13049 | 116.66 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10107 | 116.66 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15711 | 116.66 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31577 | 116.66 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21378 | 116.66 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14586 | 116.66 | P42:345:UMZB:# 2497 #:: SDQ IN NE. STUCK BREAKER (2196):EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13497 | 118.21 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11379 | 118.21 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15966 | 118.21 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31516 | 118.21 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21551 | 118.21 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15201 | 118.21 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13496 | 118.2 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11375 | 118.2 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15966 | 118.2 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31516 | 118.2 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21551 | 118.2 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15199 | 118.2 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13496 | 118.2 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11375 | 118.2 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15966 | 118.2 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31516 | 118.2 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21551 | 118.2 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15199 | 118.2 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13683 | 118.27 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10683 | 118.27 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16783 | 118.27 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.32382 | 118.27 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.22191 | 118.27 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15409 | 118.27 | 640404 WAYSIDE4 230 652484 NUNDRWD4 230 1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12856 | 112.18 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.09942 | 112.18 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15362 | 112.18 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31305 | 112.18 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21105 | 112.18 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14327 | 112.18 | System Intact | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.1352 | 118.83 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.1113 | 118.83 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15717 | 118.83 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31799 | 118.83 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21793 | 118.83 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15278 | 118.83 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13507 | 118.75 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11118 | 118.75 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15706 | 118.75 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31784 | 118.75 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21779 | 118.75 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15266 | 118.75 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13507 | 118.75 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11118 | 118.75 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15706 | 118.75 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31784 | 118.75 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21779 | 118.75 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15266 | 118.75 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13507 | 118.69 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11118 | 118.69 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15706 | 118.69 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31784 | 118.69 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21779 | 118.69 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15266 | 118.69 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13507 | 118.66 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11118 | 118.66 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15706 | 118.66 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31784 | 118.66 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21779 | 118.66 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15266 | 118.66 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.30949 | 108.32 | POI 640252_2 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.30907 | 107.15 | POI 640252_1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31016 | 106.81 | P23:345:UMZW:# 825 #:: WH IN SD. :EHV: | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31016 | 106.8 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27L | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31016 | 106.8 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:WHITE3:1 | TDF Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.12978 | 116.82 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.10045 | 116.82 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15588 | 116.82 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31479 | 116.82 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.2128 | 116.82 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.14493 | 116.82 | POI 640252_2 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13769 | 116.66 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.11112 | 116.66 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16032 | 116.66 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31703 | 116.66 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21707 | 116.66 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.1515 | 116.66 | P21:345:XEL-WAPA:SPLTRK-SIOUXCY:1(1) | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13755 | 116.58 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.111 | 116.58 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16021 | 116.58 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31688 | 116.58 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21694 | 116.58 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15139 | 116.58 | P12:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13755 | 116.58 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.111 | 116.58 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16021 | 116.58 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31688 | 116.58 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21694 | 116.58 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15139 | 116.58 | P21:345:XEL-WAPA:AUTO-SINGLE:SPLTRK3:SIOUXCY-LNX3:1 | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13755 | 116.52 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.111 | 116.52 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16021 | 116.52 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31688 | 116.52 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21694 | 116.52 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15139 | 116.52 | P12:345:UMZW:# 851 #:: SC2-SR IN IA. SC2-SR 345 KV LINE:EHV: | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-012 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.13755 | 116.5 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-082 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.111 | 116.5 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-097 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.16021 | 116.5 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-105 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.31688 | 116.5 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-154 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.21694 | 116.5 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 27SP | GEN-2023-182 | FROM->TO | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | 844 | 844 | 0.15139 | 116.5 | 652564 SIOUXCY3 345 652864 SIOUXCY-LNX3 345 Z | Cumulative Impact | Rebuild the FTTHOM to GRPRAR 345kV Line 1
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 655048 LAKECNTY-ER8 69.0 655119 LAKECNTY-ER7 115 1 | 56 | 56 | 0.29269 | 119.54 | P12:115:UMZ:# 20008 #:: PROPER N-1 FOR TAP ARLNGTN-ER7:HV: | Cumulative Impact | Multi - Madison, SD Area 115 kV System Voltage Conversion
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 655048 LAKECNTY-ER8 69.0 655119 LAKECNTY-ER7 115 1 | 56 | 56 | 0.29269 | 119.42 | P12:115:UMZW:# 1521 #:: AG IN SD. AG-BR BRANCH FAULT (AG IS A TAP):HV: | Cumulative Impact | Multi - Madison, SD Area 115 kV System Voltage Conversion
Thermal | DISIS-2023-001 | 01ALL | 1 | 24SP | GEN-2023-012 | TO->FROM | 655048 LAKECNTY-ER8 69.0 655119 LAKECNTY-ER7 115 1 | 56 | 56 | 0.11672 | 119.35 | P12:115:UMZW:# 124 #:: AUR IN SD. AUR-BR BRANCH FAULT:HV: | Cumulative Impact | Multi - Madison, SD Area 115 kV System Voltage Conversion