## Executive Summary
Executive Summary: SPP Affected Systems Impact Study of MPC03800-MPC04000
Pursuant to the Southwest Power Pool (SPP) and Minnkota Power Cooperative (MPC) Joint Operating Agreement (JOA), SPP has conducted this Affected Systems Impact Study (ASIS) for generation interconnection requests studied in the MPC Generator Interconnection Queue. The primary objective of this ASIS is to identify constraints and over-dutied equipment on SPP facilities associated with the new MPC interconnection requests. The study analysis for the generation interconnection requests included in this ASIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The Generator Interconnection Manual Version 1.6 posted on https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf contains details about the ASIS process, methodology, definitions, and useful links. Please review the Generator Interconnection Manual or contact GI-AFS@SPP.org for more information about the study process. SPP ASIS of MPC038000 - MPC04000 includes study requests in the following cluster groups: 01 - North
Generator Interconnection Manual Version 1.6
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This ASIS analyzes the impact of interconnecting new generation for total of:
701.2 MW
The total costs of Network Upgrades identified in this ASIS are estimated at:
8406249
Models Used in Study
2021 ITP Series
Summer: 2023, 2026
Winter: 2026
Light: 2026
Assumptions Used in Study
Queued after DISIS-2017-002 and all higher-queued MPC requests Incorporates DISIS-2017-002 Phase 2 and all higher queued identified network upgrades Incorporates DISIS-2017-002 Decision Point 2 withdrawals and associated impacts to identified network upgrades Incorporates model reduction Incorporates group reduction Incoporates fuel-based dispatch
By: SPP Generator Interconnection Department
Published: December 6, 2022

## Revision History
Revision History
Date | Author | Change Description
4488000% | SPP | Draft MPC03800-MPC04000 Posting
4490100% | SPP | Final MPC03800-MPC04000 Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | Area | POI | Status
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | 107.4 | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | ER/NR | OTP | Center-Prairie 345 kV Line
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 151.2 | 64.96 | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | ER/NR | OTP | Center-Prairie 345 kV Line
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 300 | 128.88 | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | ER/NR | OTP | Square Butte 230 kV Substation
J1007 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  | ER/NR | EES-EAI | Marion - Marked Tree 161 kV | Under Construction
J1025 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 290 |  |  | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | Not Started
J1026 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Wind | 380 |  |  | ER/NR | AMMO | Maywood - Spencer Creek 345 kV Line Tap | Not Started
J1030 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | EES | Poco - Menard 138 kV | Under Construction
J1034 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 225 |  |  | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | Not Started
J1040 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER/NR | MDU | Wishek Junction 230 kV Substation | Not Started
J1045 | 01 NORTH | 19.5 | DIS-18-1-PQ | Battery | 20 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | Not Started
J1050 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 225 |  |  | ER/NR | ALTW | Doud Tap 161 kV Substation | Not Started
J1060 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 450 |  |  | ER/NR | EES-EAI | West Memphis - Keo 500 kV | Under Construction
J1072 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | XEL | Adams 345 kV Substation | Under Construction
J1087 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | Not Started
J1092 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Three Lakes 115 kV Substation | Not Started
J1107 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | Not Started
J1124 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Byron 345kV Substation | Under Construction
J1125 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV | Under Construction
J1132 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | ALTW | Creston East 69 kV Substation | Not Started
J1145 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | Not Started
J1146 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Coal | 680 |  |  | ER/NR | EES-EAI | San Souci 500 kV | In Service
J1155 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | EES-EAI | Driver 230 kV | Under Construction
J1164 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER | ALTW | Magnolia 161 kV Substation | Not Started
J1169 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | XEL | Grant 115 kV Substation | Not Started
J1174 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | Not Started
J1175 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 165 |  |  | ER | ALTW | Ledyard - Colby 345kV Line Tap | Not Started
J1181 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER | ALTW | Hazleton - Mitchell county 345 kV line | Under Construction
J1182 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | AMMO | Zachary Substation 345 kV Bus | Not Started
J953 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Diesel | 2 |  |  | ER/NR | ALTW | Iowa Jct 34.5 kV | Not Started
J954 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Solar | 1.4 |  |  | ER/NR | ALTW | Iowa Jct 34.5 kV | Not Started
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Spencer Creek 345kV Substation | Not Started
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 |  |  | ER | XEL | Adams 345kV Substation | Under Construction
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | Not Started
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | Not Started
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Montgomery 161kV Substation | Not Started
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Guthrie 161 kV Substation | Not Started
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line
ASGI-2017-014 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 40 |  |  | ER/NR | KCPL | Post Oak 69 kV
GEN-2017-102 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 67.5 |  |  | ER | SPS | CROSSROADS 7 | DISIS STAGE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 |  |  | ER/NR | OPPD | Raun - Tekamah 161kV Line Tap | DISIS STAGE
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | S.HARP 5 | DISIS STAGE
GEN-2017-111 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 152 |  |  | ER | KCPL | Stilwell - S Harper 161kV Line Tap | DISIS STAGE
GEN-2017-112 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 |  |  | ER | KCPL | S Harper - Archie 161kV Line Tap | DISIS STAGE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 |  |  | ER | KCPL | HOLT 7 | DISIS STAGE
GEN-2017-116 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 192.5 |  |  | ER | SPS | OASIS 6 | DISIS STAGE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery | 19.8 |  |  | ER/NR | WFEC | EL RENO4 | DISIS STAGE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 |  |  | ER | SUNC | ELMCREEK7 | DISIS STAGE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 |  |  | ER | WERE | Northview - Abilene Energy Center 115kV Line Tap | DISIS STAGE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | WERE | SUMNER 4 | DISIS STAGE
GEN-2017-125 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | WERE | SWISVAL7 | DISIS STAGE
GEN-2017-128 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | WERE | SWISVAL7 | DISIS STAGE
GEN-2017-131 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 29.6 |  |  | ER/NR | WERE | ALTOONA4 | DISIS STAGE
GEN-2017-132 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | OKGE | ARCADIA7 | DISIS STAGE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | OKGE | ARCADIA7 | DISIS STAGE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | OKGE | ARCADIA7 | DISIS STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 |  |  | ER/NR | OKGE | ARCADIA7 | DISIS STAGE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 |  |  | ER/NR | AEPW | CLARKSV7 | DISIS STAGE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 |  |  | ER/NR | AEPW | CLARKSV7 | DISIS STAGE
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 |  |  | ER | WAPA | HOLT.CO3 | DISIS STAGE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 |  |  | ER | SPS | Deaf Smith 6 - Plant X 230kV Line Tap | DISIS STAGE
GEN-2017-148 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | EMDE | JOP391 5 | DISIS STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 |  |  | ER/NR | OKGE | JOHNCO 7 | DISIS STAGE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | MINCO 7 | DISIS STAGE
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 |  |  | ER | SPS | CRAWFISH_DR - O.K.U.-7 345kV Line Tap | DISIS STAGE
GEN-2017-152 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | OKGE | MCCLAIN4 | DISIS STAGE
GEN-2017-154 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 255 |  |  | ER/NR | OKGE | JOHNCO 7 | DISIS STAGE
GEN-2017-155 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | OKGE | MUSKOGE7 | DISIS STAGE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 |  |  | ER | SPS | TOLK 6 | DISIS STAGE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | WOODRNG7 | DISIS STAGE
GEN-2017-166 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | SUNNYSD7 | DISIS STAGE
GEN-2017-167 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | SUNNYSD7 | DISIS STAGE
GEN-2017-168 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | MCCLAIN4 | DISIS STAGE
GEN-2017-169 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | MCCLAIN4 | DISIS STAGE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 |  |  | ER/NR | AEPW | TERRYRD7 | DISIS STAGE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | TERRYRD7 | DISIS STAGE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | TERRYRD7 | DISIS STAGE
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 |  |  | ER | WAPA | VFODNES4 | DISIS STAGE
GEN-2017-176 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 600 |  |  | ER/NR | SPS | NEWHART 6 | DISIS STAGE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | WOODRNG7 | DISIS STAGE
GEN-2017-179 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 222 |  |  | ER/NR | WERE | EVANS S4 | DISIS STAGE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | NPPD | MOORE 3 | DISIS STAGE
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 |  |  | ER/NR | NPPD | MOORE 3 | DISIS STAGE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | KCPL | St Joe - Nashua 345kV Line Tap | DISIS STAGE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | St Joe - Nashua 345kV Line Tap | DISIS STAGE
GEN-2017-185 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | OKGE | VIOLA 7 | DISIS STAGE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 |  |  | ER | SPS | SULPHUR 3 | DISIS STAGE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 |  |  | ER | EMDE | Brookline - Flint Creek 345kV Line Tap | DISIS STAGE
GEN-2017-191 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | SWISVAL7 | DISIS STAGE
GEN-2017-192 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | WERE | SWISVAL7 | DISIS STAGE
GEN-2017-194 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | WERE | TECHILL6 | DISIS STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 |  |  | ER/NR | KCPL | W.GRDNR7 | DISIS STAGE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 128 |  |  | ER/NR | KCPL | W.GRDNR7 | DISIS STAGE
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery | 11.64 |  |  | ER | OPPD | S901 8 | DISIS STAGE
GEN-2017-199 | 01 NORTH | 19 | DIS-17-2 | Battery | 202 |  |  | ER/NR | WAPA | BROADLND-BE3 | DISIS STAGE
GEN-2017-200 | 01 NORTH | 19 | DIS-17-2 | Wind | 302 |  |  | ER/NR | WAPA | BROADLND-BE3 | DISIS STAGE
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | NPPD | HOSKINS3 | DISIS STAGE
GEN-2017-202 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 200 |  |  | ER/NR | SWPA | New Madrid - Sikeston 161kV Line Tap | DISIS STAGE
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar/ Battery | 280 |  |  | ER | OKGE | RENFROW7 | DISIS STAGE
GEN-2017-209 | 03 CENTRAL | 19 | DIS-17-2 | Solar/ Battery | 350 |  |  | ER | KCPL | LACYGNE7 | DISIS STAGE
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Solar/ Battery | 200 |  |  | ER | NPPD | MCCOOL 3 | DISIS STAGE
GEN-2017-213 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar/ Battery | 350 |  |  | ER | AEPW | CLARKSV7 | DISIS STAGE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | LOGAN___-BE4 | DISIS STAGE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | LOGAN___-BE4 | DISIS STAGE
GEN-2017-216 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | LOGAN___-BE4 | DISIS STAGE
GEN-2017-217 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 |  |  | ER/NR | SPS | PLANT_X 6 | DISIS STAGE
GEN-2017-218 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 600 |  |  | ER/NR | SPS | Tolk - Plant X 230kV Line Tap | DISIS STAGE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | BUFFALO7 | DISIS STAGE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 152 |  |  | ER/NR | WERE | BUFFALO7 | DISIS STAGE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 |  |  | ER | WAPA | DENISON4 | DISIS STAGE
GEN-2017-225 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 76 |  |  | ER/NR | KCPL | CRAIG 7 | DISIS STAGE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | EVANS N4 | DISIS STAGE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 201.6 |  |  | ER/NR | WERE | EVANS N4 | DISIS STAGE
GEN-2017-229 | 03 CENTRAL | 19 | DIS-17-2 | Battery | 76 |  |  | ER/NR | KCPL | STILWEL7 | DISIS STAGE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | TRYON 4 | DISIS STAGE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | BRANCH 5 | DISIS STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 |  |  | ER/NR | OKGE | BROWN 4 | DISIS STAGE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 |  |  | ER/NR | OKGE | MINCO 7 | DISIS STAGE
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 |  |  | ER | NPPD | Spalding - North Loup 115kV Line Tap | DISIS STAGE
GEN-2017-235 | 01 NORTH | 19 | DIS-17-2 | Wind | 50 |  |  | ER/NR | WAPA | BERTHOLD-CP7 | DISIS STAGE
GEN-2017-236 | 01 NORTH | 19 | DIS-17-2 | Wind | 50 |  |  | ER/NR | WAPA | BERTHOLD-CP7 | DISIS STAGE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 |  |  | ER | SPS | MUSTANG 6 | DISIS STAGE
GEN-2017-240 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 202 |  |  | ER/NR | OKGE | BEGGS 4 | DISIS STAGE
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  | ER/NR | AECI | McCredie 345 kV
GIA-84 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 200.62 |  |  | ER | AECI | New Madrid 345 kV
GIA-85 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar/ Battery | 477.3 |  |  | ER/NR | AECI | Morgan 345 kV
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  | ER/NR | AECI | Thomas Hill 69 kV
GIA-88 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 92.09 |  |  | ER/NR | AECI | Eudora 69 kV
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  | ER/NR | AECI | Sedalia 69 kV
GIA-92 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 170 |  |  | ER/NR | AECI | Harrisburg - Higbee 161 kV
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  | ER/NR | AECI | Palmyra 161 kV
GIA-94 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 225 |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
IR24 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | Murray Junction 69 kV substation
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  | ER | XEL | Buffalo 115kV Substation | In Service
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | OTP | Big Stone South 230kV Substation | Not Started
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | Under Construction
J803 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 32.5 |  |  | ER | XEL | Tracy 69 kV line | Not Started
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | ALTW | Ledyard 345kV Substation | Not Started
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line | Under Construction
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | Under Construction
J897 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  | ER | GRE | Prairie - Ramsey 230 kV line | Not Started
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap | Under Construction
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line | Under Construction
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 |  |  | ER | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 |  |  | ER | SUNC | Elm Creek - Summit 345 kV | FACILITY STUDY STAGE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 |  |  | ER | WERE | Marmaton - Litchfield 161 kV | FACILITY STUDY STAGE
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 |  |  | ER | WAPA | Rhame 230 kV Sub | FACILITY STUDY STAGE
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | FACILITY STUDY STAGE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Underwood - Philip Tap 230 kV | FACILITY STUDY STAGE
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 |  |  | ER/NR | SUNC | Thistle 345 kV sub | FACILITY STUDY STAGE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | FACILITY STUDY STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | FACILITY STUDY STAGE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 |  |  | ER/NR | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 |  |  | ER | WFEC | Snyder - Cache 138 kV | FACILITY STUDY STAGE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 |  |  | ER/NR | SPS | Cole 115kV | FACILITY STUDY STAGE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Neset 230 kV Substation | FACILITY STUDY STAGE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | FACILITY STUDY STAGE
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 |  |  | ER/NR | WERE | Wichita 345kV Substation | FACILITY STUDY STAGE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | GRDA | Dry Gulch 161kV sub | FACILITY STUDY STAGE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | FACILITY STUDY STAGE
GEN-2017-076 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 |  |  | ER | EMDE | Asbury Plant 161 kV | FACILITY STUDY STAGE
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 |  |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | FACILITY STUDY STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 |  |  | ER | WAPA | Underwood 115 kV Sub | FACILITY STUDY STAGE
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 |  |  | ER/NR | SPS | Texas County 115kV | FACILITY STUDY STAGE
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  | ER | BEPC-SPP | NELSON 7
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 |  |  | ER | SPS | TEXAS_CNTY 3
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 |  |  | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 |  |  | ER | NPPD | Sweetwater 345kV | IA PENDING
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 |  |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-123 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 298 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-124 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 150 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 74 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.12 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 |  |  | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery | 20 |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Gas Turbine | 17 |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-006GIA-53 | 03 CENTRAL | 16.5 | Dis-16-2-PQ | Wind | 238 |  |  | ER/NR | AECI | 5MARYVL
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 |  |  | ER | SPS | Palo Duro 115kV
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 |  |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 176 |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 248.4 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-007 | 01 NORTH | 16 | DIS-16-1 | Wind | 100.05 |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Steam Turbine | 29 |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 78.2 |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 |  |  | ER | BEPC-SPP | Fort Thompson-Leland Olds 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | WIND | 150 |  |  | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | WIND | 300 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-050 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 5.3 |  |  | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-073 | 03 CENTRAL | 16 | DIS-16-1 | WIND | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery | 20 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 2.17 |  |  | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-055 | 04 SOUTHEAST | 15 | DIS-15-2 | Solar | 40 |  |  | ER | WFEC | Erick 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 100.65 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 0.75 |  |  | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 0.75 |  |  | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 219.99 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-092 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 250 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 250 |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Tap White Lake - Stickeny 69kV
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.2 |  |  | ER | WAPA | Kimball 69kV
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 2 |  |  | ER/NR | WAPA | Wessington Springs 230kV
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  | ER/NR | XEL | Marshall 115kV
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER/NR | BEPC-SPP | Hilken 230kV [Ecklund 230kV]
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 16 |  |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.5 |  |  | ER | BEPC-SPP | Groton 115kV
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.4 |  |  | ER/NR | WAPA | Tripp Junction 115kV
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 3.5 |  |  | ER/NR | BEPC-SPP | Dickenson-Heskett 230kV
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 34 |  |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Gas | 125 |  |  | ER/NR | BEPC-SPP | Williston 115kV
MPC02100 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 0.75 |  |  | ER | OTP | Center - Mandan 230 kV
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 |  |  | ER | SUNC | Ninnescah 115kV
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.11 |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.72 |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 219.99 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 219.98 |  |  | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 300 |  |  | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.22 |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 44 |  |  | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.35 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 1 |  |  | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.53 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 3.96 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.67 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 0.11 |  |  | ER/NR | LES | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 73.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 50.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 |  |  | ER | SPS | FE-Clovis Interchange 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 1.8 |  |  | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 0.72 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-006GIA-27 | 04 SOUTHEAST | 8 | PQ | Wind | 150 |  |  | ER | AECI | Remington 138kV
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 22.5 |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 1 |  |  | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 3 |  |  | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 1 |  |  | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 15 |  |  | ER | NPPD | Ainsworth Wind Tap 115kV
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 1.8 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 290 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | Wind | 40.8 |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
NPPDBuffaloCountySolar | 02 NEBRASKA | 8 | PQ | Solar | 10 |  |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 02 NEBRASKA | 8 | PQ | Wind | 20 |  |  | ER | NPPD | Tekamah & Oakland 115kV
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 2 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 0.3 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 1.8 |  |  | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 |  |  | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 13.13 |  |  | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 59.2 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 1 |  |  | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 0.4 |  |  | ER | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 68.8 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 04 SOUTHEAST | 2 | ICS1 | Wind | 200 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 0.3 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
00NR | NRIS | Non-Converged | None | N/A | None | [7 empty] | None
01ALL | ERIS | Non-Converged | None | N/A | None | [7 empty] | None
01NR | NRIS | Non-Converged | None | N/A | None | [7 empty] | None
00NR | NRIS | Thermal | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 | 23SP, 26SP | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1 |  | 342 | 94.4 | 110.01 |  |  |  | Fargo 230 kV Terminal Equipment Upgrades
00NR | NRIS | Thermal | None | 26WP | None | [7 empty] | None
01ALL | ERIS | Thermal | 652296 WARD 4 230 652426 BISMARK4 230 1 | 23SP | P12:230:MDU::MERRICOURT:WISHEK:1:::: |  | 331 | 70.4 | 103.16 |  |  |  | Ward to Bismark 230 kV Structure Replacements
01ALL | ERIS | Thermal | None | 26L | None | [7 empty] | None
01ALL | ERIS | Thermal | None | 26SP | None | [7 empty] | None
01ALL | ERIS | Thermal | None | 26WP | None | [7 empty] | None
01NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
00NR | NRIS | Voltage | None | N/A | None | [7 empty] | None
01ALL | ERIS | Voltage | None | N/A | None | [7 empty] | None
01NR | NRIS | Voltage | None | N/A | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
MPC03800 | 01-North | TBD | ERIS | Ward to Bismark 230 kV Structure Replacements | Current Study | Transimission line structure replacements/raising of spans required to meet minimum required MVA of 345 MVA | 1444994.6708 | 24.08% | 6000000 | 7.454%
MPC03900 | 01-North | TBD | ERIS | Ward to Bismark 230 kV Structure Replacements | Current Study | Transimission line structure replacements/raising of spans required to meet minimum required MVA of 345 MVA | 873932.7769 | 14.57% | 6000000 | 7.454%
MPC04000 | 01-North | TBD | ERIS | Ward to Bismark 230 kV Structure Replacements | Current Study | Transimission line structure replacements/raising of spans required to meet minimum required MVA of 345 MVA | 3681072.5523 | 61.35% | 6000000 | 15.82%
MPC03800 | 01-North | TBD | NRIS | Fargo 230 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at the Fargo 230 kV substation | 884589.4089 | 36.76% | 2406249 | 2.723%
MPC03900 | 01-North | TBD | NRIS | Fargo 230 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at the Fargo 230 kV substation | 534999.6745 | 22.23% | 2406249 | 2.723%
MPC04000 | 01-North | TBD | NRIS | Fargo 230 kV Terminal Equipment Upgrades | Current Study | Upgrade terminal equipment at the Fargo 230 kV substation | 986659.9166 | 41% | 2406249 | 2.531%
Total | [6 empty] | 8406249

## Upgrade Summary
Upgrade Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time (months) | Total Upgrade Cost
Current Study | 01 - North | MPC03800-MPC04000 | NRIS | Fargo 230 kV Terminal Equipment Upgrades | TBD | Upgrade terminal equipment at the Fargo 230 kV substation | WAPA | 36 | 2406249
Current Study | 01 - North | MPC03800-MPC04000 | ERIS | Ward to Bismark 230 kV Structure Replacements | TBD | Transimission line structure replacements/raising of spans on the existing Ward to Bismark 230 kV 4.2 mile line | WAPA | 36 | 6000000
8406249

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00NR | 0 | 23SP | N/A | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | 26SP | N/A | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | 26WP | N/A | " | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | 23SP | N/A | " | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | 26L | N/A | " | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | 26WP | N/A | " | None |  |  |  |  | None
Non-Converge | 01NR | 0 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 00NR | 2 | 23SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07622 | 110.01 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 23SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07622 | 110.01 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 23SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07622 | 110.01 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 23SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07622 | 110.01 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 23SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09813 | 110.01 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 23SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09813 | 110.01 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 23SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07622 | 109.97 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 00NR | 2 | 23SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07622 | 109.97 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 00NR | 2 | 23SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09814 | 109.97 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 00NR | 2 | 23SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07622 | 109.96 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 00NR | 2 | 23SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07622 | 109.96 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 00NR | 2 | 23SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09814 | 109.96 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 00NR | 2 | 23SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07617 | 109.87 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 2 | 23SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07617 | 109.87 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 2 | 23SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09809 | 109.87 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 2 | 23SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07596 | 109.76 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 2 | 23SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07596 | 109.76 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 2 | 23SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09788 | 109.76 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 2 | 23SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07663 | 107.12 | P23:345:OTP:JAMESTN3:3125:R2020
Thermal | 00NR | 2 | 23SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07663 | 107.12 | P23:345:OTP:JAMESTN3:3125:R2020
Thermal | 00NR | 2 | 23SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09864 | 107.12 | P23:345:OTP:JAMESTN3:3125:R2020
Thermal | 00NR | 2 | 26SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07611 | 101.78 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 26SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07611 | 101.78 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 26SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07611 | 101.78 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 26SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07611 | 101.78 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 26SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09803 | 101.78 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 26SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09803 | 101.78 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 00NR | 2 | 26SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07611 | 101.74 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 00NR | 2 | 26SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07611 | 101.74 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 00NR | 2 | 26SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07611 | 101.74 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 00NR | 2 | 26SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07611 | 101.74 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 00NR | 2 | 26SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09803 | 101.74 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 00NR | 2 | 26SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09803 | 101.74 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 00NR | 2 | 26SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07606 | 101.64 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 2 | 26SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07606 | 101.64 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 2 | 26SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09798 | 101.64 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 00NR | 2 | 26SP | MPC03800 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07584 | 101.49 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 2 | 26SP | MPC03900 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.07584 | 101.49 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 2 | 26SP | MPC04000 | TO -> FROM' | 602006 SHEYNNE4 230 652435 FARGO 4 230 1 |  | 342 | 0.09777 | 101.49 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 00NR | 2 | 26WP | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 2 | 23SP | MPC03800 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10852 | 103.16 | P12:230:MDU::MERRICOURT:WISHEK:1::::
Thermal | 01ALL | 2 | 23SP | MPC03900 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10852 | 103.16 | P12:230:MDU::MERRICOURT:WISHEK:1::::
Thermal | 01ALL | 2 | 23SP | MPC04000 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.2083 | 103.16 | P12:230:MDU::MERRICOURT:WISHEK:1::::
Thermal | 01ALL | 2 | 23SP | MPC03800 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10224 | 100.76 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 01ALL | 2 | 23SP | MPC03800 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10224 | 100.76 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 01ALL | 2 | 23SP | MPC03800 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10224 | 100.75 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 01ALL | 2 | 23SP | MPC03800 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10225 | 100.74 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 01ALL | 2 | 23SP | MPC03800 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10221 | 100.73 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 2 | 23SP | MPC03800 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10225 | 100.71 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 01ALL | 2 | 23SP | MPC03900 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10224 | 100.76 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 01ALL | 2 | 23SP | MPC03900 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10224 | 100.76 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 01ALL | 2 | 23SP | MPC03900 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10224 | 100.75 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 01ALL | 2 | 23SP | MPC03900 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10225 | 100.74 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 01ALL | 2 | 23SP | MPC03900 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10221 | 100.73 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 2 | 23SP | MPC03900 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.10225 | 100.71 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 01ALL | 2 | 23SP | MPC04000 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.19961 | 100.76 | P12:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 01ALL | 2 | 23SP | MPC04000 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.19961 | 100.76 | P21:345:OTP:AUTO-SINGLE:BUFFALO3:JAMESTN3:1
Thermal | 01ALL | 2 | 23SP | MPC04000 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.19961 | 100.75 | P23:345:OTP:BUFFALO3:3655:V2016
Thermal | 01ALL | 2 | 23SP | MPC04000 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.19961 | 100.74 | P23:345:OTP:JAMESTN3:3135:V2020
Thermal | 01ALL | 2 | 23SP | MPC04000 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.19958 | 100.73 | P12:345:MPC:JAMESTOWN-BISON:JAMESTN3:BISON 3
Thermal | 01ALL | 2 | 23SP | MPC04000 | FROM -> TO' | 652296 WARD 4 230 652426 BISMARK4 230 1 |  | 331 | 0.19961 | 100.71 | P23:345:OTP:JAMESTN3:3145:V2020
Thermal | 01ALL | 2 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 2 | 26SP | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 2 | 26WP | N/A | " | None |  |  |  |  | None
Thermal | 01NR | 2 | 26L | N/A | " | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00NR | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 01ALL | 3 | N/A | N/A | None | [7 empty] | None
Voltage | 01NR | 3 | N/A | N/A | None | [7 empty] | None