## Executive Summary
Executive Summary: SPP Affected Systems Impact Study of MPC04300
Pursuant to the Southwest Power Pool (SPP) and Minnkota Power Cooperative (MPC) Joint Operating Agreement (JOA), SPP has conducted this Affected Systems Impact Study (ASIS) for generation interconnection requests studied in the MPC Generator Interconnection Queue. The primary objective of this ASIS is to identify constraints and over-dutied equipment on SPP facilities associated with the new MPC interconnection request. The study analysis for the generation interconnection requests included in this ASIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The Generator Interconnection Manual Version 1.7 posted on https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf contains details about the ASIS process, methodology, definitions, and useful links. Please review the Generator Interconnection Manual or contact GI-AFS@SPP.org for more information about the study process. SPP ASIS of MPC04200 includes study requests in the following cluster groups: 01 - North
Generator Interconnection Manual Version 1.7
https://opsportal.spp.org/documents/studies/DISIS%20Manual.pdf
This ASIS analyzes the impact of interconnecting new generation for total of:
400 MW
The total costs of Network Upgrades identified in this ASIS are estimated at:
7931000
Models Used in Study
2021 ITP Series
Summer: 2023, 2026
Winter: 2026
Light: 2026
Assumptions Used in Study
Queued after DISIS-2017-002 and all higher-queued MPC requests Incorporates DISIS-2017-002 Phase 2 and all higher queued identified network upgrades Incorporates DISIS-2017-002 Decision Point 2 withdrawals and associated impacts to identified network upgrades Incorporates model reduction Incorporates group reduction Incoporates fuel-based dispatch
By: SPP Generator Interconnection Department
Published: May 8, 2023

## Revision History
Revision History
Date | Author | Change Description
4500800% | SPP | Draft MPC04300 Posting
4505400% | SPP | Final MPC04300 Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Service | Area | POI | Status
MPC04300 | 01 - North | 20.5 | DIS-18-2/19-1-PQ | Wind | 400 | 160 | 652437 GRNDFKS4 230 996740 GK KV1A _1 115 1 (ftlo) System Intact | ER/NR | OTP | Center-Prairie 345 kV Line | --
ASGI-2017-013 | 01 - North | 20 | DIS-18-1 | Wind | 40 |  |  | ER | WAPA | Wolsey 69kV Substation | DISIS STAGE
GEN-2018-007 | 01 - North | 20 | DIS-18-1 | Solar | 150 |  |  | ER/NR | WAPA | Summit 115kV Substation | DISIS STAGE
GEN-2018-008 | 01 - North | 20 | DIS-18-1 | Wind | 252 |  |  | ER/NR | BEPC-SPP | Groton-Leland Olds 345kV Line | DISIS STAGE
GEN-2018-010 | 01 - North | 20 | DIS-18-1 | Battery | 74.1 |  |  | ER/NR | BEPC-SPP | Neset 230kV Substation | DISIS STAGE
GEN-2018-039 | 01 - North | 20 | DIS-18-1 | Solar | 72 |  |  | ER/NR | WAPA | Edgeley 115kV substation | DISIS STAGE
GEN-2018-012 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 74.1 |  |  | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2018-025 | 02 - Nebraska | 20 | DIS-18-1 | Battery | 200 |  |  | ER | OPPD | Fort Calhoun 345kV Substation | DISIS STAGE
GEN-2018-033 | 02 - Nebraska | 20 | DIS-18-1 | Battery | 200 |  |  | ER | OPPD | Cass County 345kV Substation | DISIS STAGE
GEN-2018-037 | 02 - Nebraska | 20 | DIS-18-1 | Battery | 100 |  |  | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | DISIS STAGE
GEN-2018-043 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 500 |  |  | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | DISIS STAGE
GEN-2018-044 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 500 |  |  | ER | OPPD | Fort Calhoun 345kV Substation | DISIS STAGE
GEN-2018-056 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 102.6 |  |  | ER/NR | WAPA | Grand Prairie 345kV | DISIS STAGE
GEN-2018-060 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 50 |  |  | ER/NR | NPPD | Axtell-Post Rock 345 kV | DISIS STAGE
ASGI-2018-003 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  | ER | KCPL | AP City 69kV Substation | DISIS STAGE
ASGI-2018-006 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  | ER | KCPL | Metz 69kV Substation | DISIS STAGE
ASGI-2018-007 | 03 - Central | 20 | DIS-18-1 | Solar | 20 |  |  | ER | KCPL | Salisbury 161kV Substation | DISIS STAGE
ASGI-2018-010 | 03 - Central | 20 | DIS-18-1 | Solar | 35 |  |  | ER | KCPL | Pleasant Valley 161kV Substation | DISIS STAGE
ASGI-2018-011 | 03 - Central | 20 | DIS-18-1 | Solar | 35 |  |  | ER | KCPL | South Ottawa 161kV Substation | DISIS STAGE
GEN-2018-009 | 03 - Central | 20 | DIS-18-1 | Wind | 150 |  |  | ER | SUNC | Cimarron 115kV Substation | DISIS STAGE
GEN-2018-013 | 03 - Central | 20 | DIS-18-1 | Wind | 74.1 |  |  | ER | WERE | Abilene Energy Center-Northview 115kV Line | DISIS STAGE
GEN-2018-014 | 03 - Central | 20 | DIS-18-1 | Wind | 74.1 |  |  | ER | KCPL | Holt County 345kV Substation | DISIS STAGE
GEN-2018-022 | 03 - Central | 20 | DIS-18-1 | Solar | 300 |  |  | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-030 | 03 - Central | 20 | DIS-18-1 | Battery | 200 |  |  | ER | SPS | Lamar-Finney 345kV Substation | DISIS STAGE
GEN-2018-031 | 03 - Central | 20 | DIS-18-1 | Battery | 50 |  |  | ER | KCPL | Blue Valley 161kV Substation | DISIS STAGE
GEN-2018-032 | 03 - Central | 20 | DIS-18-1 | Wind | 310 |  |  | ER | WERE | Neosho 345kV Substation | DISIS STAGE
GEN-2018-049 | 03 - Central | 20 | DIS-18-1 | Solar | 120 |  |  | ER | SUNC | Thistle 345kV Substation | DISIS STAGE
GEN-2018-053 | 03 - Central | 20 | DIS-18-1 | Wind | 100 |  |  | ER | WERE | Kelly 161kV Substation | DISIS STAGE
GEN-2018-054 | 03 - Central | 20 | DIS-18-1 | Solar | 120 |  |  | ER | KCPL | KC South - N. Raymore 161kV Line | DISIS STAGE
GEN-2018-057 | 03 - Central | 20 | DIS-18-1 | Solar | 203.4 |  |  | ER/NR | WERE | Gordon Evans 138kV | DISIS STAGE
GEN-2018-058 | 03 - Central | 20 | DIS-18-1 | Solar | 252 |  |  | ER/NR | WERE | Stranger Creek 345kV | DISIS STAGE
GEN-2018-059 | 03 - Central | 20 | DIS-18-1 | Solar | 252 |  |  | ER/NR | WERE | Stranger Creek 345kV | DISIS STAGE
GEN-2018-061 | 03 - Central | 20 | DIS-18-1 | Wind | 50 |  |  | ER | WERE | Kelly 161kV Substation | DISIS STAGE
GEN-2018-062 | 03 - Central | 20 | DIS-18-1 | Solar | 75.6 |  |  | ER/NR | KACY | Nearman 161kV substation | DISIS STAGE
GEN-2018-003 | 04 - Southeast | 20 | DIS-18-1 | Solar | 150 |  |  | ER/NR | AEPW | North Boston-Bann 138kV Line | DISIS STAGE
GEN-2018-011 | 04 - Southeast | 20 | DIS-18-1 | Battery | 74.1 |  |  | ER/NR | WFEC | Dover 138 kV Switching Station | DISIS STAGE
GEN-2018-021 | 04 - Southeast | 20 | DIS-18-1 | Solar | 74.1 |  |  | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | DISIS STAGE
GEN-2018-024 | 04 - Southeast | 20 | DIS-18-1 | Battery | 100 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2018-026 | 04 - Southeast | 20 | DIS-18-1 | Battery | 100 |  |  | ER | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2018-027 | 04 - Southeast | 20 | DIS-18-1 | Battery | 100 |  |  | ER | AEPW | Tulsa Power Station 38kV Substation | DISIS STAGE
GEN-2018-028 | 04 - Southeast | 20 | DIS-18-1 | Battery | 200 |  |  | ER | OKGE | Tulsa North 138kV Substation | DISIS STAGE
GEN-2018-029 | 04 - Southeast | 20 | DIS-18-1 | Battery | 100 |  |  | ER | OKGE | Horseshoe Lake 138kV Substation | DISIS STAGE
GEN-2018-048 | 04 - Southeast | 20 | DIS-18-1 | Solar | 300 |  |  | ER | OKGE | Pecan Creek 345kV Substation | DISIS STAGE
GEN-2018-050 | 04 - Southeast | 20 | DIS-18-1 | Solar | 200 |  |  | ER | AEPW | Longwood 345kV Substation | DISIS STAGE
GEN-2018-051 | 04 - Southeast | 20 | DIS-18-1 | Battery | 35 |  |  | ER | OKGE | Pecan Creek 345kV | DISIS STAGE
GEN-2018-055 | 04 - Southeast | 20 | DIS-18-1 | Solar | 252 |  |  | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | DISIS STAGE
GEN-2018-004 | 05 - Southwest | 20 | DIS-18-1 | Solar | 74.99 |  |  | ER | SPS | T14 Circuit 115kV line | DISIS STAGE
GEN-2018-015 | 05 - Southwest | 20 | DIS-18-1 | Solar | 252 |  |  | ER/NR | SPS | Tuco-Oklaunion 345kV Line | DISIS STAGE
GEN-2018-052 | 05 - Southwest | 20 | DIS-18-1 | Battery | 70 |  |  | ER | SPS | Roadrunner 115kV Substation | DISIS STAGE
J1040 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER/NR | MDU | Wishek Junction 230 kV Substation | Under Construction
J1045 | 01 - North | 19.5 | DIS-18-1-PQ | Battery | 20 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | Under Construction
J1072 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | XEL | Adams 345 kV Substation | Under Construction
J1092 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Three Lakes 115 kV Substation | Not Started
J1124 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Byron 345kV Substation | Under Construction
J1164 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER | ALTW | Magnolia 161 kV Substation | Not Started
J1169 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | XEL | Grant 115 kV Substation | Not Started
J1181 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER | ALTW | Hazleton - Mitchell county 345 kV line | Under Construction
J1221 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | GRE | Wing River- Riverton 230kV line | Not Started
J1298 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Hayward - Murphy Creek 161kV Line | Not Started
J1312 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | XEL | Grant 115 kV Substation | Not Started
J1314 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | DPC | Apple River 161 kV Substation | Not Started
J1325 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | ALTW | Magnolia 161 kV substation | Not Started
J1426 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Benton County 115kV Substation | Not Started
J1445 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Mayhew Lake 115kV Substation | Not Started
J1474 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  | ER/NR | XEL | Pine Lake - Eagle Point 115kV Line | Not Started
J1485 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  | ER | OTP | Astoria 345 kV Substation (J493/J510) | Not Started
J1503 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Huntley 345 kV | Not Started
J1504 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Huntley 345 kV | Not Started
J1528 | 01 - North | 19.5 | DIS-18-1-PQ | Battery | 0 |  |  | ER/NR | XEL | Eau Claire to AS King 345 kV | Not Started
J1534 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | XEL | Byron 345kV | Not Started
J1566 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | ALTW | Rutland Substation 161kV | Not Started
J1572 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | XEL | Huntley to Blue Earth 161kV | Not Started
J1575 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 70 |  |  | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Not Started
J1581 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | XEL | Nobles County 345 kV Substation | Not Started
J1588 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | XEL | Bison 345kV | Not Started
J1605 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | XEL | Sherburne 345kV | Not Started
J1611 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 120 |  |  | ER/NR | XEL | Langola 115kV Tap | Not Started
J1620 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER | XEL | Pipestone to Split Rock 115kV | Not Started
J1657 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER | XEL | Pine Lake to Apple River 161 kV | Not Started
J1730 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | XEL | Eau Claire to AS King 345 kV | Not Started
J1769 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 80 |  |  | ER | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Not Started
J1808 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 148 |  |  | ER | DPC | Barron 161 kV | Not Started
J1826 | 01 - North | 19.5 | DIS-18-1-PQ | Hydro | 4 |  |  | ER | XEL | Cannon Falls Transmission 69 kV | Not Started
J967 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 150 |  |  | ER | XEL | Adams 345kV Substation | Under Construction
MPC03600 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | --
MPC03700 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | --
MPC03800 | 01 - North | 19.5 | DIS-18-1-PQ | Wind_PQE | 250 |  |  | ER/NR | OTP | Center-Prairie 345 kV Line | --
MPC03900 | 01 - North | 19.5 | DIS-18-1-PQ | Wind_PQE | 151.2 |  |  | ER/NR | OTP | Center-Prairie 345 kV Line | --
MPC04000 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  | ER/NR | OTP | Square Butte 230 kV Substation | --
IR-39 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 150 |  |  | ER/NR | ALTW | Dundee 161 kV Substation | --
J1050 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 225 |  |  | ER/NR | ALTW | Doud Tap 161 kV Substation | Under Construction
J1132 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | ALTW | Creston East 69 kV Substation | Under Construction
J1174 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | Under Construction
J1175 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 165 |  |  | ER | ALTW | Ledyard - Colby 345kV Line Tap | Not Started
J1270 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER | MEC | Kossuth - O'Brien 345 kV Line Tap | Not Started
J1313 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | ALTW | 161kV bus at Karma substation | Not Started
J1359 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Gas | 95 |  |  | ER/NR | ALTW | Oakridge 69 kV Substation | Not Started
J1365 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 169.4 |  |  | ER | ALTW | Traer 161-kV Substation | Not Started
J1444 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | ALTW | Duane Arnold 345kV Substation | Not Started
J1520 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV | Not Started
J1529 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Not Started
J1530 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Not Started
J1532 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | MEC | Clarinda-Coburg 69 kV | Not Started
J1590 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  | ER/NR | MEC | O'Brien - Raun 345 kV | Not Started
J953 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Diesel | 2 |  |  | ER/NR | ALTW | Iowa Jct 34.5 kV | Not Started
J954 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 1.4 |  |  | ER/NR | ALTW | Iowa Jct 34.5 kV | Not Started
J982 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | Not Started
J1025 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 290 |  |  | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | Not Started
J1026 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 380 |  |  | ER/NR | AMMO | Maywood - Spencer Creek 345 kV Line Tap | Not Started
J1145 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | Not Started
J1182 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | AMMO | Zachary Substation 345 kV Bus | Under Construction
J1191 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 64 |  |  | ER/NR | CWLD | Bolstad 69 kV Substation | Not Started
J1202 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 68.4 |  |  | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | Not Started
J1208 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | Not Started
J1209 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | Not Started
J1213 | 03 - Central | 19.5 | DIS-18-1-PQ | Hydro | 60 |  |  | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | Not Started
J1216 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 185 |  |  | ER/NR | AMIL | Ashley 138 kV Substation | Not Started
J1241 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | Not Started
J1268 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | AMMO | Pike - Troy 161kV Line | Not Started
J1303 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | Not Started
J1306 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMIL | Commodore-Jordan 345kV Line | Not Started
J1311 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | Not Started
J1352 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Spencer Creek - Montgomery 345kV Line | Not Started
J1488 | 03 - Central | 19.5 | DIS-18-1-PQ | HVDC | 500 |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Not Started
J1490 | 03 - Central | 19.5 | DIS-18-1-PQ | HVDC | 1000 |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | Not Started
J956 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Spencer Creek 345kV Substation | Not Started
J976 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | Under Construction
J987 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Montgomery 161kV Substation | Under Construction
J994 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | AMMO | Guthrie 161 kV Substation | Under Construction
J1007 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  | ER/NR | EES-EAI | Marion - Marked Tree 161 kV | Under Construction
J1030 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | EES | Poco - Menard 138 kV | Under Construction
J1034 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 225 |  |  | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | Under Construction
J1060 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 450 |  |  | ER/NR | EES-EAI | West Memphis - Keo 500 kV | Under Construction
J1087 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | Under Construction
J1107 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | Under Construction
J1125 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV | Under Construction
J1146 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Coal | 680 |  |  | ER/NR | EES-EAI | San Souci 500 kV | In Service
J1155 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | EES-EAI | Driver 230 kV | Under Construction
J1205 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER | CLEC | Centennial - West Bay 138 kV | Under Construction
J1215 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 155 |  |  | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | Not Started
J1231 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  | ER/NR | BREC | Barkley - Caldwell 161kV Line | Not Started
J1299 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 149 |  |  | ER/NR | AMMO | Miner - Kelso 161kV Line | Not Started
J1373 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | Under Construction
J1402 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Battery | 0 |  |  | ER/NR | EES-EAI | Cash - Newport AB161kV Line | Not Started
J1415 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | Not Started
J1424 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER | CLEC | Cooper - Penton Road 230 kV | Under Construction
J1425 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Gas | 230 |  |  | ER/NR | EES-EAI | Pine Bluff International Paper 115 kV | In Service
J1434 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | Under Construction
J1436 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER | EES | Oak Ridge 115 kV | Not Started
J1437 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 180 |  |  | ER/NR | EES-EAI | AECC Dry Creek 161 kV | Under Construction
J1442 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 105 |  |  | ER | EES | Rich (SHECO) - Livingston 138 kV | Not Started
J1509 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EMI | Greenwood - Pickens 115 kV | Not Started
J1514 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | Driver 230kV | Not Started
J1558 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | Not Started
J1559 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Not Started
J1562 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | Not Started
J1577 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | Hardin West SS to Sheridan 115 kV | Not Started
J1598 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 325 |  |  | ER | EES | Solac - Chalkley 230kV | Not Started
J1602 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Battery | 25 |  |  | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Not Started
J1607 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Battery | 0 |  |  | ER/NR | EES-EAI | Hardin West SS to Sheridan 115 kV | Not Started
J1612 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Not Started
J1669 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | Not Started
J1670 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Not Started
J1671 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER | EES | Rocky Creek to Lewis Creek 230kV | Not Started
J1672 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  | ER/NR | EES-EMI | Tinnin Road 230kV | Not Started
J1673 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | Not Started
J1709 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Battery | 100 |  |  | ER | EES | 138 kV Grimes | Not Started
J1710 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | Not Started
J1747 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  | ER/NR | EES-EMI | J830 POI | Not Started
J1748 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EMI | Twinkletown 230 kV | Not Started
J1759 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Battery | 0 |  |  | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | Not Started
J1760 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 205 |  |  | ER/NR | EES | Timberland 230kV | Not Started
J1816 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | Not Started
J1819 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Battery | 0 |  |  | ER/NR | EES-EAI | Entergy Keo - West Memphis 500kV Line Tap | Not Started
J1820 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | Not Started
J1821 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Battery | 0 |  |  | ER/NR | EES-EAI | Entergy Keo -West Memphis 500kV Line tap | Not Started
J1827 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 90 |  |  | ER/NR | EES | Bastrop tap point | Not Started
J1834 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Gas | 126 |  |  | ER/NR | EES | Sabine 138/230 kV Substation | Not Started
J1842 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 135 |  |  | ER | EES-EAI | Forrest City to Wynne S 161 KV | Not Started
GEN-2017-175 | 01 - North | 19 | DIS-17-2 | Wind | 300 |  |  | ER | WAPA | VFODNES4 | DISIS STAGE
GEN-2017-199 | 01 - North | 19 | DIS-17-2 | Battery | 202 |  |  | ER/NR | WAPA | BROADLND-BE3 | DISIS STAGE
GEN-2017-200 | 01 - North | 19 | DIS-17-2 | Wind | 302 |  |  | ER/NR | WAPA | BROADLND-BE3 | DISIS STAGE
GEN-2017-214 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | LOGAN___-BE4 | DISIS STAGE
GEN-2017-215 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | LOGAN___-BE4 | DISIS STAGE
GEN-2017-216 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  | ER/NR | WAPA | LOGAN___-BE4 | DISIS STAGE
GEN-2017-222 | 01 - North | 19 | DIS-17-2 | Wind | 180 |  |  | ER | WAPA | DENISON4 | FACILITY STUDY STAGE
GEN-2017-235 | 01 - North | 19 | DIS-17-2 | Wind | 50 |  |  | ER/NR | WAPA | BERTHOLD-CP7 | DISIS STAGE
GEN-2017-236 | 01 - North | 19 | DIS-17-2 | Wind | 50 |  |  | ER/NR | WAPA | BERTHOLD-CP7 | DISIS STAGE
GEN-2017-105 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 75 |  |  | ER/NR | OPPD | Raun - Tekamah 161kV Line Tap | FACILITY STUDY STAGE
GEN-2017-144 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 200 |  |  | ER | WAPA | HOLT.CO3 | FACILITY STUDY STAGE
GEN-2017-181 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | NPPD | MOORE 3 | FACILITY STUDY STAGE
GEN-2017-182 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 128 |  |  | ER/NR | NPPD | MOORE 3 | FACILITY STUDY STAGE
GEN-2017-198 | 02 - Nebraska | 19 | DIS-17-2 | Battery | 11.64 |  |  | ER | OPPD | S901 8 | FACILITY STUDY STAGE
GEN-2017-201 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | NPPD | HOSKINS3 | FACILITY STUDY STAGE
GEN-2017-210 | 02 - Nebraska | 19 | DIS-17-2 | Solar | 310 |  |  | ER | NPPD | MCCOOL 3 | FACILITY STUDY STAGE
GEN-2017-234 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 115 |  |  | ER | NPPD | Spalding - North Loup 115kV Line Tap | FACILITY STUDY STAGE
ASGI-2017-014 | 03 - Central | 19 | DIS-17-2 | Solar | 40 |  |  | ER/NR | KCPL | Post Oak 69 kV | --
GEN-2017-108 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | S.HARP 5 | DISIS STAGE
GEN-2017-111 | 03 - Central | 19 | DIS-17-2 | Solar | 152 |  |  | ER | KCPL | Stilwell - S Harper 161kV Line Tap | DISIS STAGE
GEN-2017-115 | 03 - Central | 19 | DIS-17-2 | Wind | 244 |  |  | ER | KCPL | HOLT 7 | DISIS STAGE
GEN-2017-119 | 03 - Central | 19 | DIS-17-2 | Wind | 180 |  |  | ER | SUNC | ELMCREEK7 | DISIS STAGE
GEN-2017-120 | 03 - Central | 19 | DIS-17-2 | Wind | 260 |  |  | ER | WERE | Northview - Abilene Energy Center 115kV Line Tap | DISIS STAGE
GEN-2017-121 | 03 - Central | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | WERE | SUMNER 4 | DISIS STAGE
GEN-2017-125 | 03 - Central | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | WERE | SWISVAL7 | DISIS STAGE
GEN-2017-128 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | WERE | SWISVAL7 | DISIS STAGE
GEN-2017-131 | 03 - Central | 19 | DIS-17-2 | Battery | 29.6 |  |  | ER/NR | WERE | ALTOONA4 | DISIS STAGE
GEN-2017-148 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  | ER/NR | EMDE | JOP391 5 | FACILITY STUDY STAGE
GEN-2017-179 | 03 - Central | 19 | DIS-17-2 | Wind | 222 |  |  | ER/NR | WERE | EVANS S4 | DISIS STAGE
GEN-2017-183 | 03 - Central | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | KCPL | St Joe - Nashua 345kV Line Tap | DISIS STAGE
GEN-2017-184 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  | ER/NR | KCPL | St Joe - Nashua 345kV Line Tap | DISIS STAGE
GEN-2017-188 | 03 - Central | 19 | DIS-17-2 | Solar | 130 |  |  | ER | EMDE | Brookline - Flint Creek 345kV Line Tap | FACILITY STUDY STAGE
GEN-2017-191 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | SWISVAL7 | DISIS STAGE
GEN-2017-192 | 03 - Central | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | WERE | SWISVAL7 | DISIS STAGE
GEN-2017-194 | 03 - Central | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | WERE | TECHILL6 | DISIS STAGE
GEN-2017-195 | 03 - Central | 19 | DIS-17-2 | Solar | 500.4 |  |  | ER/NR | KCPL | W.GRDNR7 | DISIS STAGE
GEN-2017-196 | 03 - Central | 19 | DIS-17-2 | Battery | 128 |  |  | ER/NR | KCPL | W.GRDNR7 | DISIS STAGE
GEN-2017-202 | 03 - Central | 19 | DIS-17-2 | Solar | 200 |  |  | ER/NR | SWPA | New Madrid - Sikeston 161kV Line Tap | FACILITY STUDY STAGE
GEN-2017-209 | 03 - Central | 19 | DIS-17-2 | Solar | 300 |  |  | ER | KCPL | LACYGNE7 | DISIS STAGE
GEN-2017-220 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | BUFFALO7 | DISIS STAGE
GEN-2017-221 | 03 - Central | 19 | DIS-17-2 | Battery | 152 |  |  | ER/NR | WERE | BUFFALO7 | DISIS STAGE
GEN-2017-225 | 03 - Central | 19 | DIS-17-2 | Battery | 76 |  |  | ER/NR | KCPL | CRAIG 7 | DISIS STAGE
GEN-2017-226 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  | ER/NR | WERE | EVANS N4 | DISIS STAGE
GEN-2017-227 | 03 - Central | 19 | DIS-17-2 | Battery | 201.6 |  |  | ER/NR | WERE | EVANS N4 | DISIS STAGE
GEN-2017-229 | 03 - Central | 19 | DIS-17-2 | Battery | 76 |  |  | ER/NR | KCPL | STILWEL7 | DISIS STAGE
GEN-2017-117 | 04 - Southeast | 19 | DIS-17-2 | Battery | 19.8 |  |  | ER/NR | WFEC | EL RENO4 | DISIS STAGE
GEN-2017-132 | 04 - Southeast | 19 | DIS-17-2 | Wind | 400 |  |  | ER/NR | OKGE | ARCADIA7 | DISIS STAGE
GEN-2017-133 | 04 - Southeast | 19 | DIS-17-2 | Wind | 200 |  |  | ER/NR | OKGE | ARCADIA7 | DISIS STAGE
GEN-2017-134 | 04 - Southeast | 19 | DIS-17-2 | Wind | 250 |  |  | ER/NR | OKGE | ARCADIA7 | DISIS STAGE
GEN-2017-137 | 04 - Southeast | 19 | DIS-17-2 | Wind | 295 |  |  | ER/NR | OKGE | ARCADIA7 | DISIS STAGE
GEN-2017-140 | 04 - Southeast | 19 | DIS-17-2 | Solar | 160 |  |  | ER/NR | AEPW | CLARKSV7 | DISIS STAGE
GEN-2017-141 | 04 - Southeast | 19 | DIS-17-2 | Solar | 241.7 |  |  | ER/NR | AEPW | CLARKSV7 | DISIS STAGE
GEN-2017-149 | 04 - Southeast | 19 | DIS-17-2 | Wind | 258 |  |  | ER/NR | OKGE | JOHNCO 7 | DISIS STAGE
GEN-2017-150 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | MINCO 7 | DISIS STAGE
GEN-2017-152 | 04 - Southeast | 19 | DIS-17-2 | Wind | 252 |  |  | ER/NR | OKGE | MCCLAIN4 | DISIS STAGE
GEN-2017-154 | 04 - Southeast | 19 | DIS-17-2 | Wind | 255 |  |  | ER/NR | OKGE | JOHNCO 7 | DISIS STAGE
GEN-2017-155 | 04 - Southeast | 19 | DIS-17-2 | Wind | 300 |  |  | ER/NR | OKGE | MUSKOGE7 | DISIS STAGE
GEN-2017-164 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | WOODRNG7 | DISIS STAGE
GEN-2017-166 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | SUNNYSD7 | DISIS STAGE
GEN-2017-167 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | SUNNYSD7 | DISIS STAGE
GEN-2017-168 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  | ER/NR | OKGE | MCCLAIN4 | DISIS STAGE
GEN-2017-169 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | MCCLAIN4 | DISIS STAGE
GEN-2017-171 | 04 - Southeast | 19 | DIS-17-2 | Solar | 150 |  |  | ER/NR | AEPW | TERRYRD7 | DISIS STAGE
GEN-2017-172 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | TERRYRD7 | DISIS STAGE
GEN-2017-173 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  | ER/NR | AEPW | TERRYRD7 | DISIS STAGE
GEN-2017-178 | 04 - Southeast | 19 | DIS-17-2 | Battery | 52 |  |  | ER/NR | OKGE | WOODRNG7 | DISIS STAGE
GEN-2017-203 | 04 - Southeast | 19 | DIS-17-2 | Solar | 210 |  |  | ER | OKGE | RENFROW7 | DISIS STAGE
GEN-2017-213 | 04 - Southeast | 19 | DIS-17-2 | Solar | 300 |  |  | ER | AEPW | CLARKSV7 | DISIS STAGE
GEN-2017-230 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | TRYON 4 | DISIS STAGE
GEN-2017-231 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  | ER/NR | OKGE | BRANCH 5 | FACILITY STUDY STAGE
GEN-2017-232 | 04 - Southeast | 19 | DIS-17-2 | Solar | 52.2 |  |  | ER/NR | OKGE | BROWN 4 | DISIS STAGE
GEN-2017-233 | 04 - Southeast | 19 | DIS-17-2 | Wind | 215 |  |  | ER/NR | OKGE | MINCO 7 | DISIS STAGE
GEN-2017-240 | 04 - Southeast | 19 | DIS-17-2 | Solar | 202 |  |  | ER/NR | OKGE | BEGGS 4 | DISIS STAGE
GEN-2017-146 | 05 - Southwest | 19 | DIS-17-2 | Wind | 151.8 |  |  | ER | SPS | Deaf Smith 6 - Plant X 230kV Line Tap | DISIS STAGE
GEN-2017-151 | 05 - Southwest | 19 | DIS-17-2 | Wind | 300 |  |  | ER | SPS | CRAWFISH_DR - O.K.U.-7 345kV Line Tap | DISIS STAGE
GEN-2017-158 | 05 - Southwest | 19 | DIS-17-2 | Wind | 265 |  |  | ER | SPS | TOLK 6 | DISIS STAGE
GEN-2017-187 | 05 - Southwest | 19 | DIS-17-2 | Solar | 150 |  |  | ER | SPS | SULPHUR 3 | DISIS STAGE
GEN-2017-239 | 05 - Southwest | 19 | DIS-17-2 | Solar | 300 |  |  | ER | SPS | MUSTANG 6 | DISIS STAGE
J545 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  | ER | XEL | Buffalo 115kV Substation | In Service
J722 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | OTP | Big Stone South 230kV Substation | Under Construction
J801 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | Under Construction
J803 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 32.5 |  |  | ER | XEL | Tracy 69 kV line | Under Construction
J874 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line | Under Construction
J897 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  | ER | GRE | Prairie - Ramsey 230 kV line | Not Started
J898 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap | Under Construction
J926 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 101.28 |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line | Under Construction
IR24 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC | --
IR32 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  | ER/NR | ALTW | Murray Junction 69 kV substation | --
J836 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  | ER | ALTW | Ledyard 345kV Substation | Not Started
J877 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | Under Construction
GIA-83 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  | ER/NR | AECI | McCredie 345 kV | --
GIA-85 | 03 - Central | 18.5 | DIS-17-2-PQ | Battery | 447.3 |  |  | ER/NR | AECI | Morgan 345 kV | --
GIA-86 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  | ER/NR | AECI | Thomas Hill 69 kV | --
GIA-88 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 92.09 |  |  | ER/NR | AECI | Eudora 69 kV | --
GIA-90 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  | ER/NR | AECI | Montgomery City 161 kV | --
GIA-91 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  | ER/NR | AECI | Sedalia 69 kV | --
GIA-93 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  | ER/NR | AECI | Palmyra 161 kV | --
GIA-95 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  | ER/NR | AECI | Jasper-Morgan 345 kV | --
GEN-2017-010 | 01 - North | 18 | DIS-17-1 | Wind | 200.1 |  |  | ER | WAPA | Rhame 230 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-014 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Underwood - Philip Tap 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-048 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  | ER | WAPA | Neset 230 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-094 | 01 - North | 18 | DIS-17-1 | Wind | 200 |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-097 | 01 - North | 18 | DIS-17-1 | Solar | 128 |  |  | ER | WAPA | Underwood 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-004 | 03 - Central | 18 | DIS-17-1 | Wind | 201.6 |  |  | ER | SUNC | Elm Creek - Summit 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-005 | 03 - Central | 18 | DIS-17-1 | Wind | 190 |  |  | ER | WERE | Marmaton - Litchfield 161 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-018 | 03 - Central | 18 | DIS-17-1 | Solar | 189 |  |  | ER/NR | SUNC | Thistle 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-022 | 03 - Central | 18 | DIS-17-1 | Solar | 65 |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-068 | 03 - Central | 18 | DIS-17-1 | Solar | 103.5 |  |  | ER/NR | WERE | Wichita 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-086 | 03 - Central | 18 | DIS-17-1 | Wind | 150 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-037 | 04 - Southeast | 18 | DIS-17-1 | Wind | 300 |  |  | ER | AEPW | Chisholm-Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-011 | 04 - Southeast | 18 | DIS-17-1 | Solar | 151.8 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-023 | 04 - Southeast | 18 | DIS-17-1 | Solar | 85 |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-027 | 04 - Southeast | 18 | DIS-17-1 | Wind | 140 |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-036 | 04 - Southeast | 18 | DIS-17-1 | Solar | 100 |  |  | ER | WFEC | Snyder - Cache 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-040 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200.1 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-057 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Hosston 69kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-061 | 04 - Southeast | 18 | DIS-17-1 | Solar | 101.5 |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-071 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-072 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | OKGE | Greenwood 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-073 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | GRDA | Dry Gulch 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-074 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  | ER | AEPW | Pryor Junction 138kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-075 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-076 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  | ER | AEPW | Chamber Springs 161kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-077 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-092 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-033 | 05 - Southwest | 18 | DIS-17-1 | Wind | 200 |  |  | ER/NR | AEPW | Oklaunion 345 kV sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2017-047 | 05 - Southwest | 18 | DIS-17-1 | Wind | 102 |  |  | ER/NR | SPS | Cole 115kV | IA PENDING
GEN-2017-100 | 05 - Southwest | 18 | DIS-17-1 | Solar | 102.6 |  |  | ER/NR | SPS | Texas County 115kV | IA FULLY EXECUTED/ON SCHEDULE
BEPCNDPW1 | 01 - North | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  | ER | BEPC-SPP | NELSON 7 | --
GEN-2016-036 | 01 - North | 17 | DIS-16-2 | Wind | 44.6 |  |  | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-087 | 01 - North | 17 | DIS-16-2 | Wind | 98.9 |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 - North | 17 | DIS-16-2 | Wind | 200 |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 - North | 17 | DIS-16-2 | Wind | 202 |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  |  | ER | NPPD | Sweetwater 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-147 | 02 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  |  | ER | NPPD | Sidney 115 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-111 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-115 | 03 - Central | 17 | DIS-16-2 | Wind | 300 |  |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 - Central | 17 | DIS-16-2 | Wind | 134 |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 - Central | 17 | DIS-16-2 | Battery | 20 |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-176 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-091 | 04 - Southeast | 17 | DIS-16-2 | Wind | 303.6 |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-095 | 04 - Southeast | 17 | DIS-16-2 | Wind | 200 |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-097 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-102 | 04 - Southeast | 17 | DIS-16-2 | Wind | 150.9 |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-118 | 04 - Southeast | 17 | DIS-16-2 | Wind | 288 |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-119 | 04 - Southeast | 17 | DIS-16-2 | Wind | 600 |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 - Southeast | 17 | DIS-16-2 | Wind | 172.5 |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-128 | 04 - Southeast | 17 | DIS-16-2 | Wind | 176 |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 - Southeast | 17 | DIS-16-2 | Wind | 2.5 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-132 | 04 - Southeast | 17 | DIS-16-2 | Wind | 6.12 |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-133 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-134 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-137 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-138 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-139 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-141 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-142 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-145 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-146 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  | ER | AEPW | Riverside 345kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-167 | 04 - Southeast | 17 | DIS-16-2 | Solar | 73.5 |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 - Southwest | 17 | DIS-16-2 | Wind | 90 |  |  | ER | SPS | TEXAS_CNTY 3 | --
GEN-2016-121 | 05 - Southwest | 17 | DIS-16-2 | Solar | 110 |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 - Southwest | 17 | DIS-16-2 | Gas Turbine | 17 |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2017-006GIA-53 | 03 - Central | 16.5 | Dis-16-2-PQ | Wind | 238 |  |  | ER/NR | AECI | 5MARYVL | --
GEN-2016-004 | 01 - North | 16 | DIS-16-1 | Wind | 202 |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-007 | 01 - North | 16 | DIS-16-1 | Wind | 100.05 |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-021 | 02 - Nebraska | 16 | DIS-16-1 | WIND | 300 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-043 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | NPPD | Axtell â€“ Post Rock 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-075 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-009 | 03 - Central | 16 | DIS-16-1 | Steam Turbine | 29 |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Central | 16 | DIS-16-1 | Wind | 78.2 |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 - Central | 16 | DIS-16-1 | Wind | 299 |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-073 | 03 - Central | 16 | DIS-16-1 | WIND | 220 |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-036 | 04 - Southeast | 16 | DIS-16-1 | Wind | 303.6 |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 - Southeast | 16 | DIS-16-1 | Wind | 176 |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 - Southeast | 16 | DIS-16-1 | Wind | 248.4 |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 04 - Southeast | 16 | DIS-16-1 | WIND | 150 |  |  | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 - Southeast | 16 | DIS-16-1 | Solar | 100 |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 - Southeast | 16 | DIS-16-1 | Wind | 1.5 |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 - Southeast | 16 | DIS-16-1 | Wind | 9.8 |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-057 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-061 | 04 - Southeast | 16 | DIS-16-1 | Wind | 250.7 |  |  | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200.1 |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-004 | 05 - Southwest | 16 | DIS-16-1 | Wind | 10 |  |  | ER | SPS | Palo Duro 115kV | --
GEN-2015-082 | 05 - Southwest | 16 | DIS-16-1 | Wind | 200 |  |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 - Southwest | 16 | DIS-16-1 | Wind | 5.3 |  |  | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-088 | 02 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 - Central | 15 | DIS-15-2 | Wind | 300 |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 04 - Southeast | 15 | DIS-15-2 | Battery | 20 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-055 | 04 - Southeast | 15 | DIS-15-2 | Solar | 40 |  |  | ER | WFEC | Erick 138kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-062 | 04 - Southeast | 15 | DIS-15-2 | Wind | 4.5 |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-066 | 04 - Southeast | 15 | DIS-15-2 | Wind | 248.4 |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  | ER/NR | XEL | Marshall 115kV | --
GEN-2007-020IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 16 |  |  | ER/NR | BEPC-SPP | Nelson 115kV | --
GEN-2008-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  | ER/NR | WAPA | Nelson 115kV | --
GEN-2010-003IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 34 |  |  | ER/NR | BEPC-SPP | Wessington Springs 230kV | --
MPC02100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 100 |  |  | ER | OTP | Center - Mandan 230 kV | --
GEN-2015-023 | 02 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 - Central | 14 | DIS-15-1 | Thermal | 6.13 |  |  | ER | SUNC | Ninnescah 115kV | --
GEN-2015-013 | 04 - Southeast | 14 | DIS-15-1 | Solar | 120 |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-032 | 02 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 - Central | 13 | DIS-14-2 | Wind | 2.42 |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 - Southwest | 13 | DIS-14-2 | Solar | 30 |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-004 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 - Central | 12 | DIS-14-1 | Wind | 200.6 |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 - Southeast | 12 | DIS-14-1 | Wind | 10.53 |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 - Southeast | 12 | DIS-14-1 | Wind | 5.67 |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 - Southwest | 11 | DIS-13-2 | Wind | 1.65 |  |  | ER | SPS | FE Clovis 115kV | --
GEN-2013-002 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Tucumcari 115kV | --
ASGI-2013-003 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  | ER | SPS | FE Clovis 115kV | --
ASGI-2012-002 | 05 - Southwest | 9 | DIS-12-2 | Wind | 18.15 |  |  | ER | SPS | FE-Clovis Interchange 115kV | --
NPPDBuffaloCountySolar | 02 - Nebraska | 8 | PQ | Solar | 10 |  |  | ER | NPPD | Kearney Northeast | --
NPPDBurtCountyWind | 02 - Nebraska | 8 | PQ | Wind | 20 |  |  | ER | NPPD | Tekamah & Oakland 115kV | --
ASGI-2012-006 | 03 - Central | 8 | DIS-12-1 | Steam | 22.5 |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV | --
ASGI-2010-006GIA-27 | 04 - Southeast | 8 | PQ | Wind | 150 |  |  | ER | AECI | Remington 138kV | --
GEN-2012-004 | 04 - Southeast | 8 | DIS-12-1 | Wind | 40.8 |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 - Southeast | 7 | DIS-11-2 | Wind | 6.6 |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 - Southeast | 6 | DIS-11-1 | Wind | 175 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 - Southeast | 6 | DIS-11-1 | Wind | 165.6 |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 - Southwest | 6 | DIS-11-1 | Wind | 299 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-014 | 05 - Southwest | 4 | DIS-10-1 | Wind | 358.8 |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 - Central | 3 | DIS-09-1 | Wind | 200.1 |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
01ALL | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
01ALL | ERIS | Thermal | 652437 GRNDFKS4 230 996740 GK KV1A _1 115 1 | 26WP | System Intact | 250 |  | 94.84 | 107.44 |  |  |  | Replace Grand Forks 230-115 kV Transformer
01ALL | ERIS | Thermal | None | 23SP, 26SP, 26L | None | [7 empty] | None
01ALL | ERIS | Voltage | None | N/A | None | [7 empty] | None
00NR | NRIS | Non-Converged | None | N/A | None | [7 empty] | None
00NR | NRIS | Thermal | None | N/A | None | [7 empty] | None
00NR | NRIS | Voltage | None | N/A | None | [7 empty] | None
01NR | NRIS | Non-Converged | None | N/A | None | [7 empty] | None
01NR | NRIS | Thermal | None | N/A | None | [7 empty] | None
01NR | NRIS | Voltage | None | N/A | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
MPC04300 | 01 - North | TBD | ERIS | Replace Grand Forks 230-115 kV Transformer | Current Study | Replace the Grand Forks 230-115 kV transformer to a minimum of 269 MVA | 7931000 | 100% | 7931000 | 7.763%
Total | [6 empty] | 7931000 |  | 7931000

## Upgrade Summary
Upgrade Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time (months) | Total Upgrade Cost
Current Study | 01 - North | MPC04300 | ERIS | Replace Grand Forks 230-115 kV Transformer | TBD | Replace the Grand Forks 230-115 kV transformer to a minimum of 269 MVA | WAPA | 36 | 7931000
7931000

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00NR | 0 | N/A | N/A | " | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | N/A | N/A | " | None |  |  |  |  | None
Non-Converge | 01NR | 0 | N/A | N/A | " | None |  |  |  |  | None
Thermal | 00NR | 1 | N/A | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 1 | 26WP | MPC04300 | FROM -> TO | 652437 GRNDFKS4 230 996740 GK KV1A _1 115 1 | 250 |  | 0.07763 | 107.44 | System Intact
Thermal | 01ALL | 1 | 26WP | MPC04300 | TO -> FROM | 652443 GRNDFKS7 115 996740 GK KV1A _1 115 1 | 250 |  | 0.07763 | 107.3 | System Intact
Thermal | 01NR | 1 | N/A | N/A | " | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 01NR | 2 | N/A | N/A | None | [7 empty] | None