## tblAllFacilityLog
STUDYDES | FacilityName | FacilityUpgradeCode | ModelArea1 | ModelArea2 | FZONENAME | TZONENAME | MONTFLAG | MONTFB | MONTFNAME | MONTTB1 | MONTTNAME1 | MONTTB2 | MONTTNAME2 | MONTCKT | Case | RATEA | RATEB | RATEC | Assessment Loading % | TransferCaseLoading % | NameOfBusWithMonitoredVoltage | Assessment Voltage | TransferCaseVoltage | VINIT | VMIN | VMAX | CATEGORY | CONTTYPE | CONTNAME | CONTXFMRFLAG | CONTFB | CONTFNAME | CONTTB1 | CONTTNAME1 | CONTTB2 | CONTTNAME2 | CONTCKT | TransmissionProviderCommentsNotes | RequiredRateB | TransmissionOwnerComments | OwnerDesignation | UpgradeName | UpgradeComponentWithinFacility | NewSummerA | NewSummerB | NewOtherA | NewOtherB | DistToConstruct | TotalLead | ConstructionLeadOnly | NewOrConstructWhileEnergized | NewR | NewX | NewB | CommentsRegardingUpgradeRequirements | NewCost | EffDate | NetPlantDate | ReusableEx_GrossValue | ReusableEx_NetValue | Reusable_EndofDepr | SalvageValue | NewCostWhileExpediting | EffDateExpedited | StartDeprExpedited | EndDeprExpedited | NetPlantDateExpedited | ReusableEx_GrossExpedited | ReusableEx_NetExpedited | Reusable_EndofDeprExpedited | SalvageValueExpedited | Generation 1 Owner & Unit (Name) | Generation 1 Redispatch Cost ($) | Generation 1 Redispatch Date (M/D/Y) | Generation 2 Owner & Unit (Name) | Generation 2 Redispatch Cost ($) | Generation 2 Redispatch Date (M/D/Y) | Generation 3 Owner & Unit (Name) | Generation 3 Redispatch Cost ($) | Generation 3 Redispatch Date (M/D/Y) | ActualCompletion | ActualNewCost | ActualNetPlantDate | ActualReusableEx_GrossValue | ActualReusableEx_NetValue | ActualReusable_EndofDepr | ActualSalvageValue | Actual_NewCostWhileExpediting | Actual_StartDeprExp | Actual_EndDeprExp | Actual_NetPlantDateExpedited | ActualReusableEx_GrossExpedited | ActualReusableEx_NetExpedited | ActualReusable_EndofDeprExpedited | Actual_SalvageValueExpedited | SPPReliabilityDate | DUN | EOC | EarliestDate
2006-AG1 | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | U | WERE | WERE |  |  | 0 | 533233 |  | 533243 |  | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WR | 166TH STREET - JAGGARD JUNCTION 115KV CKT 1 | Rebuild 166th Street - Jaggard Junction 115 kV line. | [53 empty] | 2010-02-03 | 2010-02-03
2024-AG2 | AES 5 - TARBY 5 - 1 | S | OKGE | OKGE |  |  | 0 | 515262 | AES 5 | 515264 | TARBY 5 | 0 |  | 1 | 26LP | 335 | 335 | 0 | 95.4013 | 107.2 | [6 empty] | CATEGORYB | SINGLE | BONANZT5 - AES 5 - 1 | 0 | 515261 | BONANZT5 | 515262 | AES 5 | 0 |  | 1 |  |  |  | OGE | AES Cogen & Tarby 115kV Terminal Upgrades | Upgrade various CT ratios, upgrade line switch and various jumpers at Tarby and AES Cogen. AEP CT coordination | [12 empty] | 1566485 | 2025-03-13 | [39 empty] | 2026-04-01 | 2026-12-01
2024-AG2 | AES 5 - TARBY 5 - 1 | S | OKGE | OKGE |  |  | 0 | 515262 | AES 5 | 515264 | TARBY 5 | 0 |  | 1 | 26LP | 335 | 335 | 0 | 95.3634 | 107.2 | [6 empty] | CATEGORYB | NONSINGLE | 271909 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OGE | AES Cogen & Tarby 115kV Terminal Upgrades | Upgrade various CT ratios, upgrade line switch and various jumpers at Tarby and AES Cogen. AEP CT coordination | [12 empty] | 1566485 | 2025-03-13 | [39 empty] | 2026-04-01 | 2026-12-01
2024-AG2 | AES 5 - TARBY 5 - 1 | S | OKGE | OKGE |  |  | 0 | 515262 | AES 5 | 515264 | TARBY 5 | 0 |  | 1 | 26LP | 335 | 335 | 0 | 95.3517 | 107.2 | [6 empty] | CATEGORYB | NONSINGLE | 266521 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OGE | AES Cogen & Tarby 115kV Terminal Upgrades | Upgrade various CT ratios, upgrade line switch and various jumpers at Tarby and AES Cogen. AEP CT coordination | [12 empty] | 1566485 | 2025-03-13 | [39 empty] | 2026-04-01 | 2026-12-01
2024-AG2 | AES 5 - TARBY 5 - 1 | S | OKGE | OKGE |  |  | 0 | 515262 | AES 5 | 515264 | TARBY 5 | 0 |  | 1 | 29LP | 335 | 335 | 0 | 95.2277 | 107 | [6 empty] | CATEGORYB | NONSINGLE | 266521 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OGE | AES Cogen & Tarby 115kV Terminal Upgrades | Upgrade various CT ratios, upgrade line switch and various jumpers at Tarby and AES Cogen. AEP CT coordination | [12 empty] | 1566485 | 2025-03-13 | [39 empty] | 2026-04-01 | 2026-12-01
2024-AG2 | AES 5 - TARBY 5 - 1 | S | OKGE | OKGE |  |  | 0 | 515262 | AES 5 | 515264 | TARBY 5 | 0 |  | 1 | 29LP | 335 | 335 | 0 | 95.2351 | 107 | [6 empty] | CATEGORYB | NONSINGLE | 271909 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OGE | AES Cogen & Tarby 115kV Terminal Upgrades | Upgrade various CT ratios, upgrade line switch and various jumpers at Tarby and AES Cogen. AEP CT coordination | [12 empty] | 1566485 | 2025-03-13 | [39 empty] | 2026-04-01 | 2026-12-01
2024-AG2 | AES 5 - TARBY 5 - 1 | S | OKGE | OKGE |  |  | 0 | 515262 | AES 5 | 515264 | TARBY 5 | 0 |  | 1 | 29LP | 335 | 335 | 0 | 95.2529 | 107 | [6 empty] | CATEGORYB | SINGLE | BONANZT5 - AES 5 - 1 | 0 | 515261 | BONANZT5 | 515262 | AES 5 | 0 |  | 1 |  |  |  | OGE | AES Cogen & Tarby 115kV Terminal Upgrades | Upgrade various CT ratios, upgrade line switch and various jumpers at Tarby and AES Cogen. AEP CT coordination | [12 empty] | 1566485 | 2025-03-13 | [39 empty] | 2026-04-01 | 2026-12-01
GI | ALBION - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640318 | PETRSBG7 115.00 | 640054 | ALBION 7 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Albion - Petersburg 115kV Ckt 1 Hansford Upgrade | Replace Breaker Switch 1106-D & jumpers; Replace Petersburg 115kV Substation main bus; Upgrade and replace transmission structures on 115kV lines TL1168 A & B to facilitate 100 degrees Centigrade line operation | [13 empty] | 2011-01-01 | [39 empty] | 2012-12-31 | 2012-12-31
2006-AG1 | ALUMAX TAP - BANN 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 508049 | ALUMXT 4 138 | 508054 | BANN 4 138 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | ALUMAX TAP - BANN 138KV CKT 1 | Replace six (6) 138 kV switches, five at Bann & one at Alumax Tap. Rebuild 0.67 miles of 1024 ACAR with 2156 ACSR. Replace wavetrap & jumpers @ Bann. Replace breaker 3300 @ Bann. | [53 empty] | 2008-06-01 | 2008-06-01
GI-DP | Ashdown REC (AECC delivery point) | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 507431 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | Ashdown REC (AECC delivery point) | Replace switches 6276 and 6277 with 3000 A, 138 kV switches and replace the conductor between them with 1590 ACSR. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507428 | OKAY 4 138.00 | 507402 | ASHDWNR4 138.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | ASHDOWN REC (MILLWOOD) - OKAY 138KV CKT 1 | Rebuild fourteen (14.3) miles of 115 kV line to 138 kV and reconductor with 1590 ACSR. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | U | AEPW | AEPW | SARKAECC | SARK | 0 | 507402 | ASHDWNR4 138.00 | 507431 | PATTERS4 138.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | ASHDOWN REC (MILLWOOD) - PATTERSON 138KV CKT 1 | Reconductor line and convert line to 138 kV. Convert Patterson station to breaker-and-a half configuration. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
2007-AG3 | BARBER - MEDICINE LODGE 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539673 | MED-LDG3 115.00 | 539760 | BARBER 3 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | BARBER - MEDICINE LODGE 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | BARBER - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539760 | BARBER 3 115.00 | 539649 | SAWYER 3 138 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | BARBER - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | BARBER (BARBER 4) 138/115/2.72KV TRANSFORMER CKT 1 | U | MKEC |  |  |  | 2 | 539674 | BARBER 4 138.00 | 539760 | BARBER 3 115.00 | 539917 | BARBER-T 2.7200 | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | MEDICINE LODGE 138/115KV TRANSFORMER CKT 1 | Upgrade transformer | [53 empty] | 2009-12-01 | 2013-06-01
2005-AG2 | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515473 | EXPGLNT4 | 515247 | BEELINE4 138 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | BEELINE - EXPLORER GLENPOOL 138KV CKT 1 | Reconductor .92miles of line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
2024-AG2 | BONANZT5 - AES 5 - 1 | S | OKGE | OKGE |  |  | 0 | 515262 | AES 5 | 515261 | BONANZT5 | 0 |  | 1 | 26LP | 335 | 335 | 0 | 95.5341 | 108.3 | [6 empty] | CATEGORYB | NONSINGLE | 272204 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OGE | AES Cogen & Tarby 115kV Terminal Upgrades | Upgrade various CT ratios, upgrade line switch and various jumpers at Tarby and AES Cogen. AEP CT coordination | [12 empty] | 1566485 | 2025-03-13 | [39 empty] | 2026-04-01 | 2026-12-01
2024-AG2 | BONANZT5 - AES 5 - 1 | S | OKGE | OKGE |  |  | 0 | 515262 | AES 5 | 515261 | BONANZT5 | 0 |  | 1 | 26LP | 335 | 335 | 0 | 95.5341 | 108.3 | [6 empty] | CATEGORYB | SINGLE | AES 5 - TARBY 5 - 1 | 0 | 515262 | AES 5 | 515264 | TARBY 5 | 0 |  | 1 |  |  |  | OGE | AES Cogen & Tarby 115kV Terminal Upgrades | Upgrade various CT ratios, upgrade line switch and various jumpers at Tarby and AES Cogen. AEP CT coordination | [12 empty] | 1566485 | 2025-03-13 | [39 empty] | 2026-04-01 | 2026-12-01
2024-AG2 | BONANZT5 - AES 5 - 1 | S | OKGE | OKGE |  |  | 0 | 515262 | AES 5 | 515261 | BONANZT5 | 0 |  | 1 | 29LP | 335 | 335 | 0 | 95.2018 | 107.2 | [6 empty] | CATEGORYB | SINGLE | AES 5 - TARBY 5 - 1 | 0 | 515262 | AES 5 | 515264 | TARBY 5 | 0 |  | 1 |  |  |  | OGE | AES Cogen & Tarby 115kV Terminal Upgrades | Upgrade various CT ratios, upgrade line switch and various jumpers at Tarby and AES Cogen. AEP CT coordination | [12 empty] | 1566485 | 2025-03-13 | [39 empty] | 2026-04-01 | 2026-12-01
2024-AG2 | BONANZT5 - AES 5 - 1 | S | OKGE | OKGE |  |  | 0 | 515262 | AES 5 | 515261 | BONANZT5 | 0 |  | 1 | 29LP | 335 | 335 | 0 | 95.2018 | 107.2 | [6 empty] | CATEGORYB | NONSINGLE | 272204 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OGE | AES Cogen & Tarby 115kV Terminal Upgrades | Upgrade various CT ratios, upgrade line switch and various jumpers at Tarby and AES Cogen. AEP CT coordination | [12 empty] | 1566485 | 2025-03-13 | [39 empty] | 2026-04-01 | 2026-12-01
GI | Border 345 kV Capacitive Reactive Support (OKGE) | U | OKGE | SPS |  |  | 0 | 515458 | BORDER 7 | 525832 | TUCO_INT 7 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | Border 345 kV Capacitive Reactive Support (OKGE) | Install +275 Mvar Capacitor Bank(s) at Border 345kV | [53 empty] | 2020-06-01 | 2020-06-01
2005-AG2 | BROWN - STRAIGHT ROAD TAP 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515157 | BROWN 4 138 | 515944 | STRRDTP4 138.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | BROWN - STRAIGHT ROAD TAP 138KV CKT 1 | Upgrade CT at Brown. | [53 empty] | 2006-06-01 | 2006-06-01
2005-AG2 | CACHE - SNYDER 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 511500 | CACHETP4 | 588779 | TAP_G17-036 | 0 |  | 2 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | CACHE - SNYDER 138KV CKT 1 | Replace Snyder wavetrap | [53 empty] | 2008-05-21 | 2008-05-21
GI | Cleo Corner - Cleo Plant Tap 138kV Ckt 1 | U | OKGE | OKGE |  |  | 0 | 514778 | CLEOCOR4 | 515562 | CLEOPLT4 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | Cleo Corner - Cleo Plant Tap 138kV Ckt 1 | Construct four (4) 2000 continuous ampacity breakers, control panel replacement, line relaying, disconect switches, structures, foundations, conductors, insulators, and all other associated work and materials. Reroute transmission line to the south to ope | [53 empty] | 2020-10-01 | 2020-10-01
2007-AG3 | CLIFTON - GREENLEAF 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539656 | CLIFTON3 115.00 | 539665 | GRNLEAF3 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | CLIFTON - GREENLEAF 115KV CKT 1 | Rebuild 14.4 miles | [53 empty] | 2011-06-01 | 2013-06-01
GI | COUNTY LINE - BATTLE CREEK 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640115 | CO.LINE7 | 640072 | BATTLCRK7 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Battle Creek - County Line 115kV Rebuild | Rebuild/Upgrade the Battle Creek – County Line 115kV to rerate line segments to greater than 125 MVA. | [53 empty] | 2017-05-01 | 2017-05-01
GI | Crossroads - Eddy County 345 kV CKT 1 Rebuild | U | SPS | SPS |  |  | 0 | 527656 | CROSSROADS | 527802 | EDDY_CNTY | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Crossroads - Eddy County 345 kV CKT 1 Rebuild | Replace 2 x 345 kV structures, wave traps (3x), and jumpers to achieve minimum emergency rating of 956 MVA | [53 empty] | 2020-12-01 | 2020-12-01
GI | Crossroads - Tolk 345 kV CKT 1 Rebuild | U | SPS | SPS |  |  | 0 | 527656 | CROSSROADS | 525549 | TOLK | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Crossroads - Tolk 345 kV CKT 1 Rebuild | Replace approximately 4 structures on the Crossroads-Tolk 345 kV line to achieve a minimum rating of 956 MVA | [53 empty] | 2020-12-01 | 2020-12-01
GI | Crossroads 345 kV Capacitive Reactive Support (SPS) | U | SPS | SPS |  |  | 0 | 527656 | CROSSROADS | 525549 | TOLK | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Crossroads 345 kV Capacitive Reactive Support (SPS) | Install +100 Mvar Capacitor Bank(s) at Crossroad 345 kV | [53 empty] | 2021-12-01 | 2021-12-01
GI | CURRY3 - DEAF SMITH TAP20 CKT1 | U | SPS | SPS |  |  | 0 | 524822 | CURRY 3 | 524668 | DS-#20 +3 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | CURRY3 - DEAF SMITH TAP20 CKT1 | Rebuild line to achieve minimum normal/emergency rating of 90/90 MVA | [53 empty] | 2021-12-01 | 2021-12-01
GI | Deaf Smith - Plant X 230 kV Rebuild | U | SPS | SPS |  |  | 0 | 525481 | PLANT_X 6230.00 | 524623 | DEAFSMITH | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Deaf Smith - Plant X 230 kV Rebuild | Rebuild line to achieve minimum system emergency rating of 430 MVA | [53 empty] | 2020-12-01 | 2020-12-01
GI | Deaf Smith 115 kV Capacitive Reactive Power Support | U | SPS | SPS |  |  | 0 | 525481 | PLANT_X 6230.00 | 524623 | DEAFSMITH | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Deaf Smith 115 kV Capacitive Reactive Power Support | Build 100 MVar at Deaf Smith 115 kVSubstation | [53 empty] | 2021-10-28 | 2021-10-28
GI | DEAF SMITH TAP20 - DEAF SMITH 20 CKT1 | U | SPS | SPS |  |  | 0 | 524668 | DS-#20 +3 | 524669 | DS-#20 3 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | DEAF SMITH TAP20 - DEAF SMITH 20 CKT1 | Rebuild line to achieve minimum normal/emergency rating of 90/90 MVA | [53 empty] | 2021-12-01 | 2021-12-01
2007-AG3 | DEARING 138KV | U | WERE |  | SEAST |  |  | 533002 | DEARING4 138.00 | [18 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WR | DEARING 138KV | Dearing 138 kV 20 MVAR Capacitor Addition | [53 empty] | 2012-06-01 | 2012-06-01
GI | DICKINSON 230/115/13.8kV CKT 2 | U | WAPA | MDU |  |  | 1 | 659124 | DICKNSN4 230.00 | 659125 | DKSN-NK7 115.00 | 659197 | DK.KW1A_-BE913.800 | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | BEPM | DICKINSON 230/115/13.8KV CKT 2 | Build new 230/115/13.8kV Transformer circuit #2 at Dickinson. | [53 empty] | 2019-03-01 | 2019-03-01
GI | Dover - Henessey 138kV CKT 1 | U | WFEC | WFEC |  |  | 0 | 520881 | DOVERSW2 | 520940 | HENESEY2 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | Dover - Henessey 138kV CKT 1 | Upgrade terminal equipment from 800A CT to 1200A CT | [53 empty] | 2019-03-06 | 2019-03-06
GI | DRY CREEK - RAPID CITY 115 KV CKT 1 | U | WAPA | WAPA |  |  | 0 | 652490 | RAPIDCY7 115.00 | 659377 | DRYCREEK-BE7115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WAPA | DRY CREEK - RAPID CITY 115 KV CKT 1 | Replace thirty-five (35) 115 kV transmission structures. Replace the 115 kV strain bus, circuit switchers, and jumpers at Newell. Reset relays. Replace the main and transfer 115 kV buses of Rapid City substation, transfer bay, and transmission line bay | [53 empty] | 2020-02-28 | 2020-02-28
GI | ELK CREEK - NEWELL 115 KV CKT 1 | U | WAPA | WAPA |  |  | 0 | 652483 | NEWELL 7 115.00 | 652473 | ELKCRK 7 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WAPA | ELK CREEK - NEWELL 115 KV CKT 1 | Replace thirty-five (35) 115 kV transmission structures. Replace the 115 kV strain bus, circuit switchers, and jumpers at Newell. Reset relays. Replace the main and transfer 115 kV buses of Rapid City substation, transfer bay, and transmission line bay | [53 empty] | 2020-02-28 | 2020-02-28
GI | ELK CREEK - RAPID CITY 115 KV CKT 1 | U | WAPA | WAPA |  |  | 0 | 652473 | ELKCRK 7 115.00 | 652490 | RAPIDCY7 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WAPA | ELK CREEK - RAPID CITY 115 KV CKT 1 | Replace thirty-five (35) 115 kV transmission structures. Replace the 115 kV strain bus, circuit switchers, and jumpers at Newell. Reset relays. Replace the main and transfer 115 kV buses of Rapid City substation, transfer bay, and transmission line bay | [53 empty] | 2020-02-28 | 2020-02-28
2005-AG2 | EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 AEPW | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515473 | EXPGLNT4 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 (AEP) | Reconductor 1.82 miles with ACCC. Replace wave trap jumpers at Riverside. | [53 empty] | 2009-03-23 | 2009-03-23
2005-AG2 | EXPLORER GLENPOOL TAP - RIVERSIDE STATION 138KV CKT 1 OKGE | U | AEPW | OKGE |  |  | 0 | 509783 | R.S.S.-4 138 | 515473 | EXPGLNT4 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | EXPLORER GLENPOOL - RIVERSIDE STATION 138KV CKT 1 (OGE) | Reconductor 1.82 miles line with Drake ACCC/TW. | [53 empty] | 2009-06-01 | 2009-06-01
GI | Fairfax - Pawnee 138kV Ckt 1 | U |  |  |  |  | 0 | 300139 |  | 512749 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | GRDA | FAIRFAX - PAWNEE 138KV CKT 1 | Construct Approx. 15 miles of 138kV transmission line from Fairfax to a new substation on the Cleveland-Stillwater 138kV line near Pawnee. & Fairfax Substation: Install 138kV line terminal and any additional modifications that are necessary to connect to | [13 empty] | 2011-06-15 | [39 empty] | 2014-06-30 | 2014-06-30
2007-AG3 | FLATRDG3 138.00 - MEDICINE LODGE 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539674 | MED-LDG4 138.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | FLATRDG3 - MEDICINE LODGE 138KV CKT 1 | Rebuild 8.05 mile line | [53 empty] | 2009-12-01 | 2013-06-01
2007-AG3 | FLATRDG3 138.00 - HARPER 138KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539638 | FLATRDG3 138.00 | 539668 | HARPER 4 138.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | FLATRDG3 - HARPER 138KV CKT 1 | Rebuild 24.15 mile line |  | 286 |  |  | 24.15 | 24 | 24 | [46 empty] | 2009-12-01 | 2013-06-01
GI | Fort Randall - Madison County 230kV Ckt 1 | U |  |  |  |  | 0 | 640540 |  | 652509 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Fort Randall - Madison County 230kV Ckt 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320 MVA | [53 empty] | 2014-10-01 | 2014-10-01
2006-AG1 | FT SUPPLY 138/69KV TRANSFORMER CKT 1 | U | WFEC | WFEC |  |  | 1 | 520920 | FTSUPLY4 138 | 520919 | FTSUPLY269.0 | 521182 |  | 2 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | FT SUPPLY 138/69KV TRANSFORMER CKT 2 | Install 2nd 70 MVA auto at Ft Supply | [53 empty] | 2006-12-01 | 2008-06-01
GI | Ft. Dodge - North Ft. Dodge 115 kV Ckt 2 | U | MKEC | MKEC |  |  | 0 | 539671 |  | 539771 |  |  |  | 2 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | Ft. Dodge - North Ft. Dodge 115 kV Ckt 2 | Build appoximately 0.5 mile 115 kV line | [53 empty] | 2015-05-01 | 2015-05-01
GI | KINGFISHER CO TAP - MATHEWSON 345kV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515875 | REDNGTN7 345.00 | 515497 | MATHWSON7 345.00 |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | Kingfisher Co Tap - Mathewson 345kV CKT 1 | Replace terminal equipment to achieve conductor limit | [53 empty] | 2018-03-01 | 2018-03-01
GI | GRACMNT4 138.00 - WASHITA 138KV CKT 2 OKGE | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | Gracemont 138kV line terminal addition | 138kV line terminal at Gracemont substation, including breaker, line relaying, disconnect switches and associated equipment, dead end structures, revenue metering with CT's and PT's. | [13 empty] | 2010-11-20 | [39 empty] | 2012-10-12 | 2012-10-12
GI | GRACMNT4 138.00 - WASHITA 138KV CKT 2 WFEC | U | WFEC | OKGE | AEP-CS | ARDMORE | 0 | 521089 | WASHITA4 138.00 | 515802 | GRACMNT4 138.00 | 0 |  | 2 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WFEC | WASHITA - GRACEMONT 138 KV CKT 2 | BUILD WASHITA - GRACEMONT 138KV CKT 2 (APPROXIMATELY 7 MILES). ADD LINE TERMINAL AT WASHITA AND PROCURE RIGHT OF WAY. REQUIRED AS SHARED NETWORK UPGRADE FOR INTERCONNECTION OF GEN-2008-037. | [13 empty] | 2010-11-20 | [39 empty] | 2012-10-12 | 2012-10-12
2008-AGP1 | GREENLEAF - KNOB HILL 115KV CKT 1 | U | SUNC | WERE |  | NCENTRAL | 0 | 539665 | GRNLEAF3 115.00 | 533332 | KNOB HL3 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | GREENLEAF - KNOB HILL 115KV CKT 1 (MKEC) | Rebuild 43.5% Ownership of 20.9 miles | [53 empty] | 2013-06-01 | 2013-06-01
GI | Harrington Mid - Nichols 230 kV Ckt 2 | U | SPS | SPS |  |  | 0 | 523978 |  | 524044 |  |  |  | 2 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Harrington Mid - Nichols 230 kV Ckt 2 | Reconductor Harrington Mid - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | [13 empty] | 2011-10-01 | [39 empty] | 2012-12-01 | 2012-12-01
GI | Harrington West - Nichols 230kV Ckt 1 | U | SPS | SPS |  |  | 0 | 523977 |  | 524044 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Harrington West - Nichols 230kV Ckt 1 | Reconductor Harrington West - Nichols 230kV. Replace switches and breakers to get circuit to 727/727 MVA rating. New limit should be bus rating. | [13 empty] | 2011-10-01 | [39 empty] | 2012-12-01 | 2012-12-01
GI | Hoskins - Dixon County 230kV Line Upgrade | U | NPPD | NPPD |  |  | 0 | 640560 | WAKEFIELD 4 | 640227 | HOSKINS4 |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Hoskins - Dixon County 230kV Line Upgrade | Increase clearances to accommodate 320MVA facility rating to address loading issues | [53 empty] | 2015-10-24 | 2015-10-24
2005-AG2 | HUGO POWER PLANT - VALLIANT 138KV CKT 1 | U | WFEC | AEPW |  |  | 0 | 521157 | HUGO PP4 138 | 510911 | VALIANT4 138 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | ITCM | HUGO - VALLIANT 345KV CKT 1 | New 19 miles 345 KV | [53 empty] | 2012-07-01 | 2012-07-01
2005-AG2 | HUGO POWER PLANT 345/138KV TRANSFORMER CKT 1 | U | WFEC | AEPW |  |  | 1 | 521157 | HUGO PP4 138 | 520560 | HUGO PP4 138.00 | 521189 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | ITCM | HUGO 345/138KV TRANSFORMER CKT 1 | New 345/138 kv Auto | [53 empty] | 2012-07-01 | 2012-07-01
2006-AG1 | JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | U | WERE | WERE |  |  | 0 | 533243 |  | 533261 |  | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WR | JAGGARD JUNCTION - PENTAGON 115KV CKT 1 | Rebuild Jaggard Junction - Pentagon 115 kV line. | [53 empty] | 2010-05-13 | 2010-05-13
2006-AG1 | JARBALO JUNCTION SWITCHING STATION - 166TH STREET 115KV CKT 1 | U | WERE | WERE |  |  | 0 | 533244 |  | 533233 |  | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WR | 166TH STREET - JARBALO JUNCTION SWITCHING STATION 115KV CKT 1 | Rebuild Jarbalo - 166th Street 115 kV line. | [53 empty] | 2010-09-18 | 2010-09-18
2008-AGP1 | KCI - Platte City 161kV Ckt 1 | U | KCPL | KCPL |  |  | 0 | 541221 |  | 541212 |  | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KCPL | KCI - Platte City 161kV Ckt 1 | Replace 800 amp wavetrap at KCI | [53 empty] | 2010-08-31 | 2010-08-31
GEN | KELLY - MADISONCO 230.00 230KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640540 | MADISONCO 230.00 | 640133 | COLMBUS4 230.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Kelly - Madison County 230kV Ckt 1 | Raise structures and line clearances as necessary to re-rate the transmission line to 320MVA |  | 320 |  |  |  | 24 | 24 | [5 empty] | 480000 | 2011-01-01 | [39 empty] | 2014-11-01 | 2014-11-01
2006-AG1 | KNOBHILL (KNOBHIL4) 138/69/13.2KV TRANSFORMER CKT 1 | U | OKGE |  |  |  | 1 | 514795 | KNOBHIL4 138 | 514794 | KNOBHIL269.0 | 515732 | KNOBHIL113.2 | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | KNOBHILL 138/69KV TRANSFORMER CKT 1 | Replace bus tie with 100MVA transformer | [53 empty] | 2006-06-01 | 2008-06-01
NA | LACYGNE - WEST GARDNER 345KV CKT 1 | U | KACP | KACP |  |  | 0 | 542981 | LACYGNE7 | 542965 | W.GRDNR7 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | KCPL | LACYGNE - WEST GARDNER 345KV CKT 1 | KCPL Sponsored Project to Reconductor Line to be In-Service by 6/1/2006 | [53 empty] | 2006-06-01 | 2006-06-01
2019-AG2 | Locust Grove - Kerr 115 kV Rebuild | U | AEPW | GRDA |  |  | 0 | 510423 | L GROVE3 115.00 | 512634 | KERR GR3 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | Locust Grove - Kerr 115 kV Rebuild | Rebuild 0.47 miles of 115 kV line from Kerr - Locust Grove | [13 empty] | 2020-04-30 | [39 empty] | 2022-06-01 | 2022-12-01
GEN-2006-010 | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 508105 | MANDEVILTP4 | 508078 | SETEXAR4 138.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | MANDEVILTP4 - SE TEXARKANA 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
GEN-2006-010 | MANDEVILTP4 - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | TURK 4 138.00 | 508105 | MANDEVILTP4 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | MANDEVILTP4 - TURK 138KV CKT 1 | Build new Turk-SE Texarkana 138 kV line and add SE Texarkana 138 kV terminal. | [53 empty] | 2012-07-01 | 2012-07-01
NA | MATHEWSON - NORTHWEST 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 514880 |  | 515497 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | MATHEWSON - NORTHWEST 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
NA | MATHEWSON - TATONGA 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515497 |  | 515407 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | MATHEWSON - TATONGA 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
GI | MAURINE - SULPHUR 115 KV CKT 1 | U | WAPA | WAPA |  |  | 0 | 652491 | SULPHUR | 652480 | MAURINE7 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WAPA | MAURINE - SULPHUR 115 KV CKT 1 | Replace thirty-five (35) 115 kV transmission structures. Replace the 115 kV strain bus, circuit switchers, and jumpers at Newell. Reset relays. Replace the main and transfer 115 kV buses of Rapid City substation, transfer bay, and transmission line bay | [53 empty] | 2020-02-28 | 2020-02-28
GI | MCNAB REC - TURK 115KV CKT 1 | U | AEPW | AEPW | SARK | SARKAECC | 0 | 507456 | HEMPSTD3 115.00 | 504122 | MCNAB 3 115.00 |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | MCNAB REC - Turk 115KV CKT 1 #2 (AEP) | Build a new two mile, 138kV, 1590 ACSR line section (operated at 115kV) from Turk Substation to the existing Okay-Hope 115kV line to form a Turk - Hope 115kV line. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
2024-AG2 | MIDWEST4 - FRNKLNS4 - 1 | S | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 34SP | 268 | 308 | 0 | 99.4136 | 107.3 | [6 empty] | CATEGORYB | NONSINGLE | 272093 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OGE | Reconductor Midwest - Franklin 138kV Line | Rebuild 1.3 miles of 138kV to 2000A 478MVA SN/SE/WN/WE | [12 empty] | 2000000 | 2025-03-13 | [39 empty] | 2034-06-01 | 2027-06-01
2024-AG2 | MIDWEST4 - FRNKLNS4 - 1 | S | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 34SP | 268 | 308 | 0 | 99.4136 | 107.3 | [6 empty] | CATEGORYB | NONSINGLE | 283515 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OGE | Reconductor Midwest - Franklin 138kV Line | Rebuild 1.3 miles of 138kV to 2000A 478MVA SN/SE/WN/WE | [12 empty] | 2000000 | 2025-03-13 | [39 empty] | 2034-06-01 | 2027-06-01
2024-AG2 | MIDWEST4 - FRNKLNS4 - 1 | S | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 34SP | 268 | 308 | 0 | 98.127 | 105.9 | [6 empty] | CATEGORYB | NONSINGLE | 273070 | 0 | 0 |  | 0 |  | 0 | [5 empty] | OGE | Reconductor Midwest - Franklin 138kV Line | Rebuild 1.3 miles of 138kV to 2000A 478MVA SN/SE/WN/WE | [12 empty] | 2000000 | 2025-03-13 | [39 empty] | 2034-06-01 | 2027-06-01
2024-AG2 | MIDWEST4 - FRNKLNS4 - 1 | S | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 34SP | 268 | 308 | 0 | 96.7471 | 104.5 | [6 empty] | CATEGORYB | SINGLE | MINCO 7 - GRACMNT7 - 1 | 0 | 514801 | MINCO 7 | 515800 | GRACMNT7 | 0 |  | 1 |  |  |  | OGE | Reconductor Midwest - Franklin 138kV Line | Rebuild 1.3 miles of 138kV to 2000A 478MVA SN/SE/WN/WE | [12 empty] | 2000000 | 2025-03-13 | [39 empty] | 2034-06-01 | 2027-06-01
2024-AG2 | MIDWEST4 - FRNKLNS4 - 1 | S | OKGE | WFEC |  |  | 0 | 514946 | MIDWEST4 | 520917 | FRNKLNS4 | 0 |  | 1 | 34SP | 268 | 308 | 0 | 94.0396 | 100.4 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | 0 | 0 |  | 0 |  | 0 | [5 empty] | OGE | Reconductor Midwest - Franklin 138kV Line | Rebuild 1.3 miles of 138kV to 2000A 478MVA SN/SE/WN/WE | [12 empty] | 2000000 | 2025-03-13 | [39 empty] | 2034-06-01 | 2027-06-01
2024-AG2 | MINGO-N4 - 21STTAP4 - 1 | S | AEPW | AEPW |  |  | 0 | 509828 | 21STTAP4 | 509760 | MINGO-N4 | 0 |  | 1 | 34SP | 221 | 221 | 0 | 96.412 | 104.9 | [6 empty] | CATEGORYB | SINGLE | BA.N-ST4 - E 11TH ST 4 - 1 | 0 | 509786 | BA.N-ST4 | 509804 | E 11TH ST 4 | 0 |  | 1 |  |  |  | AEP | Reconductor 21St Tap - Mingo North 138kV | Reconductor 0.64 mile of 138 kV conductor and replace double-circuit towers | [12 empty] | 4500000 | 2025-03-13 | [39 empty] | 2034-06-01 | 2028-06-01
GI | NELIGH - PETERSBURG 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640444 |  | 640293 | NELIGH 7 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Neligh - Petersburg North 115kV Ckt 1 | Replace Breaker 1106, jumpers, & 115kV Switch 1106-D2; Replace Petersburg 115kV Substation main bus; Upgrade and replace transmission structures on 115kV lines TL1168 A & B to facilitate 100 degrees Centigrade line operation | [13 empty] | 2011-01-01 | [39 empty] | 2012-12-31 | 2012-12-31
GI | NELIGH EAST - COUNTY LINE 115KV CKT 1 | U | NPPD | NPPD | NPPD_686 | NPPD_686 | 0 | 640521 | NELIGH.EAST7 | 640115 | CO.LINE7 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Antelope - County Line - 115kV Rebuild | Rebuild/Upgrade the Antelope ΓÇô County Line 115kV to rerate line segments to greater than 125 MVA. | [53 empty] | 2017-05-01 | 2017-05-01
2019-AG1 | Neosho - Riverton 161kV Line Rebuild (EMDE) | U | EMDE | WERE |  |  | 0 | 532937 | NEOSHO 5 161.00 | 547469 | RIV4525 161.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | EDE | Neosho - Riverton 161kV Line Rebuild (EMDE) | Rebuild 28.41 miles of 161kV line from Neosho to Riverton and upgrade any necessary terminal equipment | [13 empty] | 2023-10-01 | [39 empty] | 2023-10-01 | 2023-10-01
2019-AG1 | Neosho - Riverton 161kV Line Rebuild (WERE) | U | EMDE | WERE |  |  | 0 | 532937 | NEOSHO 5 161.00 | 547469 | RIV4525 161.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WR | Neosho - Riverton 161kV Line Rebuild (WERE) | Rebuild 2.44 miles of Neosho-Riverton 161kV line using bundled 1590 Lapwing ACSR and OPGW. Remove the wavetrap. | [13 empty] | 2023-10-01 | [39 empty] | 2023-10-01 | 2023-10-01
GI | Newhart - Plant X 230 kV CKT 1 Rebuild | U | SPS | SPS |  |  | 0 | 525481 | PLANT_X 6230.00 | 525461 | NEWHART | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Newhart - Plant X 230 kV CKT 1 Rebuild | Rebuild line to achieve minimum system intact/emergency rating of 456 MVA | [53 empty] | 2020-12-31 | 2020-12-31
GI | North Ft. Dodge - Spearville 115 kV Ckt 2 | U | MKEC | MKEC |  |  | 0 | 539771 |  | 539759 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | North Ft. Dodge - Spearville 115kV Ckt 2 | Build appoximately 20 mile 115 kV line | [53 empty] | 2015-05-01 | 2015-05-01
GI | OKAY - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | SARK | 0 | 507454 | HEMPSTD4 138.00 | 507428 | OKAY 4 138.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | OKAY - TURK 138KV CKT 1 | Build a new two mile, 138kV, 1590 ACSR line section from Turk Substation to the existing Okay-Hope 115kV line and rebuild twelve miles of 115kV line to Okay Substation to 138kV, 1590 ACSR, to form a Turk - Okay 138kV line. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | OKAY 138/69KV TRANSFORMER CKT 1 | U | AEPW | AEPW | SARK | SARK | 1 | 507428 | OKAY 4 138.00 | 507427 | OKAY 2 69.000 | 507442 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | OKAY 138/69KV TRANSFORMER CKT 1 | Replace three single-phase 115-69kV autotransformers with one 90 MVA, three-phase 138-69kV autotransformer and convert high side of station to 138kV. | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | Oklaunion 345 kV Capacitive Reactive Support (AEP) | U | SPS | AEPW |  |  | 0 | 525832 | TUCO_INT 7 | 511584 | O.K.U.2-7 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | Oklaunion 345 kV Capacitive Reactive Support (AEP) | Install +200 Mvar Capacitor Bank(s) at Oklaunion 345kV | [53 empty] | 2022-06-01 | 2022-06-01
GI | Osage - Shidler 138kV | U |  |  |  |  | 0 | 301369 |  | 510403 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | Osage - Shidler 138kV | Osage Substation:Replace Shidler 138kV line terminal primary and redundant relaying with SEL uProcessor based relays, install 3-138kV PTs, Install 1-138kV CB, Install metering, Install 2000A line Trap | [13 empty] | 2012-01-15 | [39 empty] | 2014-01-15 | 2014-01-15
GI | Pawnee 138 kV | U |  |  |  |  | 0 | 300139 |  | 512749 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | GRDA | Pawnee 138 kV | New three breaker ring bus on the Cleveland-Stillwater 138kV line near Pawnee. Station will have terminals to Cleveland, Stillwater, and Fairfax. | [13 empty] | 2011-06-15 | [39 empty] | 2014-06-30 | 2014-06-30
GI | RENFROW - RENFROW TAP 138KV | U | OKGE | WFEC |  |  | 0 | 515544 | RENFROW4 138.00 | 520409 | RENFROW4 138.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | Renfrow-Renfrow Tap 138kV Ckt 1 | Replace terminal equipment. | [53 empty] | 2017-09-25 | 2017-09-25
GI | Rice - Circle 230 kV Ckt 1 (MIDW portion) | U | WERE | MIDW |  |  | 0 | 530686 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Circle 230 kV Ckt 1 (MIDW portion) | ALL WORK REQUIRED TO CONVERT RICE - CIRCLE 115KV TO 230KV OPERATION. INCLUDES NEW 230KV 3 BREAKER RING BUS, AN EXTENSION OF THE 230KV FROM CURRENT RICE STATION TO NEW RICE SUBSTATION, AND ANY ADDITIONAL WORK REQUIRED FOR THE CONVERSION. | [13 empty] | 2011-12-27 | [39 empty] | 2012-11-07 | 2012-11-07
GI | Rice - Circle 230 kV Ckt 1 (WR portion) | U | WERE | MIDW |  |  | 0 | 530686 | RICECO 230.00 | 532871 | CIRCLE 6 230.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WR | Rice - Circle 230 kV Ckt 1 (WR portion) | Install necessary equipment and perform line work at Circle substation to accommodate new bus position. | [13 empty] | 2012-01-15 | [39 empty] | 2012-11-29 | 2012-11-29
GI | Rice - Lyons 115 kV Ckt 1 | U | MIDW | WERE |  |  | 0 | 530623 | RICE 3 115.00 | 530620 | LYONS 3 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice - Lyons 115 kV Ckt 1 | Rebuild and extend 115 kV transmission line from existing Rice Co. substation to new Rice Co. substation, including engineering, surveying, and modification of existing easements as required. | [13 empty] | 2011-12-27 | [39 empty] | 2013-04-01 | 2013-04-01
GI | Rice County 230/115 kV transformer Ckt 1 | U | MIDW | MIDW |  |  | 1 | 530686 | RICECO 230.00 | 530623 | RICE 3 115.00 | 530687 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MIDW | Rice County 230/115 kV transformer Ckt 1 | Install 230/115 kV transformer at Rice County. | [13 empty] | 2011-12-27 | [39 empty] | 2012-10-01 | 2012-10-01
2007-AG3 | RIVER ROAD - SAWYER 115KV CKT 1 | U | MKEC | MKEC |  |  | 0 | 539649 | SAWYER 3 115.00 | 539651 | RVROAD 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | RIVER ROAD - SAWYER 115KV CKT 1 | Rebuild line | [53 empty] | 2009-12-01 | 2013-06-01
GI | Shidler 138 kV | U |  |  |  |  | 0 | 301369 |  | 510403 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | Shidler 138 kV | Replace existing 138kV CB at Shidler substation with 4 breaker ring. Provide Terminal for KAMO's 138kV line from Remington Station. Replace ground switch and circuit switcher, Move terminal for OG&E Osage 138kV line. Replace relay panels for OGE Osage and AEP Mound Road line terminals. Install 138kV meter transformers and meter at Shidler station. Install relay panel, line trap and RTU at Mound Road station for line to Shidler station. | [13 empty] | 2011-07-28 | [39 empty] | 2014-02-08 | 2014-02-08
GI | Spearville 345/115 kV Transfomer CKT 1 | U | MKEC | MKEC |  |  | 1 | 539759 |  | 531469 |  | 539960 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | MKEC | Spearville 345/115 kV Transformer CKT 1 | Spearville Substation - Add 345/115kV autotransformer and 345kV and 115kV terminal positions for autotransformer. Needed as Network Upgrade for GEN-2008-079 but cost shared with GEN-2006-006. - Update! GEN-2006-006 withdrawn, sole cost to GEN-2008-079. | [53 empty] | 2015-05-01 | 2015-05-01
2005-AG2 | STRAIGHT ROAD TAP - EXPLORER TAP 138KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515944 | STRRDTP4 138.00 | 515153 | COLEMNT4 138 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | STRAIGHT ROAD TAP - EXPLORER TAP 138KV CKT 1 | Upgrade terminal equipment. | [53 empty] | 2006-06-01 | 2006-06-01
2005-AG2 | SUB 110 - ORONOGO JCT. - SUB 167 - RIVERTON 161KV CKT 1 | U | EMDE | EMDE |  |  | 0 | 547469 | RIV167 5 161 | 547467 | ORO110 5 161 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | EDE | SUB 110 - ORONOGO JCT. - SUB 452 - RIVERTON 161KV CKT 1 | Reconductor Oronogo 59467 to Riverton 59469 with Bundled 556 ACSR | [53 empty] | 2011-06-01 | 2011-06-01
GI | SUGAR HILL - TURK 138KV CKT 1 | U | AEPW | AEPW | SARK | TEXARK | 0 | 507454 | HEMPSTD4 138.00 | 508080 | SUGARHL4 138.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | SUGAR HILL - TURK 138KV CKT 1 | Build new 24 mile Turk - Sugar Hill 138 kV line and add Sugar Hill 138 kV terminal. | [13 empty] | 2007-10-01 | [39 empty] | 2010-12-16 | 2010-12-16
GI | SULPHUR - NEWELL 115 KV CKT 1 | U | WAPA | WAPA |  |  | 0 | 652491 | SULPHUR | 652483 | NEWELL 7 115.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | WAPA | SULPHUR - NEWELL 115 KV CKT 1 | Replace thirty-five (35) 115 kV transmission structures. Replace the 115 kV strain bus, circuit switchers, and jumpers at Newell. Reset relays. Replace the main and transfer 115 kV buses of Rapid City substation, transfer bay, and transmission line bay | [53 empty] | 2020-02-28 | 2020-02-28
GI | Sunnyside to tap on Pooleville - Ratliff 138kV Ckt 1 | U |  |  |  |  | 0 | 515561 |  | 515135 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | Carter County - Sunnyside 138kV Ckt 1 | Rebuild 0.75 mi of 138kV Transmission Line DBL CKT | [53 empty] | 2014-06-01 | 2014-06-01
2005-AG2 | CACHE - SNYDER 138KV CKT 1 | U | AEPW | AEPW |  |  | 0 | 588779 | TAP_G17-036 | 511435 | SNYDER-4 138 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | CACHE - SNYDER 138KV CKT 1 | Replace Snyder wavetrap | [53 empty] | 2008-05-21 | 2008-05-21
GI | TATONGA - MATTHEWSON 345KV CKT 1 | U | OKGE | OKGE |  |  | 0 | 515407 | TATONGA7 345.00 | 515497 | MATHWSON7 345.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | Woodward EHV 138kV Phase Shifting Transformer circuit #1 | Install one (1) 138 kV phase shifting transformer along with upgrading relay, protective, and metering equipment, and all associated and miscellaneous materials. | [53 empty] | 2017-08-02 | 2017-08-02
NA | TATONGA - WOODWARD 345KV CKT 1 | U | OKGE | OKGE | ENID | ENID | 0 | 515407 |  | 515375 |  |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | OGE | TATONGA - WOODWARD 345KV CKT 1 | Build 345 kV line | [53 empty] | 2010-01-01 | 2010-01-01
GI | Tolk 345/230 kV CKT 2 Transformer | U | SPS | SPS |  |  | 1 | 525549 | TOLK 7 | 525531 | TOLK 6 | 525537 | TOLK_TR | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Tolk 345/230 kV CKT 2 Transformer | Build new 345/230 transformer CKT 2 at Tolk to achieve a minimum normal/emergency rating of 921 MVA on the Crossroads-Tolk 345 kV CKT1 line | [53 empty] | 2020-12-31 | 2020-12-31
GI | TOLK EAST - PLANT X 230KV CKT 1 | U | SPS | SPS |  |  | 0 | 525531 | TOLK_EAST 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 2 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Plant X - Tolk 230kV rebuild circuit #2 | Rebuild Plant X – Tolk 230kV transmission circuit #2 which is approximately 10 miles in length. The existing 795 MCM ACSR conductor will be replaced with 995 MCM ACCS conductor along with upgrading associated disconnect switches, structural steel, foundat | [53 empty] | 2017-12-31 | 2017-12-31
GI | Tolk East - Tuco 230 kV Ckt 1 Rebuild | U | SPS | SPS |  |  | 0 | 525531 | TOLK | 525830 | TUCO_INT 6230.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Tolk East - Tuco 230 kV Ckt 1 Rebuild | Rebuild line to achieve minimum normal/emergency rating of 478 MVA | [53 empty] | 2020-12-15 | 2020-12-15
GI | TOLK WEST - PLANT X 230KV CKT 1 | U | SPS | SPS |  |  | 0 | 525531 | TOLK_WEST 6230.00 | 525481 | PLANT_X 6230.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Plant X - Tolk 230kV rebuild circuit #1 | Rebuild Plant X – Tolk 230kV transmission circuit #1 which is approximately 10 miles in length. The existing 795 MCM ACSR conductor will be replaced with 995 MCM ACCS conductor along with upgrading associated disconnect switches, structural steel, foundat | [53 empty] | 2017-12-31 | 2017-12-31
GI | Tuco 230 kV Capacitive Reactive Power Support | U | SPS | SPS |  |  | 0 | 525531 | TOLK | 525830 | TUCO_INT 6230.00 | 0 |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | Tuco 230 kV Capacitive Reactive Power Support | Install +100 MVar at Tuco 230 kV Substation | [53 empty] | 2020-12-31 | 2020-12-31
GI | TUCO INTERCHANGE 345/230KV TRANSFORMER CKT 1 | U | SPS | SPS |  |  | 1 | 525832 | TUCO_INT 7345.00 | 525830 | TUCO_INT 6230.00 | 525824 | TUCO_TR 113.200 | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | SPS | TUCO Interchange 345/230kV CKT 1 Replacement | The existing 345/230kV 560/560MVA autotransformer at Tuco Substation will be replaced with a new transformer unit to match the other transformer at this site. The new transformer can be installed at Tuco Substation by removing the existing transformer fro | [53 empty] | 2018-06-01 | 2018-06-01
GI | TURK 138/115KV TRANSFORMER CKT 1 | U | AEPW |  | SARK |  | 1 | 507454 | HEMPSTD4 138.00 | 507456 | HEMPSTD3 115.00 | 507458 | HEMP1 1 13.800 | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | AEP | TURK 138/115KV TRANSFORMER CKT 1 | Build Turk 138-115 kV station and relocate autotransformer (and spare) from Patterson to this new Turk station | [13 empty] | 2007-10-01 | [39 empty] | 2011-12-01 | 2011-12-01
GI | Twin Church - Dixon County 230kV Line Upgrade | U | NPPD | NPPD |  |  | 0 | 640560 | WAKEFIELD 4 | 640386 | TWIN CH4 |  |  | 1 | [13 empty] | BASECASE | BASE CASE | [8 empty] | Credit Flowgate |  |  | NPPD | Twin Church - Dixon County 230kV Line Upgrade | Increase clearances to accommodate 320MVA facility rating | [53 empty] | 2015-10-24 | 2015-10-24
2024-AG2 | ERCOTE DC TIE | S | AEPW | ERCOTE |  |  | 0 | 508847 | WELSHDC1 | 599893 | DCEAST | 0 |  |  | 26SP | 600 | 600 | 0 | 16.7 | 108.3333 | [6 empty] | CATEGORYA | BASECASE | BASE CASE | [11 empty] | AEPW | ERCOT North DC Tie Upgrade | Add additional 50 MW DC tie | [12 empty] | 35000000 | 2025-03-13 | [39 empty] | 2026-07-01 | 2030-12-01