## Executive Summary
Executive Summary: SPP Affected Systems Impact Study of AECI GIA-120-122
Pursuant to the Southwest Power Pool (SPP) and Associated Electric Cooperative Inc. (AECI) Joint Operating Agreement (JOA), SPP has conducted this Affected Systems Impact Study (ASIS) for generation interconnection requests studied in the AECI Generator Interconnection Queue. The primary objective of this ASIS is to identify constraints and over-dutied equipment on SPP facilities associated with the new AECI interconnection requests. The study analysis for the generation interconnection requests included in this ASIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 3.0 posted on http://opsportal.spp.org/Studies/Gen contains details about the ASIS process, methodology, definitions, and useful links. Please review the Generator Interconnection Manual or contact GI-AFS@SPP.org for more information about the study process. The withdrawal or termination of higher-queued requests could affect the results of this study, thereby requiring restudies to be performed. SPP will determine the need for further restudies. SPP ASIS of AECI GIA-120-122 includes study requests in the following cluster groups: 03 CENTRAL
Generator Interconnection Manual Version 1.6
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20240424.pdf
This ASIS analyzes the impact of interconnecting new generation for total of:
1205 MW
The total costs of Network Upgrades identified in this ASIS are estimated at:
0
Models Used in Study
2022 ITP Series (DISIS 2023-001 Phase 1)
Summer: 2024, 2027
Winter: 2027
Light: 2027
Assumptions Used in Study
Queued after DISIS-2023 and all higher-queued AECI requests. Removed higher-queued withdrawn units within a defined Study Area. Includes DISIS-2023 Phase 1 and all higher-queued identified Network Upgrades. Removed DISIS-2023 Phase 1 Network Upgrades allocated at 100% to withdrawn generators within the defined Study Area. Removed higher-queued Network Upgrades in the defined Study Area based on the most recent DISIS report posting. Includes AECI Network Upgrades for higher-queued requests. Incorporates model and group reduction. Incorporates fuel-based dispatch.
By: SPP Generator Interconnection Department
Published: May 30, 2025

## Revision History
Revision History
Date | Author | Change Description
4580700% | SPP | Initial Report Posting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Ammount | Limiting Element | Service | Area | POI | Status
GI-120 | 03 CENTRAL | 25.5 | DIS-24-1 PQ | Solar | 245 | 245 | N/A | ER/NR | AECI | Thomas Hill 345 kV Substation
GI-121 | 03 CENTRAL | 25.5 | DIS-24-1 PQ | Gas | 460 | 460 | N/A | ER/NR | AECI | Thomas Hill - McCredie 345 kV
GI-122 | 03 CENTRAL | 25.5 | DIS-24-1 PQ | Wind | 500 | 500 | N/A | ER | AECI | McCredie 345 kV Substation
GEN-2023-012 | 01 NORTH | 25 | DIS-23-1 | Wind | 98.6 | N/A | N/A | ER/NR | BEPC-SPP | Kingsbury County 115kV Substation | DISIS STAGE
GEN-2023-062 | 01 NORTH | 25 | DIS-23-1 | Thermal | 98 | N/A | N/A | ER | BEPC-SPP | REN 115 kV Substation | DISIS STAGE
GEN-2023-082 | 01 NORTH | 25 | DIS-23-1 | Battery/Storage | 175 | N/A | N/A | ER/NR | WAPA | White 115 kV Substation | DISIS STAGE
GEN-2023-097 | 01 NORTH | 25 | DIS-23-1 | Battery/Storage | 250 | N/A | N/A | ER/NR | BEPC-SPP | Judson 345 kV Substation | DISIS STAGE
GEN-2023-105 | 01 NORTH | 25 | DIS-23-1 | Wind | 249 | N/A | N/A | ER/NR | BEPC-SPP | Chappelle Creek 345 kV | DISIS STAGE
GEN-2023-154 | 01 NORTH | 25 | DIS-23-1 | Solar | 200 | N/A | N/A | ER/NR | WAPA | Fort Thompson - Huron 230 kV Tap | DISIS STAGE
GEN-2023-182 | 01 NORTH | 25 | DIS-23-1 | Wind | 300 | N/A | N/A | ER/NR | BEPC-SPP | Groton - Leland Olds 345 kV Line | DISIS STAGE
GEN-2023-011 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 190 | N/A | N/A | ER/NR | NPPD | Harbine 115 kV Substation | DISIS STAGE
GEN-2023-077 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 303 | N/A | N/A | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2023-078 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 303 | N/A | N/A | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2023-079 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 303 | N/A | N/A | ER/NR | OPPD | Substation 3740 345 kV | DISIS STAGE
GEN-2023-116 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 500 | N/A | N/A | ER/NR | NPPD | Keystone 345 kV Substation | DISIS STAGE
GEN-2023-117 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 300 | N/A | N/A | ER/NR | NPPD | Keystone 345 kV Substation | DISIS STAGE
GEN-2023-133 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 250 | N/A | N/A | ER | NPPD | Sweetwater 345 kV Substation | DISIS STAGE
GEN-2023-153 | 02 NEBRASKA | 25 | DIS-23-1 | Hybrid; Solar/Storage | 120 | N/A | N/A | ER/NR | BEPC-SPP | Grant 115 kV Substation | DISIS STAGE
GEN-2023-199 | 02 NEBRASKA | 25 | DIS-23-1 | Hybrid; Solar/Storage | 250 | N/A | N/A | ER/NR | NPPD | Twin Church 230 kV Substation | DISIS STAGE
GEN-2023-216 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 200 | N/A | N/A | ER/NR | NPPD | Turtle Creek 345 kV Substation | DISIS STAGE
GEN-2023-217 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 200 | N/A | N/A | ER/NR | NPPD | Turtle Creek 345 kV Substation | DISIS STAGE
GEN-2023-218 | 02 NEBRASKA | 25 | DIS-23-1 | Wind | 200 | N/A | N/A | ER/NR | NPPD | Turtle Creek 345 kV Substation | DISIS STAGE
GEN-2023-222 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | N/A | N/A | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2023-223 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 239 | N/A | N/A | ER/NR | NPPD | New Beatrice Power Station 345 kV | DISIS STAGE
GEN-2023-224 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 478 | N/A | N/A | ER | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2023-225 | 02 NEBRASKA | 25 | DIS-23-1 | Thermal | 217 | N/A | N/A | ER | NPPD | Olive Creek 345 kV Substation | DISIS STAGE
GEN-2023-006 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 202 | N/A | N/A | ER | WERE | Wolf Creek- Blackberry 345 kV Line Break | DISIS STAGE
GEN-2023-015 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 330 | N/A | N/A | ER/NR | SPS | Finney-Carpenter 345 KV line | DISIS STAGE
GEN-2023-023 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | KACY | Center City 161 kV Substation | DISIS STAGE
GEN-2023-032 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 200 | N/A | N/A | ER/NR | KCPL | Odessa and Lexington 161 kV Line | DISIS STAGE
GEN-2023-033 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | KCPL | Liberty South 161 kV Substation | DISIS STAGE
GEN-2023-034 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 130 | N/A | N/A | ER/NR | WERE | Clear Water - Waco 138 kV line | DISIS STAGE
GEN-2023-036 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | INDN | Eckles Road 161 kV Substation | DISIS STAGE
GEN-2023-037 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | KACY | Quindaro Bluffs 161 kV Substation | DISIS STAGE
GEN-2023-050 | 03 CENTRAL | 25 | DIS-23-1 | Hybrid; Solar/Storage | 400 | N/A | N/A | ER/NR | WERE | Neosho 345 kV Substation | DISIS STAGE
GEN-2023-061 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 100 | N/A | N/A | ER/NR | SWPA | Carthage 161 kV Substation | DISIS STAGE
GEN-2023-063 | 03 CENTRAL | 25 | DIS-23-1 | Hybrid; Solar/Storage | 135 | N/A | N/A | ER/NR | AEPW | Catoosa - Owasso 88th 138 kV line | DISIS STAGE
GEN-2023-065 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 140 | N/A | N/A | ER/NR | WERE | Halstead 69 kV Substation | DISIS STAGE
GEN-2023-073 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 400 | N/A | N/A | ER/NR | WERE | Rose Hill 345 kV Substation | DISIS STAGE
GEN-2023-085 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 150 | N/A | N/A | ER/NR | SWPA | Mansfield - Logan 161 kV Line | DISIS STAGE
GEN-2023-087 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 200 | N/A | N/A | ER/NR | KCPL | Archie 161 kV Substation | DISIS STAGE
GEN-2023-099 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 300 | N/A | N/A | ER/NR | WERE | Jeffery Energy Center 345 kV Substation | DISIS STAGE
GEN-2023-107 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 300 | N/A | N/A | ER | SUNC | Setab 345 kV | DISIS STAGE
GEN-2023-149 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 300 | N/A | N/A | ER/NR | KCPL | LaCygne - Stilwell 345 kV Line | DISIS STAGE
GEN-2023-169 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 125 | N/A | N/A | ER/NR | KCPL | Missouri City - Liberty South 161 kV Line | DISIS STAGE
GEN-2023-170 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 150 | N/A | N/A | ER | KCPL | Salisbury 161 kV Substation | DISIS STAGE
GEN-2023-171 | 03 CENTRAL | 25 | DIS-23-1 | Battery/Storage | 150 | N/A | N/A | ER/NR | INDN | Sub M 161 kV Substation | DISIS STAGE
GEN-2023-172 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 200 | N/A | N/A | ER/NR | SUNC | Holcomb 345 kV | DISIS STAGE
GEN-2023-173 | 03 CENTRAL | 25 | DIS-23-1 | Wind | 100 | N/A | N/A | ER/NR | SUNC | Holcomb 345 kV | DISIS STAGE
GEN-2023-194 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 225 | N/A | N/A | ER/NR | EMDE | Riverton - Neosho 161 kV Line Tap | DISIS STAGE
GEN-2023-219 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 125 | N/A | N/A | ER/NR | WERE | Reading - Osage Jct 115 kV Line | DISIS STAGE
GEN-2023-220 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | N/A | N/A | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | DISIS STAGE
GEN-2023-221 | 03 CENTRAL | 25 | DIS-23-1 | Solar | 250 | N/A | N/A | ER/NR | WERE | Emporia Energy Center - Swissvale 345 kV Line | DISIS STAGE
GEN-2023-231 | 03 CENTRAL | 25 | DIS-23-1 | Hybrid; Wind/Storage (studied as Solar/Storage) | 310 | N/A | N/A | ER | WERE | Neosho - LaCynge 345 kV Line | DISIS STAGE
GEN-2023-009 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 250 | N/A | N/A | ER/NR | WFEC | Hugo 138 kV Substation | DISIS STAGE
GEN-2023-022 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 250 | N/A | N/A | ER/NR | OKGE | Canadian River 345 kV Substation | DISIS STAGE
GEN-2023-027 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Battery | 150 | N/A | N/A | ER/NR | AEPW | Bird Hollow (Langley) - Pryor Junction 138 kV Line | DISIS STAGE
GEN-2023-028 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Battery | 230 | N/A | N/A | ER/NR | GRDA | Dry Gulch - Pensacola 161 kV Line | DISIS STAGE
GEN-2023-030 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 25 | N/A | N/A | ER/NR | AEPW | Tap between 345 kV SW Shreveport to Dolet Hills Substations | DISIS STAGE
GEN-2023-035 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | N/A | N/A | ER/NR | WFEC | Cleveland - Amber Tap 138 kV Line | DISIS STAGE
GEN-2023-038 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | N/A | N/A | ER/NR | OKGE | Lula 138 kV Substation | DISIS STAGE
GEN-2023-049 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | N/A | N/A | ER/NR | GRDA | Dry Gulch - Pensacola 161 kV Line | DISIS STAGE
GEN-2023-055 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 100 | N/A | N/A | ER/NR | GRDA | Kerr Grove 161 kV | DISIS STAGE
GEN-2023-056 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | N/A | N/A | ER/NR | SWPA | Van Buren 161 kV | DISIS STAGE
GEN-2023-057 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | N/A | N/A | ER/NR | GRDA | Pawnee Switch 138 kV | DISIS STAGE
GEN-2023-059 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/RECIP Gas | 200 | N/A | N/A | ER/NR | AEPW | Tap Rockhill to South Shreveport 138 kV line | DISIS STAGE
GEN-2023-064 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 200 | N/A | N/A | ER/NR | SWPA | RS Kerr-Stigler 161 kV line | DISIS STAGE
GEN-2023-069 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | N/A | N/A | ER/NR | WFEC | Tupelo - Atoka 138 kV Line | DISIS STAGE
GEN-2023-075 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 200 | N/A | N/A | ER/NR | WERE | Delaware to Neosho 345 kV | DISIS STAGE
GEN-2023-076 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 100 | N/A | N/A | ER/NR | WERE | Delaware - Neosho 345 kV | DISIS STAGE
GEN-2023-088 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 117 | N/A | N/A | ER/NR | WFEC | Pharaoh 138 kV Substation | DISIS STAGE
GEN-2023-092 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 125 | N/A | N/A | ER/NR | WFEC | Unger - Frogville 138 kV line | DISIS STAGE
GEN-2023-100 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | N/A | N/A | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2023-101 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | N/A | N/A | ER/NR | SPS | Tap Stateline Demarc - Wheeler 230 kV Line | DISIS STAGE
GEN-2023-102 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 475 | N/A | N/A | ER/NR | OKGE | Degrasse 345 kV Substation | DISIS STAGE
GEN-2023-104 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | N/A | N/A | ER/NR | WFEC | Mooreland - Noel 138 kV Line | DISIS STAGE
GEN-2023-132 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | N/A | N/A | ER/NR | SWPA | Jonesboro - Independence 161 kV | DISIS STAGE
GEN-2023-134 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 252 | N/A | N/A | ER/NR | AEPW | Fixico Tap to Weleetka 138 kV Line | DISIS STAGE
GEN-2023-135 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 52 | N/A | N/A | ER/NR | AEPW | Lydia 345kV substation | DISIS STAGE
GEN-2023-138 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 250 | N/A | N/A | ER/NR | GRDA | GRDA1 - Tonece7 345 kV Line | DISIS STAGE
GEN-2023-150 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | N/A | N/A | ER/NR | OKGE | Gracemont 138 kV Substation | DISIS STAGE
GEN-2023-151 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 100 | N/A | N/A | ER/NR | AEPW | South Nashville - South Murfreesboro 138kV | DISIS STAGE
GEN-2023-161 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 74.9 | N/A | N/A | ER/NR | OKGE | Roman Nose 138 kV Substation | DISIS STAGE
GEN-2023-164 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 210 | N/A | N/A | ER/NR | OKGE | Gracemont 345 kV Substation | DISIS STAGE
GEN-2023-165 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 210 | N/A | N/A | ER/NR | OKGE | Gracemont 345 kV Substation | DISIS STAGE
GEN-2023-166 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | N/A | N/A | ER | OKGE | 84th Street - Tennessee Tap 138 kV Line | DISIS STAGE
GEN-2023-167 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 250 | N/A | N/A | ER/NR | OKGE | Washington Park 138 kV Substation | DISIS STAGE
GEN-2023-168 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 175 | N/A | N/A | ER/NR | OKGE | Classen 138 kV Substation | DISIS STAGE
GEN-2023-174 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 150 | N/A | N/A | ER | WFEC | Paoli West 138 kV Substation | DISIS STAGE
GEN-2023-177 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 200 | N/A | N/A | ER/NR | OKGE | Paoli - Seminole 138 kV line tap | DISIS STAGE
GEN-2023-180 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 150 | N/A | N/A | ER/NR | AEPW | Hackett - N Huntington 161 kV Line Tap | DISIS STAGE
GEN-2023-193 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 175 | N/A | N/A | ER/NR | AEPW | Pirkey - Whitney 138 kV Line | DISIS STAGE
GEN-2023-204 | 04 SOUTHEAST | 25 | DIS-23-1 | Thermal | 953 | N/A | N/A | ER/NR | AEPW | Welsh-Lydia 345kV Line | DISIS STAGE
GEN-2023-205 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 180 | N/A | N/A | ER/NR | AEPW | McAlester City - Weleetka 138 kV line | DISIS STAGE
GEN-2023-206 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 50 | N/A | N/A | ER/NR | OKGE | Battlefield BESS 161 kV Substation | DISIS STAGE
GEN-2023-210 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 191 | N/A | N/A | ER/NR | WFEC | Prague - Chernicky 138 kV Line | DISIS STAGE
GEN-2023-211 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Battery/Wind | 250 | N/A | N/A | ER/NR | OKGE | Ranch Road 345 kV Substation | DISIS STAGE
GEN-2023-212 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 400 | N/A | N/A | ER/NR | AEPW | Northwest Texarkana - Valliant 345 kV Line | DISIS STAGE
GEN-2023-213 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 100 | N/A | N/A | ER/NR | AEPW | Chamber Springs 161 kV Substation | DISIS STAGE
GEN-2023-227 | 04 SOUTHEAST | 25 | DIS-23-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | AEP | Petty to Chapel 138 kV Line | DISIS STAGE
GEN-2023-229 | 04 SOUTHEAST | 25 | DIS-23-1 | Wind | 230 | N/A | N/A | ER/NR | AEPW | Southwestern Power Station 138 kV Substation (SWS4) | DISIS STAGE
GEN-2023-230 | 04 SOUTHEAST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 150 | N/A | N/A | ER/NR | AEPW | Red Pointe 138 kV Substation | DISIS STAGE
GEN-2023-241 | 04 SOUTHEAST | 25 | DIS-23-1 | Solar | 93 | N/A | N/A | ER | AEPW | Winnsboro 138 kV Substation | DISIS STAGE
ASGI-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 20 | N/A | N/A | ER/NR | SPS | Chevron Eddy 115 kV | DISIS STAGE
GEN-2023-001 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 230 | N/A | N/A | ER/NR | SPS | T14 Circuit 115 V Line | DISIS STAGE
GEN-2023-005 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 256 | N/A | N/A | ER/NR | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2023-008 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 75 | N/A | N/A | ER/NR | SPS | Tuco - Carlisle 230 kV line | DISIS STAGE
GEN-2023-010 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 280 | N/A | N/A | ER/NR | SPS | Moore Co 230 kV Substation | DISIS STAGE
GEN-2023-060 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 256 | N/A | N/A | ER/NR | SPS | Plant X 230kV Substation | DISIS STAGE
GEN-2023-081 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 625 | N/A | N/A | ER/NR | SPS | Crossroads - Hobbs 345 kV Line | DISIS STAGE
GEN-2023-086 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | N/A | N/A | ER/NR | SPS | Potter - Newhart 230 kV line | DISIS STAGE
GEN-2023-110 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 250 | N/A | N/A | ER/NR | SPS | Tap Border to Tuco 345 kV Line | DISIS STAGE
GEN-2023-120 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 130 | N/A | N/A | ER/NR | SPS | Kress 115 kV Substation | DISIS STAGE
GEN-2023-123 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 285 | N/A | N/A | ER/NR | SPS | Pringle Interchange 230 kV Substation | DISIS STAGE
GEN-2023-142 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 275 | N/A | N/A | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2023-143 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2023-158 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 335 | N/A | N/A | ER/NR | SPS | Needmore - Yoakum 230 kV Line | DISIS STAGE
GEN-2023-159 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | SPS | Needmore - Yoakum 230 kV Line | DISIS STAGE
GEN-2023-176 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 300 | N/A | N/A | ER/NR | SPS | Plant X 230 kV Substation | DISIS STAGE
GEN-2023-178 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 200 | N/A | N/A | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2023-183 | 05 SOUTHWEST | 25 | DIS-23-1 | Thermal | 217 | N/A | N/A | ER/NR | SPS | Tuco 345kV | DISIS STAGE
GEN-2023-184 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 200 | N/A | N/A | ER/NR | SPS | Phantom 115 kV Substation | DISIS STAGE
GEN-2023-188 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 160 | N/A | N/A | ER/NR | AEPW | Oklaunion - Lawton 345 kV Line | DISIS STAGE
GEN-2023-195 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 250 | N/A | N/A | ER/NR | SPS | Roosevelt - Tolk 230 kV line tap | DISIS STAGE
GEN-2023-201 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | N/A | N/A | ER/NR | SPS | Crossroads - Hobbs 345 kV Line | DISIS STAGE
GEN-2023-203 | 05 SOUTHWEST | 25 | DIS-23-1 | Hybrid; Solar/Storage | 300 | N/A | N/A | ER/NR | SPS | Hobbs - Ink Basin 230 kV Transmission Line | DISIS STAGE
GEN-2023-208 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 200 | N/A | N/A | ER | SPS | Rolling Hills 115 kV | DISIS STAGE
GEN-2023-209 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 125 | N/A | N/A | ER/NR | SPS | Amarillo South 115 kV | DISIS STAGE
GEN-2023-228 | 05 SOUTHWEST | 25 | DIS-23-1 | Battery/Storage | 250 | N/A | N/A | ER/NR | SPS | Tuco-Okalunion 345 kV line | DISIS STAGE
GEN-2023-236 | 05 SOUTHWEST | 25 | DIS-23-1 | Solar | 400 | N/A | N/A | ER/NR | SPS | Hobbs - Yoakum 345 kV | DISIS STAGE
GEN-2023-237 | 05 SOUTHWEST | 25 | DIS-23-1 | Wind | 500 | N/A | N/A | ER/NR | SPS | Crawfish Draw 345 kV Substation | DISIS STAGE
GEN-2022-009 | 01 NORTH | 24 | DIS-22-1 | Thermal | 125 | N/A | N/A | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-010 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | N/A | N/A | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-083 | 01 NORTH | 24 | DIS-22-1 | Thermal | 250 | N/A | N/A | ER | BEPC | Judson Substation 345 kV | DISIS STAGE
GEN-2022-004 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 33 | N/A | N/A | ER/NR | WERE | Murray Gill 138 kV Substation | DISIS STAGE
GEN-2022-005 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | N/A | N/A | ER/NR | WERE | Northeast Parsons 138kV Substation | DISIS STAGE
GEN-2022-006 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | N/A | N/A | ER/NR | WERE | Neosho - N345 161 kV Substation | DISIS STAGE
GEN-2022-007 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 135 | N/A | N/A | ER/NR | WERE | Lang - Reading 115 kV Transmission Line | DISIS STAGE
GEN-2022-013 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 300 | N/A | N/A | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2022-015 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 270 | N/A | N/A | ER/NR | SUNC | Tap of Mingo - Red Willow 345 kV Line | DISIS STAGE
GEN-2022-024 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | WERE | Tap of Neosho - LaCygne 345 kV Line | DISIS STAGE
GEN-2022-054 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 200 | N/A | N/A | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Tap | DISIS STAGE
GEN-2022-065 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 145 | N/A | N/A | ER/NR | SUNC | tap on Arthur Mullergreen-Spearville 230 kV line | DISIS STAGE
GEN-2022-073 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 300 | N/A | N/A | ER/NR | KCPL | Nashua 161 kV Substation | DISIS STAGE
GEN-2022-075 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 175 | N/A | N/A | ER/NR | MIDW | Tap on the Spearville - Post Rock 345kV line | DISIS STAGE
GEN-2022-100 | 03 CENTRAL | 24 | DIS-22-1 | Hybrid | 80 | N/A | N/A | ER/NR | KCPL | Overton - Sedalia East 161 kV Substation | DISIS STAGE
GEN-2022-102 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 100 | N/A | N/A | ER/NR | KCPL | Liberty West 161 kV | DISIS STAGE
GEN-2022-142 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | KCPL | Shoal Creek 161 kV Substation | DISIS STAGE
GEN-2022-144 | 03 CENTRAL | 24 | DIS-22-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | KCPL | Blue Mills BESS 161kV Substation | DISIS STAGE
GEN-2022-161 | 03 CENTRAL | 24 | DIS-22-1 | Wind | 400 | N/A | N/A | ER | WERE | Burns 345kV Substation | DISIS STAGE
GEN-2022-214 | 03 CENTRAL | 24 | DIS-22-1 | Solar | 239 | N/A | N/A | ER | WERE | Gill - Viola 138 kV Line Break | DISIS STAGE
GEN-2022-012 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | N/A | N/A | ER/NR | OGE | Woodward 345 kV Substation | DISIS STAGE
GEN-2022-016 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 288 | N/A | N/A | ER/NR | OGE | Woodward 345kV Substation | DISIS STAGE
GEN-2022-017 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | N/A | N/A | ER/NR | OGE | Woodward 345kV Substation | DISIS STAGE
GEN-2022-038 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | N/A | N/A | ER/NR | AEP | Longwood to Scottville 138 kV line | DISIS STAGE
GEN-2022-055 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | N/A | N/A | ER/NR | WFEC | Sunshine North to Anadarko 138 kV | DISIS STAGE
GEN-2022-071 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 90.824 | N/A | N/A | ER/NR | AEP | Talawanda to Canadian River 138 kV Line Tap | DISIS STAGE
GEN-2022-098 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | N/A | N/A | ER/NR | OGE | Bison 345kV Substation | DISIS STAGE
GEN-2022-104 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 113.078 | N/A | N/A | ER/NR | WFEC | Brown - South Coleman Junction 138kV line | DISIS STAGE
GEN-2022-111 | 04 SOUTHEAST | 24 | DIS-22-1 | Hybrid | 150 | N/A | N/A | ER/NR | AEP | Wilkes 345 kV Substation | DISIS STAGE
GEN-2022-130 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | OGE | Battlefield BESS 161kV | DISIS STAGE
GEN-2022-136 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | WFEC | Colbert 138 kV Substation | DISIS STAGE
GEN-2022-139 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 300 | N/A | N/A | ER/NR | AEP | Pirkey 345kV Substation | DISIS STAGE
GEN-2022-143 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | OGE | Caney Creek 138 kV Substation | DISIS STAGE
GEN-2022-145 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 195 | N/A | N/A | ER | AEP | Weatherford Jct. to Hinton 138 kV line | DISIS STAGE
GEN-2022-154 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | N/A | N/A | ER | WFEC | Canadian Switch 138 kV Substation | DISIS STAGE
GEN-2022-155 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 200 | N/A | N/A | ER | OGE | Horseshoe Lake 138 kV Substation | DISIS STAGE
GEN-2022-156 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 100 | N/A | N/A | ER | GRDA | Silver City 138 kV Substation | DISIS STAGE
GEN-2022-176 | 04 SOUTHEAST | 24 | DIS-22-1 | Wind | 215 | N/A | N/A | ER/NR | AEP | Northeastern - Delaware 345 kV transmission line | DISIS STAGE
GEN-2022-231 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 166 | N/A | N/A | ER/NR | OGE | Crescent to Cottonwood Creek 138 kV Line | DISIS STAGE
GEN-2022-234 | 04 SOUTHEAST | 24 | DIS-22-1 | Solar | 200 | N/A | N/A | ER/NR | AEP | Alluwe Tap â€“ Chelsea 138 kV line | DISIS STAGE
GEN-2022-235 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | N/A | N/A | ER/NR | WFEC | El Reno SW 138 kV | DISIS STAGE
GEN-2022-238 | 04 SOUTHEAST | 24 | DIS-22-1 | Battery/Storage | 150 | N/A | N/A | ER/NR | OGE | Maud 138 kV substation | DISIS STAGE
GEN-2022-147 | 05 SOUTHWEST | 24 | DIS-22-1 | Thermal | 203 | N/A | N/A | ER | SPS | Tuco 345kV | DISIS STAGE
GEN-2021-008 | 01 NORTH | 23 | DIS-21-1 | Solar | 200 | N/A | N/A | ER/NR | BEPC | 345kV Bus at BEPC Patent Gate Substation, McKenzie County, ND | DISIS STAGE
GEN-2021-027 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 102.06 | N/A | N/A | ER | NPPD | Olive Creek 115 kV Substation | DISIS STAGE
GEN-2021-034 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 113 | N/A | N/A | ER | LES | Rokeby 115 kV Substation | DISIS STAGE
GEN-2021-039 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 100 | N/A | N/A | ER | OPPD | New 161kV substation looping in OPPD 161kV lines S1211 to S1220 and S1211 to S1299 | DISIS STAGE
GEN-2021-040 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 200 | N/A | N/A | ER | OPPD | OPPD District, Cass County Power Plant Substation, 345kV Bus | DISIS STAGE
GEN-2021-043 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 250 | N/A | N/A | ER | LES | 8000 SW 12th (Rokeby) Station, 115kV Bus | DISIS STAGE
GEN-2021-048 | 02 NEBRASKA | 23 | DIS-21-1 | Battery/Storage | 75 | N/A | N/A | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-049 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 250 | N/A | N/A | ER/NR | LES | Wagener 115kV Substation | DISIS STAGE
GEN-2021-057 | 02 NEBRASKA | 23 | DIS-21-1 | Wind | 300 | N/A | N/A | ER | NPPD | Antelope 345kV substation | DISIS STAGE
GEN-2021-108 | 02 NEBRASKA | 23 | DIS-21-1 | Solar | 182.25 | N/A | N/A | ER/NR | OPPD | OPPD 345KV Cass County Substation | DISIS STAGE
GEN-2021-005 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 350 | N/A | N/A | ER/NR | WERE | Summit 345 kV substation in Saline County, KS | DISIS STAGE
GEN-2021-006 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 300 | N/A | N/A | ER/NR | WERE | Neosho 345kV substation in Labette County, KS | DISIS STAGE
GEN-2021-017 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 37.5 | N/A | N/A | ER | SUNC | Elm Creek 345 kV interconnection substation | DISIS STAGE
GEN-2021-021 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 150 | N/A | N/A | ER | SPS | Carpenter 345 kV Substation | DISIS STAGE
GEN-2021-023 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 306.18 | N/A | N/A | ER | WERE | Wild Plains 345kV Substation | DISIS STAGE
GEN-2021-029 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 253.8 | N/A | N/A | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-030 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 510.3 | N/A | N/A | ER | KCPL | Evergy Tap the La Cygne to Stillwel 345 kV Line | DISIS STAGE
GEN-2021-035 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | N/A | N/A | ER | SUNC | Tap Sunflower Santana 115kV Transmission Line | DISIS STAGE
GEN-2021-042 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 50 | N/A | N/A | ER/NR | KCPL | Independence Power & Light, Blue Valley Substation, 161kV Bus | DISIS STAGE
GEN-2021-050 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 200 | N/A | N/A | ER/NR | KCPL | 161kV Stilwell-Clinton Line | DISIS STAGE
GEN-2021-051 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 75 | N/A | N/A | ER/NR | KCPL | 161kV Stilwell-Clinton Line | DISIS STAGE
GEN-2021-056 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 300 | N/A | N/A | ER | WERE | Viola 345kV Substation | DISIS STAGE
GEN-2021-068 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | N/A | N/A | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-069 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 249.6 | N/A | N/A | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-070 | 03 CENTRAL | 23 | DIS-21-1 | Wind | 504 | N/A | N/A | ER | SUNC | SUNC Spearville - Holcomb 345kV | DISIS STAGE
GEN-2021-076 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 113 | N/A | N/A | ER/NR | MIDW | ITC Post Rock 345 kV Substation | DISIS STAGE
GEN-2021-077 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 95 | N/A | N/A | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV | DISIS STAGE
GEN-2021-096 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 500 | N/A | N/A | ER/NR | WERE | Wolf Creek - Benton 345 kV | DISIS STAGE
GEN-2021-101 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 159 | N/A | N/A | ER/NR | WERE | Evergy's Midland Substation 115kV bus | DISIS STAGE
GEN-2021-103 | 03 CENTRAL | 23 | DIS-21-1 | Battery/Storage | 150 | N/A | N/A | ER/NR | WERE | Evergy's Atlantic Substation115kV bus | DISIS STAGE
GEN-2021-107 | 03 CENTRAL | 23 | DIS-21-1 | Solar | 201.6 | N/A | N/A | ER | WERE | Evergy 345kV Jeffrey Energy Center | DISIS STAGE
GEN-2021-001 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | N/A | N/A | ER/NR | OKGE | 138kV Brown Substation | DISIS STAGE
GEN-2021-015 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 74.9 | N/A | N/A | ER | OKGE | Bobcat 345 kV interconnection substation | DISIS STAGE
GEN-2021-016 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 250 | N/A | N/A | ER | AEPW | Sunnyside-Johnston 345 kV | DISIS STAGE
GEN-2021-018 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 231 | N/A | N/A | ER | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-019 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 74.9 | N/A | N/A | ER/NR | OKGE | Sooner 345 kV | DISIS STAGE
GEN-2021-025 | 04 SOUTHEAST | 23 | DIS-21-1 | Wind | 203.04 | N/A | N/A | ER | WFEC | Western Farmers 138kV Mooreland Substation | DISIS STAGE
GEN-2021-033 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | N/A | N/A | ER | OKGE | Grand Prairie 161kV Substation | DISIS STAGE
GEN-2021-036 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 204.12 | N/A | N/A | ER/NR | AEPW | Craig to Patterson 138 kV Transmission Line | DISIS STAGE
GEN-2021-038 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | AEPW | Welsh 345kV Substation | DISIS STAGE
GEN-2021-041 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | N/A | N/A | ER/NR | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2021-047 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 250 | N/A | N/A | ER | GRDA | Tulsa (Bus #509852) - Igloo (Bus #513596) 345kV line | DISIS STAGE
GEN-2021-052 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 75 | N/A | N/A | ER | OKGE | Pecan Creek 345kV substation | DISIS STAGE
GEN-2021-053 | 04 SOUTHEAST | 23 | DIS-21-1 | Solar | 300 | N/A | N/A | ER | OKGE | Pecan Creek 345 kV Substation | DISIS STAGE
GEN-2021-063 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 155 | N/A | N/A | ER/NR | AEPW | Craig JCT 138kV | DISIS STAGE
GEN-2021-064 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 100 | N/A | N/A | ER/NR | AEPW | Carnegie South 138kV | DISIS STAGE
GEN-2021-075 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 300 | N/A | N/A | ER/NR | AEPW | CAMPCOR4 138kV Substation | DISIS STAGE
GEN-2021-088 | 04 SOUTHEAST | 23 | DIS-21-1 | Battery/Storage | 100 | N/A | N/A | ER/NR | OKGE | Cedar Lane - Canadian 138 kV Transmission Line | DISIS STAGE
GEN-2021-098 | 04 SOUTHEAST | 23 | DIS-21-1 | Hybrid | 160 | N/A | N/A | ER/NR | OKGE | Dewey District 138 kV Substation | DISIS STAGE
ASGI-2021-001 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid | 50 | N/A | N/A | ER/NR | SPS |  | DISIS STAGE
ASGI-2021-003 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid | 40 | N/A | N/A | ER/NR | SPS |  | DISIS STAGE
GEN-2021-010 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 231 | N/A | N/A | ER | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-012 | 05 SOUTHWEST | 23 | DIS-21-1 | Battery/Storage | 225 | N/A | N/A | ER | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-014 | 05 SOUTHWEST | 23 | DIS-21-1 | Solar | 231 | N/A | N/A | ER | OKGE | Border 345 kV interconnection substation | DISIS STAGE
GEN-2021-090 | 05 SOUTHWEST | 23 | DIS-21-1 | Hybrid | 400 | N/A | N/A | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2020-014 | 01 NORTH | 22 | DIS-20-1 | Thermal | 45 | N/A | N/A | ER/NR | BEPC | Lonesome Creek 115kV | DISIS STAGE
GEN-2020-021 | 01 NORTH | 22 | DIS-20-1 | Wind | 235 | N/A | N/A | ER/NR | BEPC | LeLand Olds-Chapelle Creek 345kV line | DISIS STAGE
GEN-2020-083 | 01 NORTH | 22 | DIS-20-1 | Hybrid | 74.5 | N/A | N/A | ER/NR | WAPA | Fairview 115kV Substation | DISIS STAGE
GEN-2020-091 | 01 NORTH | 22 | DIS-20-1 | Solar | 150 | N/A | N/A | ER/NR | BEPC | Patent Gate Substation 345 kV | DISIS STAGE
GEN-2020-002 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 81 | N/A | N/A | ER | OPPD | 6846 Substation 69 kV | DISIS STAGE
GEN-2020-011 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid | 320 | N/A | N/A | ER/NR | NPPD | Axtell-Sweetwater Substation 345kV | DISIS STAGE
GEN-2020-013 | 02 NEBRASKA | 22 | DIS-20-1 | Hybrid | 215 | N/A | N/A | ER/NR | NPPD | Orleans-Holdrege Substation 115kV | DISIS STAGE
GEN-2020-025 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | N/A | N/A | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-028 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 255 | N/A | N/A | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-031 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 303 | N/A | N/A | ER | OPPD | Substation 1363; 161kV Substation | DISIS STAGE
GEN-2020-038 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 303 | N/A | N/A | ER | OPPD | Substation 3740; 345kV | DISIS STAGE
GEN-2020-043 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | N/A | N/A | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-044 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | N/A | N/A | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-045 | 02 NEBRASKA | 22 | DIS-20-1 | Thermal | 56.52 | N/A | N/A | ER | OPPD | Between Substation 1209 and 1252; 161kV | DISIS STAGE
GEN-2020-069 | 02 NEBRASKA | 22 | DIS-20-1 | Wind | 52.85 | N/A | N/A | ER/NR | NPPD | Cody to Valentine 115kV line | DISIS STAGE
GEN-2020-078 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 100 | N/A | N/A | ER/NR | OPPD | Substation 1226 to Substation 1237, 161kV Tap | DISIS STAGE
GEN-2020-084 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 350 | N/A | N/A | ER/NR | OPPD | Raun - Fort Calhoun 345 kV | DISIS STAGE
GEN-2020-094 | 02 NEBRASKA | 22 | DIS-20-1 | Solar | 250 | N/A | N/A | ER/NR | OPPD | Neb. City - 103rd & Rokeby 345 kV | DISIS STAGE
ASGI-2020-001 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 35 | N/A | N/A | ER | KCPL |  | DISIS STAGE
ASGI-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 35 | N/A | N/A | ER | KCPL |  | DISIS STAGE
GEN-2020-003 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 58 | N/A | N/A | ER/NR | WERE | East Substation 69 kV | DISIS STAGE
GEN-2020-007 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 650 | N/A | N/A | ER/NR | KCPL | Evergy La Cygne to Wolf Creek 345kV Substation | DISIS STAGE
GEN-2020-008 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 250 | N/A | N/A | ER | SPS | Corporation Carpenter 345kV Substation | DISIS STAGE
GEN-2020-056 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 20 | N/A | N/A | ER/NR | SUNC | Russell 115 kV Substation | DISIS STAGE
GEN-2020-057 | 03 CENTRAL | 22 | DIS-20-1 | Battery/Storage | 424.5 | N/A | N/A | ER/NR | KCPL | Atlantic 345 kV Substation | DISIS STAGE
GEN-2020-058 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 424.5 | N/A | N/A | ER/NR | KCPL | Evergy Atlantic 345kV Substation | DISIS STAGE
GEN-2020-061 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 29 | N/A | N/A | ER/NR | KCPL | Pleasant Hill 345/161/69 kV Substation | DISIS STAGE
GEN-2020-064 | 03 CENTRAL | 22 | DIS-20-1 | Thermal | 64 | N/A | N/A | ER/NR | EDE | 4544 Stateline CC 161kV Substation | DISIS STAGE
GEN-2020-072 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 150 | N/A | N/A | ER/NR | KCPL | Windsor to AEC Sedalia 161 kV line | DISIS STAGE
GEN-2020-073 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 150 | N/A | N/A | ER/NR | KCPL | SE Ottawa to Pleasant Valley 161kV | DISIS STAGE
GEN-2020-079 | 03 CENTRAL | 22 | DIS-20-1 | Hybrid | 225 | N/A | N/A | ER/NR | EDE | Riverton-Neosho 161kV line | DISIS STAGE
GEN-2020-088 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 150 | N/A | N/A | ER/NR | EDE | La Russell 161 kV Substation | DISIS STAGE
GEN-2020-090 | 03 CENTRAL | 22 | DIS-20-1 | Solar | 204.3 | N/A | N/A | ER/NR | WERE | Wolf Creek - Blackberry 345 kV Substation | DISIS STAGE
GEN-2020-010 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid | 140 | N/A | N/A | ER/NR | WFEC | Seiling-Taloga Substations 138kV | DISIS STAGE
GEN-2020-012 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid | 113 | N/A | N/A | ER/NR | AEPW | Snyder â€“ Altus Jct. 138kV | DISIS STAGE
GEN-2020-020 | 04 SOUTHEAST | 22 | DIS-20-1 | Hybrid | 201.6 | N/A | N/A | ER/NR | AEPW | Tap the 345 kV Northwest Texarkana - Valliant line | DISIS STAGE
GEN-2020-054 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 298 | N/A | N/A | ER/NR | AEPW | Lydia 345 kV Station | DISIS STAGE
GEN-2020-074 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | AEPW | Lawton to Sunnyside 345 kV Substation | DISIS STAGE
GEN-2020-075 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-081 | 04 SOUTHEAST | 22 | DIS-20-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | AEPW | Tenaska Switching Substation 345kV | DISIS STAGE
GEN-2020-085 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | N/A | N/A | ER/NR | AEPW | Lawton to Sunnyside 345 kV Line | DISIS STAGE
GEN-2020-087 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 500 | N/A | N/A | ER/NR | AEPW | Cimmarron to Lawton 345 kV Line | DISIS STAGE
GEN-2020-092 | 04 SOUTHEAST | 22 | DIS-20-1 | Solar | 100 | N/A | N/A | ER/NR | AEPW | Pryor Junction - Midwest Carbide 138kV line | DISIS STAGE
GEN-2020-009 | 05 SOUTHWEST | 22 | DIS-20-1 | Hybrid | 300 | N/A | N/A | ER/NR | AEPW | Lawton East Side to Oklaunion 345kV | DISIS STAGE
GEN-2020-017 | 05 SOUTHWEST | 22 | DIS-20-1 | Solar | 74.88 | N/A | N/A | ER/NR | SPS | 230kV Lamb County Interchange | DISIS STAGE
GEN-2020-059 | 05 SOUTHWEST | 22 | DIS-20-1 | Hybrid | 250 | N/A | N/A | ER | SPS | Tuco-Yoakum-Hobbs 345 kV | DISIS STAGE
GEN-2020-060 | 05 SOUTHWEST | 22 | DIS-20-1 | Battery/Storage | 200 | N/A | N/A | ER | SPS | Lubbock East Substation 230 kV | DISIS STAGE
GEN-2020-062 | 05 SOUTHWEST | 22 | DIS-20-1 | Solar | 256 | N/A | N/A | ER | SPS | OASIS 230kV Substation | DISIS STAGE
GEN-2020-065 | 05 SOUTHWEST | 22 | DIS-20-1 | Thermal | 1003 | N/A | N/A | ER | SPS | Hobbs-Andrews 345 kV Line | DISIS STAGE
GEN-2020-067 | 05 SOUTHWEST | 22 | DIS-20-1 | Wind | 352.5 | N/A | N/A | ER | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2020-068 | 05 SOUTHWEST | 22 | DIS-20-1 | Solar | 400 | N/A | N/A | ER | SPS | Tuco to Yoakum 345kV line | DISIS STAGE
GEN-2018-067 | 01 NORTH | 21 | DIS-18-2 | Wind | 255 | N/A | N/A | ER | BEPC-SPP | 115kV Strandahl sub | DISIS STAGE
GEN-2018-069 | 01 NORTH | 21 | DIS-18-2 | Wind | 125 | N/A | N/A | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2018-074 | 01 NORTH | 21 | DIS-18-2 | Wind | 72 | N/A | N/A | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2019-019 | 01 NORTH | 21 | DIS-19-1 | Thermal | 15.15 | N/A | N/A | ER/NR | BEPC-SPP | Siouxland 69kV | DISIS STAGE
GEN-2019-023 | 01 NORTH | 21 | DIS-19-1 | Hybrid | 110 | N/A | N/A | ER/NR | WAPA | WAPA-UGP Mingusville 230kV | DISIS STAGE
GEN-2019-037 | 01 NORTH | 21 | DIS-19-1 | Solar | 150 | N/A | N/A | ER/NR | BEPC-SPP | Leland Olds 345kV substation | DISIS STAGE
GEN-2018-065 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 19.8 | N/A | N/A | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-068 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 302.4 | N/A | N/A | ER/NR | NPPD | Antelope 345 kV Substation | DISIS STAGE
GEN-2018-083 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 250 | N/A | N/A | ER | NPPD | Shell Creek-Hoskins 345kv Line Break | DISIS STAGE
GEN-2018-125 | 02 NEBRASKA | 21 | DIS-18-2 | Wind | 231 | N/A | N/A | ER/NR | NPPD | New switching station on Gentleman to Sweetwater 345kV line | DISIS STAGE
GEN-2018-131 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 221.4 | N/A | N/A | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2018-132 | 02 NEBRASKA | 21 | DIS-18-2 | Solar | 201.6 | N/A | N/A | ER/NR | NPPD | Antelope - Hoskins 345 kV | DISIS STAGE
GEN-2019-009 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | N/A | N/A | ER | OPPD | S1263 Brock 161kV substation | DISIS STAGE
GEN-2019-039 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 174.5 | N/A | N/A | ER/NR | NPPD | Columbus Southeast-Rising City 115kV | DISIS STAGE
GEN-2019-041 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 78 | N/A | N/A | ER/NR | NPPD | 115kV Monolith Substation | DISIS STAGE
GEN-2019-069 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | N/A | N/A | ER | NPPD | Shell Creek-Hoskins 345kV Line | DISIS STAGE
GEN-2019-070 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 50 | N/A | N/A | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2019-073 | 02 NEBRASKA | 21 | DIS-19-1 | Solar | 100 | N/A | N/A | ER | NPPD | Shell Creek-Hoskins 345kv Line | DISIS STAGE
GEN-2018-108 | 03 CENTRAL | 21 | DIS-18-2 | Battery/Storage | 95 | N/A | N/A | ER | SUNC | Thistle 345kV substation | DISIS STAGE
GEN-2018-128 | 03 CENTRAL | 21 | DIS-18-2 | Wind | 200.22 | N/A | N/A | ER/NR | WERE | Renfrow-Viola 345 kV | DISIS STAGE
GEN-2019-001 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 25 | N/A | N/A | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | DISIS STAGE
GEN-2019-016 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 200 | N/A | N/A | ER | EMDE | Dadeville 161kV Substation | DISIS STAGE
GEN-2019-018 | 03 CENTRAL | 21 | DIS-19-1 | Thermal | 15.56 | N/A | N/A | ER/NR | MIDW | Saxman 115kV substation | DISIS STAGE
GEN-2019-030 | 03 CENTRAL | 21 | DIS-19-1 | Wind | 252 | N/A | N/A | ER/NR | SUNC | Spearville to Clark County 345 kV line | DISIS STAGE
GEN-2019-044 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 100 | N/A | N/A | ER | SUNC | North Fort Dodge 115kV Substation | DISIS STAGE
GEN-2019-053 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | N/A | N/A | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-054 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | N/A | N/A | ER/NR | SUNC | Great Bend- Circle 230kV line | DISIS STAGE
GEN-2019-055 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | N/A | N/A | ER/NR | SUNC | Great Bend-Spearville 230kV line | DISIS STAGE
GEN-2019-058 | 03 CENTRAL | 21 | DIS-19-1 | Solar | 150 | N/A | N/A | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-063 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | N/A | N/A | ER/NR | SUNC | Clark County 345kV substation | DISIS STAGE
GEN-2019-068 | 03 CENTRAL | 21 | DIS-19-1 | Battery/Storage | 50 | N/A | N/A | ER/NR | SUNC | Great Bend - Circle 230kV line | DISIS STAGE
GEN-2018-064 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 80 | N/A | N/A | ER/NR | GRDA | Tonnece Substation 69kV | DISIS STAGE
GEN-2018-071 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | N/A | N/A | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-072 | 04 SOUTHEAST | 21 | DIS-18-2 | Battery/Storage | 151 | N/A | N/A | ER/NR | OKGE | Interconnecting into OG&E's Ranch Road 345kV substation by tapping a 0.1 gen tie line into the existing Frontier II gen-tie line | DISIS STAGE
GEN-2018-079 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 148 | N/A | N/A | ER | AEPW | Farmland-Delaware 138kV line | DISIS STAGE
GEN-2018-082 | 04 SOUTHEAST | 21 | DIS-18-2 | Wind | 215 | N/A | N/A | ER | AEPW | Pittsburg 345kV Substation | DISIS STAGE
GEN-2018-106 | 04 SOUTHEAST | 21 | DIS-18-2 | Solar | 165 | N/A | N/A | ER | AEPW | Longwood 345kV substation | DISIS STAGE
GEN-2018-115 | 04 SOUTHEAST | 21 | DIS-18-2 | Hybrid | 250 | N/A | N/A | ER/NR | AEPW | Lawton East Side 345kV/138kv Substation | DISIS STAGE
GEN-2019-002 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 100 | N/A | N/A | ER | GRDA | Maid 161kV substation | DISIS STAGE
GEN-2019-012 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 200 | N/A | N/A | ER/NR | OKGE | Woodward 345kV substation | DISIS STAGE
GEN-2019-045 | 04 SOUTHEAST | 21 | DIS-19-1 | Solar | 155 | N/A | N/A | ER | OKGE | DeGrasse 138kV Substation | DISIS STAGE
GEN-2019-065 | 04 SOUTHEAST | 21 | DIS-19-1 | Battery/Storage | 180 | N/A | N/A | ER | AEPW | Overton-Northwest Henderson 138kV | DISIS STAGE
GEN-2018-089 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 196 | N/A | N/A | ER | SPS | Newhart 230kV Substation | DISIS STAGE
GEN-2018-099 | 05 SOUTHWEST | 21 | DIS-18-2 | Wind | 300 | N/A | N/A | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2019-003 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 150 | N/A | N/A | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
GEN-2019-011 | 05 SOUTHWEST | 21 | DIS-19-1 | Battery/Storage | 207 | N/A | N/A | ER/NR | SPS | Yoakum 345kV Substation | DISIS STAGE
GEN-2019-021 | 05 SOUTHWEST | 21 | DIS-19-1 | Solar | 50 | N/A | N/A | ER/NR | SPS | Roosevelt 230kV Substation | DISIS STAGE
MPC04300 | 01 NORTH | 20.5 | DIS-18-2-PQ | Wind | 200 | N/A | N/A | ER/NR | OTP
GIA-101 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 460 | N/A | N/A | ER/NR | AECI
GIA-102 | 03 CENTRAL | 20.5 | DIS-18-2-PQ | Gas | 75 | N/A | N/A | ER/NR | AECI
GIA-103 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | N/A | N/A | ER/NR | AECI
GIA-104 | 04 SOUTHEAST | 20.5 | DIS-18-2-PQ | Gas | 460 | N/A | N/A | ER/NR | AECI
ASGI-2017-013 | 01 NORTH | 20 | DIS-18-1 | Wind | 40 | N/A | N/A | ER | WAPA |  | DISIS STAGE
GEN-2018-010 | 01 NORTH | 20 | DIS-18-1 | Battery/Storage | 74.1 | N/A | N/A | ER/NR | BEPC-SPP | Neset 230kV Substation | DISIS STAGE
GEN-2018-025 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | N/A | N/A | ER | OPPD | Fort Calhoun 345kV Substation
GEN-2018-033 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 200 | N/A | N/A | ER | OPPD | Cass County 345kV Substation
GEN-2018-037 | 02 NEBRASKA | 20 | DIS-18-1 | Battery/Storage | 100 | N/A | N/A | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV
GEN-2018-043 | 02 NEBRASKA | 20 | DIS-18-1 | Solar | 500 | N/A | N/A | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break
ASGI-2018-003 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | N/A | N/A | ER | KCPL |  | DISIS STAGE
ASGI-2018-006 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | N/A | N/A | ER | KCPL |  | DISIS STAGE
ASGI-2018-007 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 20 | N/A | N/A | ER | KCPL |  | DISIS STAGE
ASGI-2018-010 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | N/A | N/A | ER | KCPL |  | DISIS STAGE
ASGI-2018-011 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 35 | N/A | N/A | ER | KCPL |  | DISIS STAGE
GEN-2018-009 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 150 | N/A | N/A | ER | SUNC | Cimarron 115kV Substation | DISIS STAGE
GEN-2018-013 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 74.1 | N/A | N/A | ER | WERE | Abilene Energy Center-Northview 115kV Line | DISIS STAGE
GEN-2018-031 | 03 CENTRAL | 20 | DIS-18-1 | Battery/Storage | 50 | N/A | N/A | ER | KCPL | Blue Valley 161kV Substation | DISIS STAGE
GEN-2018-032 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 310 | N/A | N/A | ER | WERE | Neosho 345kV Substation | DISIS STAGE
GEN-2018-049 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 120 | N/A | N/A | ER | SUNC | Thistle 345kV Substation | DISIS STAGE
GEN-2018-057 | 03 CENTRAL | 20 | DIS-18-1 | Solar | 203.4 | N/A | N/A | ER/NR | WERE | Gordon Evans 138kV | DISIS STAGE
GEN-2018-060 | 03 CENTRAL | 20 | DIS-18-1 | Wind | 50 | N/A | N/A | ER/NR | NPPD | Axtell-Post Rock 345 kV | DISIS STAGE
GEN-2018-003 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 150 | N/A | N/A | ER/NR | AEPW | North Boston-Bann 138kV Line | DISIS STAGE
GEN-2018-011 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 74.1 | N/A | N/A | ER/NR | WFEC | Dover 138 kV Switching Station | DISIS STAGE
GEN-2018-021 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 74.1 | N/A | N/A | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | DISIS STAGE
GEN-2018-024 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | N/A | N/A | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2018-026 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | N/A | N/A | ER | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2018-027 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | N/A | N/A | ER | AEPW | Tulsa Power Station 138kV Substation | DISIS STAGE
GEN-2018-028 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 200 | N/A | N/A | ER | AEPW | Tulsa North 138kV Substation | DISIS STAGE
GEN-2018-029 | 04 SOUTHEAST | 20 | DIS-18-1 | Battery/Storage | 100 | N/A | N/A | ER | OKGE | Horseshoe Lake 138kV Substation | DISIS STAGE
GEN-2018-048 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 300 | N/A | N/A | ER | OKGE | Pecan Creek 345kV Substation | DISIS STAGE
GEN-2018-050 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 200 | N/A | N/A | ER | AEPW | Longwood 345kV Substation | DISIS STAGE
GEN-2018-055 | 04 SOUTHEAST | 20 | DIS-18-1 | Solar | 252 | N/A | N/A | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | DISIS STAGE
GEN-2018-004 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 74.99 | N/A | N/A | ER | SPS | T14 Circuit 115kV line
GEN-2018-015 | 05 SOUTHWEST | 20 | DIS-18-1 | Solar | 252 | N/A | N/A | ER/NR | SPS | Tuco-Oklaunion 345kV Line
GEN-2018-052 | 05 SOUTHWEST | 20 | DIS-18-1 | Battery/Storage | 70 | N/A | N/A | ER | SPS | Roadrunner 115kV Substation | DISIS STAGE
J967 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | N/A | N/A | ER/NR | XEL |  | IA PENDING
MPC03600 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER | OTP |  | DISIS STAGE
MPC03700 | 01 NORTH | 19.5 | DIS-18-1-PQ | Solar | 75 | N/A | N/A | ER | OTP |  | DISIS STAGE
MPC03800 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 250 | N/A | N/A | ER/NR | OTP |  | DISIS STAGE
MPC03900 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 151.2 | N/A | N/A | ER/NR | OTP
MPC04000 | 01 NORTH | 19.5 | DIS-18-1-PQ | Wind | 150 | N/A | N/A | ER/NR | OTP
J982 | 02 NEBRASKA | 19.5 | DIS-18-1-PQ | Wind | 300 | N/A | N/A | ER | MEC |  | IA PENDING
J956 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | AMMO |  | IA PENDING
J976 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 150 | N/A | N/A | ER/NR | AMMO |  | IA PENDING
J987 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | AMMO |  | IA PENDING
J994 | 03 CENTRAL | 19.5 | DIS-18-1-PQ | Solar | 100 | N/A | N/A | ER/NR | AMMO |  | IA PENDING
J1834 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Gas | 43.5 | N/A | N/A | ER/NR | EES |  | Not Started
J1842 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | Wind | 135 | N/A | N/A | ER | EES-EAI |  | Not Started
GEN-2017-175 | 01 NORTH | 19 | DIS-17-2 | Wind | 300 | N/A | N/A | ER | WAPA | Vfodnes-Utica Jct. 230kV | DISIS STAGE
GEN-2017-214 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-215 | 01 NORTH | 19 | DIS-17-2 | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-222 | 01 NORTH | 19 | DIS-17-2 | Wind | 180 | N/A | N/A | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2017-105 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 75 | N/A | N/A | ER/NR | OPPD | Tekamah - Raun 161 kV Line
GEN-2017-144 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 200 | N/A | N/A | ER | NPPD | Holt County 345kV | DISIS STAGE
GEN-2017-181 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 300 | N/A | N/A | ER/NR | NPPD | Tobias 345kV Substation
GEN-2017-182 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 128 | N/A | N/A | ER/NR | NPPD | Tobias 345kV Substation
GEN-2017-198 | 02 NEBRASKA | 19 | DIS-17-2 | Battery/Storage | 11.64 | N/A | N/A | ER | OPPD | Jones St. No 1201 69kV substation
GEN-2017-201 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 250 | N/A | N/A | ER/NR | NPPD | Hoskins 345kV Substation
GEN-2017-210 | 02 NEBRASKA | 19 | DIS-17-2 | Hybrid | 310 | N/A | N/A | ER | NPPD | McCool 345kV Substation
GEN-2017-234 | 02 NEBRASKA | 19 | DIS-17-2 | Wind | 115 | N/A | N/A | ER | NPPD | Spalding to North Loup 115kV
GEN-2017-108 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | N/A | N/A | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-115 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 244 | N/A | N/A | ER | KCPL | Holt County 345 kV | DISIS STAGE
GEN-2017-119 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 180 | N/A | N/A | ER | SUNC | Elm Creek 345kV substation | DISIS STAGE
GEN-2017-120 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 260 | N/A | N/A | ER | WERE | Abilene Energy Center-Northview 115kV | DISIS STAGE
GEN-2017-121 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 200 | N/A | N/A | ER/NR | WERE | Sumner 138kV | DISIS STAGE
GEN-2017-131 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 29.6 | N/A | N/A | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-183 | 03 CENTRAL | 19 | DIS-17-2 | Wind | 400 | N/A | N/A | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-184 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 400 | N/A | N/A | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-188 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 130 | N/A | N/A | ER | EMDE | Asbury 161 kV | DISIS STAGE
GEN-2017-195 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 500.4 | N/A | N/A | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-196 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 128 | N/A | N/A | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-220 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | N/A | N/A | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-221 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 152 | N/A | N/A | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-226 | 03 CENTRAL | 19 | DIS-17-2 | Solar | 201.6 | N/A | N/A | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-227 | 03 CENTRAL | 19 | DIS-17-2 | Battery/Storage | 201.6 | N/A | N/A | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-117 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 19.8 | N/A | N/A | ER/NR | WFEC | El Reno SW 138kV | DISIS STAGE
GEN-2017-133 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 200 | N/A | N/A | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-134 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 250 | N/A | N/A | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-137 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 295 | N/A | N/A | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-140 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 160 | N/A | N/A | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 241.7 | N/A | N/A | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-149 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 258 | N/A | N/A | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-150 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | N/A | N/A | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-164 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 250 | N/A | N/A | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-171 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 150 | N/A | N/A | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-172 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | N/A | N/A | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-173 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 50 | N/A | N/A | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-178 | 04 SOUTHEAST | 19 | DIS-17-2 | Battery/Storage | 52 | N/A | N/A | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-203 | 04 SOUTHEAST | 19 | DIS-17-2 | Hybrid | 210 | N/A | N/A | ER | OKGE | Renfrow 345kV Substation | DISIS STAGE
GEN-2017-230 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | N/A | N/A | ER/NR | OKGE | Tryon 138kV Substation | DISIS STAGE
GEN-2017-231 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 72.5 | N/A | N/A | ER/NR | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2017-232 | 04 SOUTHEAST | 19 | DIS-17-2 | Solar | 52.2 | N/A | N/A | ER/NR | OKGE | Brown 138kV Substation | DISIS STAGE
GEN-2017-233 | 04 SOUTHEAST | 19 | DIS-17-2 | Wind | 215 | N/A | N/A | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-146 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 151.8 | N/A | N/A | ER | SPS | Deaf Smith-Plant X 230kV
GEN-2017-151 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 300 | N/A | N/A | ER | SPS | TUCO-Oklaunion 345kV | DISIS STAGE
GEN-2017-158 | 05 SOUTHWEST | 19 | DIS-17-2 | Wind | 265 | N/A | N/A | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2017-187 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 150 | N/A | N/A | ER | SPS | Flatland 115 kV Substation | DISIS STAGE
GEN-2017-239 | 05 SOUTHWEST | 19 | DIS-17-2 | Solar | 300 | N/A | N/A | ER | SPS | Mahoney 230kV Substation | DISIS STAGE
J545 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 110 | N/A | N/A | ER | XEL
J722 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 200 | N/A | N/A | ER | OTP
J801 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 74 | N/A | N/A | ER | DPC |  | DISIS STAGE
J874 | 01 NORTH | 18.5 | DIS-17-2-PQ | Solar | 150 | N/A | N/A | ER/NR | XEL |  | DISIS STAGE
J898 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 100 | N/A | N/A | ER | DPC
J926 | 01 NORTH | 18.5 | DIS-17-2-PQ | Wind | 93.6 | N/A | N/A | ER | XEL
J836 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Wind | 200 | N/A | N/A | ER | ALTW
J877 | 02 NEBRASKA | 18.5 | DIS-17-2-PQ | Solar | 125 | N/A | N/A | ER/NR | MEC |  | DISIS STAGE
GIA-83 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 1031 | N/A | N/A | ER/NR | AECI
GIA-86 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 103.68 | N/A | N/A | ER/NR | AECI
GIA-90 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 108 | N/A | N/A | ER/NR | AECI
GIA-91 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 104.4 | N/A | N/A | ER/NR | AECI
GIA-93 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Solar | 100 | N/A | N/A | ER/NR | AECI
GIA-95 | 03 CENTRAL | 18.5 | DIS-17-2-PQ | Wind | 128.8 | N/A | N/A | ER/NR | AECI
GEN-2017-010 | 01 NORTH | 18 | DIS-17-1 | Wind | 200.1 | N/A | N/A | ER | WAPA | Rhame 230 kV Sub | DISIS STAGE
GEN-2017-014 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | N/A | N/A | ER | WAPA | Philip Tap 230 kV | DISIS STAGE
GEN-2017-048 | 01 NORTH | 18 | DIS-17-1 | Wind | 300 | N/A | N/A | ER | BEPC-SPP | Neset 230 kV Substation | DISIS STAGE
GEN-2017-094 | 01 NORTH | 18 | DIS-17-1 | Wind | 200 | N/A | N/A | ER | WAPA | Fort Thompson-Huron 230 kV | DISIS STAGE
GEN-2017-097 | 01 NORTH | 18 | DIS-17-1 | Solar | 128 | N/A | N/A | ER | WAPA | Underwood 115 kV Sub | DISIS STAGE
GEN-2017-004 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 201.6 | N/A | N/A | ER | SUNC | Elm Creek - Summit 345 kV | DISIS STAGE
GEN-2017-005 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 190 | N/A | N/A | ER | WERE | Marmaton - Litchfield 161 kV | DISIS STAGE
GEN-2017-009 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 302 | N/A | N/A | ER | EMDE | Neosho - Caney River 345 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-018 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 189 | N/A | N/A | ER/NR | SUNC | Thistle 345 kV sub | DISIS STAGE
GEN-2017-022 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 65 | N/A | N/A | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-060 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | N/A | N/A | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-068 | 03 CENTRAL | 18 | DIS-17-1 | Solar | 103.5 | N/A | N/A | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-082 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 149.4 | N/A | N/A | ER | EMDE | Asbury Plant 161 kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2017-086 | 03 CENTRAL | 18 | DIS-17-1 | Wind | 150 | N/A | N/A | ER | WERE | Viola 345kV | DISIS STAGE
GEN-2016-037 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 300 | N/A | N/A | ER | AEPW | Chisholm-Gracemont 345kV | FACILITY STUDY STAGE
GEN-2017-011 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 151.8 | N/A | N/A | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | DISIS STAGE
GEN-2017-023 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 85 | N/A | N/A | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | DISIS STAGE
GEN-2017-027 | 04 SOUTHEAST | 18 | DIS-17-1 | Wind | 140 | N/A | N/A | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | DISIS STAGE
GEN-2017-036 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 100 | N/A | N/A | ER | WFEC | Snyder - Cache 138 kV | DISIS STAGE
GEN-2017-040 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200.1 | N/A | N/A | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-057 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | N/A | N/A | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-061 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 101.5 | N/A | N/A | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | DISIS STAGE
GEN-2017-071 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | N/A | N/A | ER | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-072 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | N/A | N/A | ER | OKGE | Greenwood 138kV sub | DISIS STAGE
GEN-2017-073 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | N/A | N/A | ER | GRDA | Dry Gulch 161kV sub | DISIS STAGE
GEN-2017-074 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 72.5 | N/A | N/A | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | N/A | N/A | ER | OKGE | Hugo-Sunnyside 345 kV | DISIS STAGE
GEN-2017-076 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 52.2 | N/A | N/A | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 124.7 | N/A | N/A | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-092 | 04 SOUTHEAST | 18 | DIS-17-1 | Solar | 200 | N/A | N/A | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2017-033 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 200 | N/A | N/A | ER | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-047 | 05 SOUTHWEST | 18 | DIS-17-1 | Wind | 102 | N/A | N/A | ER/NR | SPS | Cole 115kV
GEN-2017-100 | 05 SOUTHWEST | 18 | DIS-17-1 | Solar | 102.6 | N/A | N/A | ER/NR | SPS | Texas County 115kV
BEPCAyrshire | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 21 | N/A | N/A | ER | BEPC-SPP
BEPCGerled | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | N/A | N/A | ER | BEPC-SPP
BEPCHummel | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 10.5 | N/A | N/A | ER | BEPC-SPP
BEPCNDPW0 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 7.5 | N/A | N/A | ER | BEPC-SPP
BEPCNDPW1 | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 5 | N/A | N/A | ER | BEPC-SPP
J718 | 01 NORTH | 17.5 | DIS-17-1-PQ | Solar | 49.98 | N/A | N/A | ER/NR | DPC
WAPAMPSWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 1.5 | N/A | N/A | ER | WAPA
WAPATitanWind | 01 NORTH | 17.5 | DIS-17-1-PQ | Wind | 25 | N/A | N/A | ER | WAPA
J748 | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 100 | N/A | N/A | ER/NR | MEC
NPPDSpringview | 02 NEBRASKA | 17.5 | DIS-17-1-PQ | Wind | 3 | N/A | N/A | ER | NPPD
SWPANixaSolar | 03 CENTRAL | 17.5 | DIS-17-1-PQ | Solar | 7.9 | N/A | N/A | ER | SWPA
SPSLeaCounty | 05 SOUTHWEST | 17.5 | DIS-17-1-PQ | Solar | 5.5 | N/A | N/A | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-036 | 01 NORTH | 17 | DIS-16-2 | Wind | 44.6 | N/A | N/A | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 NORTH | 17 | DIS-16-2 | Wind | 98.9 | N/A | N/A | ER | WAPA | Bismark-Glenham 230 kV line | IA PENDING
GEN-2016-094 | 01 NORTH | 17 | DIS-16-2 | Wind | 200 | N/A | N/A | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | N/A | N/A | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-151 | 01 NORTH | 17 | DIS-16-2 | Wind | 202 | N/A | N/A | ER | BEPC-SPP | Tande 345kV
GEN-2016-074 | 02 NEBRASKA | 17 | DIS-16-2 | Wind | 200 | N/A | N/A | ER | NPPD | Sweetwater 345kV
GEN-2016-147 | 02 NEBRASKA | 17 | DIS-16-2 | Solar | 40 | N/A | N/A | ER | NPPD | Sidney 115 kV Sub
GEN-2016-111 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Reno - Summit 345kV | IA PENDING
GEN-2016-115 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 300 | N/A | N/A | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-149 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 134 | N/A | N/A | ER | WERE | Viola 345kV | IA PENDING
GEN-2016-160 | 03 CENTRAL | 17 | DIS-16-2 | Battery/Storage | 20 | N/A | N/A | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 CENTRAL | 17 | DIS-16-2 | Wind | 302 | N/A | N/A | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 303.6 | N/A | N/A | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 200 | N/A | N/A | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | N/A | N/A | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-102 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 150.9 | N/A | N/A | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-118 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 288 | N/A | N/A | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 600 | N/A | N/A | ER | OKGE | Spring Creek-Sooner 345kV | IA PENDING
GEN-2016-126 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 172.5 | N/A | N/A | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 176 | N/A | N/A | ER | OKGE | Woodring 345kV | IA PENDING
GEN-2016-131 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 2.5 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 6.1 | N/A | N/A | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 187.5 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 100 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 350 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 SOUTHEAST | 17 | DIS-16-2 | Wind | 175 | N/A | N/A | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-167 | 04 SOUTHEAST | 17 | DIS-16-2 | Solar | 73.5 | N/A | N/A | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 90 | N/A | N/A | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-121 | 05 SOUTHWEST | 17 | DIS-16-2 | Solar | 110 | N/A | N/A | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-123 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 298 | N/A | N/A | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-124 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 150 | N/A | N/A | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-125 | 05 SOUTHWEST | 17 | DIS-16-2 | Wind | 74 | N/A | N/A | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-177 | 05 SOUTHWEST | 17 | DIS-16-2 | Thermal | 17 | N/A | N/A | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/COMMERCIAL OPERATION
J569 | 01 NORTH | 16.5 | DIS-16-2-PQ | Wind | 100 | N/A | N/A | ER/NR | XEL
J476 | 03 CENTRAL | 16.5 | DIS-16-2-PQ | Wind | 246 | N/A | N/A | ER/NR | AMMO
ASGI-2016-011 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 7.4 | N/A | N/A | ER | SWPA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-012 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 61.73 | N/A | N/A | ER | SWPA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2016-013 | 04 SOUTHEAST | 16.5 | DIS-16-2-PQ | Thermal | 4.938 | N/A | N/A | ER | WFEC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-089 | 01 NORTH | 16 | DIS-16-1 | Wind | 200 | N/A | N/A | ER | BEPC-SPP | Utica 230 kV Substation
GEN-2016-004 | 01 NORTH | 16 | DIS-16-1 | Wind | 202 | N/A | N/A | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-017 | 01 NORTH | 16 | DIS-16-1 | Wind | 250.24 | N/A | N/A | ER | BEPC-SPP | Chappelle Creek 345kV
GEN-2016-021 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 298.47 | N/A | N/A | ER | NPPD | Hoskins 345kV
GEN-2016-043 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 230 | N/A | N/A | ER | NPPD | Hoskins 345kV
GEN-2016-075 | 02 NEBRASKA | 16 | DIS-16-1 | Wind | 50 | N/A | N/A | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
ASGI-2016-003 | 03 CENTRAL | 16 | DIS-16-1 | Diesel | 15.8 | N/A | N/A | ER | KCPL |  | IA PENDING
GEN-2016-009 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 29 | N/A | N/A | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-013 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 10 | N/A | N/A | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-014 | 03 CENTRAL | 16 | DIS-16-1 | Thermal | 10 | N/A | N/A | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-046 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 299 | N/A | N/A | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-050 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 250.7 | N/A | N/A | ER | NPPD | Axtell â€“ Post Rock 345 kV
GEN-2016-067 | 03 CENTRAL | 16 | DIS-16-1 | Wind | 73.6 | N/A | N/A | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-036 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 303.6 | N/A | N/A | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-003 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.4 | N/A | N/A | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 148.4 | N/A | N/A | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-022 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 151.8 | N/A | N/A | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-028 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 100 | N/A | N/A | ER | AEPW | Clayton 138 kV Sub | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 SOUTHEAST | 16 | DIS-16-1 | Solar | 100 | N/A | N/A | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 1.5 | N/A | N/A | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200 | N/A | N/A | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | N/A | N/A | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-047 | 04 SOUTHEAST | 16 | DIS-16-1 | Thermal | 24 | N/A | N/A | ER | OKGE | Mustang 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-051 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 9.8 | N/A | N/A | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 499.1 | N/A | N/A | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250.7 | N/A | N/A | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-068 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 250 | N/A | N/A | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-071 | 04 SOUTHEAST | 16 | DIS-16-1 | Wind | 200.1 | N/A | N/A | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
PQOKGEMustang | 04 SOUTHEAST | 16 | DIS-16-1 | CT | 57 | N/A | N/A | ER | OKGE
ASGI-2016-004 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 10 | N/A | N/A | ER | SPS
GEN-2015-041 | 05 SOUTHWEST | 16 | DIS-16-1 | Thermal | 5 | N/A | N/A | ER | SPS | TUCO 345kV
GEN-2015-082 | 05 SOUTHWEST | 16 | DIS-16-1 | Wind | 200 | N/A | N/A | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-046 | 01 NORTH | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER | BEPC-SPP | Tande 345kV
GEN-2015-096 | 01 NORTH | 15 | DIS-15-2 | Wind | 150 | N/A | N/A | ER | BEPC-SPP | Brady 230kV substation
GEN-2015-088 | 02 NEBRASKA | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER/NR | NPPD | Tobias 345kV Substation
GEN-2015-052 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-064 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 197.8 | N/A | N/A | ER | SUNC | Mingo 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-065 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 202.4 | N/A | N/A | ER | SUNC | Mingo 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-069 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER | WERE | Union Ridge 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-073 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 200.1 | N/A | N/A | ER/NR | WERE | Emporia 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-090 | 03 CENTRAL | 15 | DIS-15-2 | Wind | 220 | N/A | N/A | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-045 | 04 SOUTHEAST | 15 | DIS-15-2 | Battery/Storage | 20 | N/A | N/A | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-047 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER | OKGE | Sooner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-048 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 200 | N/A | N/A | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-057 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 100 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-062 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 4.5 | N/A | N/A | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-063 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 300 | N/A | N/A | ER | OKGE | Woodring-Matthewson 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-066 | 04 SOUTHEAST | 15 | DIS-15-2 | Wind | 248.4 | N/A | N/A | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-005NWE205 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 20 | N/A | N/A | ER | WAPA
ASGI-2016-007NWE208 | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 20 | N/A | N/A | ER | WAPA
GEN-2002-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2002-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 40.5 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2005-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2005-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 50 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2006-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | N/A | N/A | ER/NR | XEL
GEN-2006-002IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 53 | N/A | N/A | ER/NR | WAPA
GEN-2006-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 10 | N/A | N/A | ER/NR | XEL
GEN-2006-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 50 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2007-013IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2007-014IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 50 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2007-015IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2007-020IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 16 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2008-008IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 5 | N/A | N/A | ER/NR | WAPA
GEN-2009-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 200 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2009-018IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 100 | N/A | N/A | ER | BEPC-SPP
GEN-2009-020AIS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 80 | N/A | N/A | ER/NR | WAPA
GEN-2009-026IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 110 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2010-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 99 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2010-003IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 34 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2013-009IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 19.5 | N/A | N/A | ER | WAPA
GEN-2014-001IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 103.24 | N/A | N/A | ER | WAPA | Sulphur 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-006IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Gas | 125 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2014-010IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2014-014IS | 01 NORTH | 14.5 | DIS-15-2-PQ | Wind | 150 | N/A | N/A | ER/NR | BEPC-SPP
GEN-2007-017IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 202 | N/A | N/A | ER/NR | OPPD
GEN-2007-018IS | 02 NEBRASKA | 14.5 | DIS-15-2-PQ | Wind | 198 | N/A | N/A | ER/NR | OPPD
GEN-2015-007 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 160 | N/A | N/A | ER | NPPD | Hoskins 345kV
GEN-2015-023 | 02 NEBRASKA | 14 | DIS-15-1 | Wind | 300.7 | N/A | N/A | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV
ASGI-2015-001 | 03 CENTRAL | 14 | DIS-15-1 | Thermal | 6.13 | N/A | N/A | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-005 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200.1 | N/A | N/A | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-016 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 200 | N/A | N/A | ER/NR | KCPL | Tap Marmaton - Centerville 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-021 | 03 CENTRAL | 14 | DIS-15-1 | Solar | 20 | N/A | N/A | ER/NR | SUNC | Johnson Corner 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-024 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | N/A | N/A | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-025 | 03 CENTRAL | 14 | DIS-15-1 | Wind | 220 | N/A | N/A | ER | WERE | Tap Thistle â€“ Wichita 345kV Dbl CKT | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2015-004 | 04 SOUTHEAST | 14 | DIS-15-1 | Thermal | 56.4 | N/A | N/A | ER | GRDA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-001 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 200 | N/A | N/A | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 SOUTHEAST | 14 | DIS-15-1 | Solar | 120 | N/A | N/A | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-015 | 04 SOUTHEAST | 14 | DIS-15-1 | Wind | 154.56 | N/A | N/A | ER/NR | OKGE | Tap Medford Tap â€“ Coyote 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-014 | 05 SOUTHWEST | 14 | DIS-15-1 | Wind | 150 | N/A | N/A | ER | SPS | Tap Cochran - Lehman 115kV substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-031 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 35.8 | N/A | N/A | ER/NR | GRIS | Meadow Grove 230kV
GEN-2014-032 | 02 NEBRASKA | 13 | DIS-14-2 | Wind | 10.2 | N/A | N/A | ER/NR | NPPD | Meadow Grove 230kV
GEN-2004-017 | 03 CENTRAL | 13 | DIS-14-2 | Thermal | 250 | N/A | N/A | ER/NR | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-021 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 300 | N/A | N/A | ER/NR | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 CENTRAL | 13 | DIS-14-2 | Wind | 2.42 | N/A | N/A | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-028 | 03 CENTRAL | 13 | DIS-14-2 | Thermal | 50 | N/A | N/A | ER | EMDE | Riverton 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2014-014 | 04 SOUTHEAST | 13 | DIS-14-2 | Thermal | 56.4 | N/A | N/A | ER | GRDA |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-020 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 100 | N/A | N/A | ER/NR | AEPW | Tuttle 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-056 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 250 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 249.9 | N/A | N/A | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-064 | 04 SOUTHEAST | 13 | DIS-14-2 | Wind | 248.4 | N/A | N/A | ER | OKGE | Otter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-027 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 148.4 | N/A | N/A | ER/NR | SPS | Tolk - Yoakum 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-033 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | N/A | N/A | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-034 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 70 | N/A | N/A | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 SOUTHWEST | 13 | DIS-14-2 | Solar | 30 | N/A | N/A | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-040 | 05 SOUTHWEST | 13 | DIS-14-2 | Wind | 320 | N/A | N/A | ER | SPS | Castro 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-004 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 4 | N/A | N/A | ER | NPPD | Steele City 115kV | DISIS STAGE
GEN-2014-013 | 02 NEBRASKA | 12 | DIS-14-1 | Wind | 73.5 | N/A | N/A | ER/NR | LES | Meadow Grove 230kV
GEN-2014-001 | 03 CENTRAL | 12 | DIS-14-1 | Wind | 200.6 | N/A | N/A | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 10.5 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 SOUTHEAST | 12 | DIS-14-1 | Wind | 5.7 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 73.6 | N/A | N/A | ER/NR | NPPD | Monolith 115kV
GEN-2013-032 | 02 NEBRASKA | 11 | DIS-13-2 | Wind | 202.5 | N/A | N/A | ER | NPPD | Antelope 115kV
ASGI-2013-004 | 03 CENTRAL | 11 | DIS-13-2 | Gas | 36.6 | N/A | N/A | ER | SUNC |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-031 | 03 CENTRAL | 11 | DIS-13-2 | Thermal | 75.6 | N/A | N/A | ER | MIDW | Knoll 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-033 | 03 CENTRAL | 11 | DIS-13-2 | Thermal | 28 | N/A | N/A | ER/NR | MIDW | Goodman Energy Center 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-028 | 04 SOUTHEAST | 11 | DIS-13-2 | Thermal | 538 | N/A | N/A | ER | GRDA | Tap N Tulsa - GRDA 1 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-029 | 04 SOUTHEAST | 11 | DIS-13-2 | Wind | 299 | N/A | N/A | ER | OKGE | Renfrow 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-005 | 05 SOUTHWEST | 11 | DIS-13-2 | Wind | 1.65 | N/A | N/A | ER | SPS
GEN-2013-022 | 05 SOUTHWEST | 11 | DIS-13-2 | Solar | 25 | N/A | N/A | ER/NR | SPS | Norton 115kV Switching Station | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-002 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 50.6 | N/A | N/A | ER/NR | NPPD | Monolith 115kV
GEN-2013-008 | 02 NEBRASKA | 10 | DIS-13-1 | Wind | 1.2 | N/A | N/A | ER | NPPD | Steele City 115kV
GEN-2006-010 | 04 SOUTHEAST | 10 | DIS-13-1 | Thermal | 620 | N/A | N/A | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-007 | 04 SOUTHEAST | 10 | DIS-13-1 | Wind | 100 | N/A | N/A | ER/NR | OKGE | Tap Prices Falls - Carter 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-011 | 04 SOUTHEAST | 10 | DIS-13-1 | Thermal | 30 | N/A | N/A | ER | AEPW | Turk 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-012 | 04 SOUTHEAST | 10 | DIS-13-1 | Thermal | 147 | N/A | N/A | ER | OKGE | Redbud 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-001 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 11.5 | N/A | N/A | ER | SPS
ASGI-2013-002 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | N/A | N/A | ER | SPS
ASGI-2013-003 | 05 SOUTHWEST | 10 | DIS-13-1 | Wind | 18.4 | N/A | N/A | ER | SPS
GEN-2013-016 | 05 SOUTHWEST | 10 | DIS-13-1 | Thermal | 203 | N/A | N/A | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-021 | 02 NEBRASKA | 9 | DIS-12-2 | Thermal | 4.8 | N/A | N/A | ER | LES | Terry Bundy Generating Station 115kV
GEN-2012-024 | 03 CENTRAL | 9 | DIS-12-2 | Wind | 180 | N/A | N/A | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-028 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 74 | N/A | N/A | ER | WFEC | Gotebo 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-032 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 299 | N/A | N/A | ER | OKGE | Rose Hill-(Ranch Road) Sooner (Open Sky) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-033 | 04 SOUTHEAST | 9 | DIS-12-2 | Wind | 98.82 | N/A | N/A | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-041 | 04 SOUTHEAST | 9 | DIS-12-2 | Thermal | 121.5 | N/A | N/A | ER | OMPA | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2012-002 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 18.15 | N/A | N/A | ER | SPS
GEN-2012-020 | 05 SOUTHWEST | 9 | DIS-12-2 | Wind | 478 | N/A | N/A | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-034 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 7 | N/A | N/A | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-035 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 7 | N/A | N/A | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-036 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 7 | N/A | N/A | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-037 | 05 SOUTHWEST | 9 | DIS-12-2 | Thermal | 203 | N/A | N/A | ER | SPS | TUCO 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-021N | 02 NEBRASKA | 8 | PQ | Wind | 75 | N/A | N/A | ER | NPPD | Ainsworth Wind Tap 115kV
GEN-2004-023N | 02 NEBRASKA | 8 | PQ | Thermal | 75 | N/A | N/A | ER | NPPD | Columbus Co 115kV
GEN-2006-020N | 02 NEBRASKA | 8 | PQ | Wind | 42 | N/A | N/A | ER | NPPD | Bloomfield 115kV
GEN-2006-038N005 | 02 NEBRASKA | 8 | PQ | Wind | 80 | N/A | N/A | ER | NPPD | Broken Bow 115kV
GEN-2006-038N019 | 02 NEBRASKA | 8 | PQ | Wind | 80 | N/A | N/A | ER | NPPD | Petersburg North 115kV
GEN-2007-011N08 | 02 NEBRASKA | 8 | PQ | Wind | 81 | N/A | N/A | ER | NPPD | Bloomfield 115kV
GEN-2008-119O | 02 NEBRASKA | 8 | PQ | Wind | 60 | N/A | N/A | ER | OPPD | S1399 161kV
NPPDBrokenBow | 02 NEBRASKA | 8 | PQ | Heat | 7.3 | N/A | N/A | ER | NPPD
NPPDBuffaloCountySolar | 02 NEBRASKA | 8 | PQ | Solar | 10 | N/A | N/A | ER | NPPD
NPPDBurtCountyWind | 02 NEBRASKA | 8 | PQ | Wind | 10 | N/A | N/A | ER | NPPD
NPPDBurwell | 02 NEBRASKA | 8 | PQ | Heat | 3.3 | N/A | N/A | ER | NPPD
NPPDColumbusHydro | 02 NEBRASKA | 8 | PQ | Hydro | 15 | N/A | N/A | ER | NPPD
NPPDOrd | 02 NEBRASKA | 8 | PQ | Heat | 10.8 | N/A | N/A | ER | NPPD
NPPDStuart | 02 NEBRASKA | 8 | PQ | Heat | 1.8 | N/A | N/A | ER | NPPD
ASGI-2012-006 | 03 CENTRAL | 8 | DIS-12-1 | Steam | 21.25 | N/A | N/A | ER | SUNC
ASGI-2012-008 | 03 CENTRAL | 8 | PQ | Gas | 3.655 | N/A | N/A | ER | WERE |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-030 | 03 CENTRAL | 8 | PQ | Thermal | 50 | N/A | N/A | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039A | 03 CENTRAL | 8 | PQ | Wind | 104 | N/A | N/A | ER | SUNC | Shooting Star Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-039M | 03 CENTRAL | 8 | PQ | Wind | 100 | N/A | N/A | ER | SUNC | Central Plains Tap 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-040 | 03 CENTRAL | 8 | PQ | Thermal | 50 | N/A | N/A | ER | EMDE | LaRussell Energy Center 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-004 | 03 CENTRAL | 8 | PQ | Wind | 153 | N/A | N/A | ER | WERE | Latham 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-025A | 03 CENTRAL | 8 | PQ | Wind | 100.5 | N/A | N/A | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-006A | 03 CENTRAL | 8 | PQ | Wind | 201 | N/A | N/A | ER | SUNC | Elm Creek 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-019 | 03 CENTRAL | 8 | PQ | Wind | 249.3 | N/A | N/A | ER | MIDW | Smoky Hills Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-014 | 03 CENTRAL | 8 | PQ | Wind | 152 | N/A | N/A | ER | SUNC | Spearville 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-012 | 03 CENTRAL | 8 | PQ | Wind | 248.4 | N/A | N/A | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-013 | 03 CENTRAL | 8 | PQ | Wind | 199.8 | N/A | N/A | ER | WERE | Caney River 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-021 | 03 CENTRAL | 8 | PQ | Wind | 94 | N/A | N/A | ER | SUNC | Flat Ridge Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-007 | 03 CENTRAL | 8 | DIS-12-1 | Thermal | 120 | N/A | N/A | ER/NR | SUNC | Rubart 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-014 | 04 SOUTHEAST | 8 | PQ | Wind | 94.5 | N/A | N/A | ER | WFEC | Ft Supply 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-026 | 04 SOUTHEAST | 8 | PQ | Wind | 74.25 | N/A | N/A | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-037 | 04 SOUTHEAST | 8 | PQ | Wind | 102 | N/A | N/A | ER | OKGE | FPL Moreland Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-005 | 04 SOUTHEAST | 8 | PQ | Wind | 123 | N/A | N/A | ER | WFEC | Red Hills Tap 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-004 | 04 SOUTHEAST | 8 | PQ | Wind | 100 | N/A | N/A | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-005 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | N/A | N/A | ER | WFEC | Anadarko - Paradise (Blue Canyon) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-022 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | N/A | N/A | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-023 | 04 SOUTHEAST | 8 | PQ | Wind | 20.6 | N/A | N/A | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-003 | 04 SOUTHEAST | 8 | PQ | Wind | 30.6 | N/A | N/A | ER | WFEC | Washita 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2005-008 | 04 SOUTHEAST | 8 | PQ | Wind | 120 | N/A | N/A | ER | OKGE | Woodward 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-002 | 04 SOUTHEAST | 8 | PQ | Wind | 100.8 | N/A | N/A | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-008 | 04 SOUTHEAST | 8 | PQ | Thermal | 550 | N/A | N/A | ER | AEP | Arsenal Hill 138kV | DISIS STAGE
GEN-2006-024S | 04 SOUTHEAST | 8 | PQ | Wind | 18.9 | N/A | N/A | ER | WFEC | Buffalo Bear Tap 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-035 | 04 SOUTHEAST | 8 | PQ | Wind | 132 | N/A | N/A | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-043 | 04 SOUTHEAST | 8 | PQ | Wind | 99 | N/A | N/A | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-046 | 04 SOUTHEAST | 8 | PQ | Wind | 129.6 | N/A | N/A | ER | OKGE | Dewey 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-004 | 04 SOUTHEAST | 8 | DIS-12-1 | Wind | 40.8 | N/A | N/A | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2001-033 | 05 SOUTHWEST | 8 | PQ | Wind | 180 | N/A | N/A | ER | SPS | San Juan Tap 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-008 | 05 SOUTHWEST | 8 | PQ | Wind | 240 | N/A | N/A | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-009 | 05 SOUTHWEST | 8 | PQ | Wind | 67.2 | N/A | N/A | ER | SPS | Hansford 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2002-022 | 05 SOUTHWEST | 8 | PQ | Wind | 239.2 | N/A | N/A | ER | SPS | Bushland 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2003-020 | 05 SOUTHWEST | 8 | PQ | Wind | 159.1 | N/A | N/A | ER | SPS | Martin 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2004-015 | 05 SOUTHWEST | 8 | PQ | Thermal | 150 | N/A | N/A | ER | SPS |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-015 | 05 SOUTHWEST | 8 | PQ | Thermal | 150 | N/A | N/A | ER | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-018 | 05 SOUTHWEST | 8 | PQ | Thermal | 168.1 | N/A | N/A | ER | SPS | TUCO 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-020S | 05 SOUTHWEST | 8 | PQ | Wind | 20 | N/A | N/A | ER | SPS | DWS Frisco 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2006-026 | 05 SOUTHWEST | 8 | PQ | Thermal | 604 | N/A | N/A | ER | SPS | Hobbs 230kV & Hobbs 115kV
GEN-2006-044 | 05 SOUTHWEST | 8 | PQ | Wind | 370 | N/A | N/A | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2012-001 | 05 SOUTHWEST | 8 | DIS-12-1 | Wind | 61.2 | N/A | N/A | ER | SPS | Tap Grassland Â- Borden County 230 kv | IA FULLY EXECUTED/COMMERCIAL OPERATION
LlanoEstacadoWhiteDeer | 05 SOUTHWEST | 8 | PQ | Wind | 80 | N/A | N/A | ER | SPS
SPSCarson | 05 SOUTHWEST | 8 | PQ | Wind | 10 | N/A | N/A | ER | SPS
SPSDumas19thSt | 05 SOUTHWEST | 8 | PQ | Wind | 10 | N/A | N/A | ER | SPS
SPSEtter | 05 SOUTHWEST | 8 | PQ | Wind | 10 | N/A | N/A | ER | SPS
SPSHopi | 05 SOUTHWEST | 8 | PQ | Solar | 10 | N/A | N/A | ER | SPS
SPSJal | 05 SOUTHWEST | 8 | PQ | Solar | 10 | N/A | N/A | ER | SPS
SPSLeaRoad | 05 SOUTHWEST | 8 | PQ | Solar | 10 | N/A | N/A | ER | SPS
SPSMonument | 05 SOUTHWEST | 8 | PQ | Solar | 10 | N/A | N/A | ER | SPS
SPSMooreE | 05 SOUTHWEST | 8 | PQ | Wind | 10 | N/A | N/A | ER | SPS
SPSOcotillo | 05 SOUTHWEST | 8 | PQ | Solar | 10 | N/A | N/A | ER | SPS
SPSSherman | 05 SOUTHWEST | 8 | PQ | Wind | 10 | N/A | N/A | ER | SPS
Sunray | 05 SOUTHWEST | 8 | PQ | Wind | 34.5 | N/A | N/A | ER | SPS
GEN-2011-056 | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | N/A | N/A | ER | NPPD | Jeffrey 115kV
GEN-2011-056A | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 3.6 | N/A | N/A | ER | NPPD | John 1 115kV
GEN-2011-056APQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 18 | N/A | N/A | ER | NPPD
GEN-2011-056B | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 4.5 | N/A | N/A | ER | NPPD | John 2 115kV
GEN-2011-056BPQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 18 | N/A | N/A | ER | NPPD
GEN-2011-056PQ | 02 NEBRASKA | 7 | DIS-11-2 | Hydro | 20 | N/A | N/A | ER | NPPD
GEN-2011-057 | 03 CENTRAL | 7 | DIS-11-2 | Wind | 150 | N/A | N/A | ER | WERE | Creswell 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 6.6 | N/A | N/A | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-040 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 111 | N/A | N/A | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-050 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 108 | N/A | N/A | ER | AEPW | Tap Rush Springs Â- Marlow 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-054 | 04 SOUTHEAST | 7 | DIS-11-2 | Wind | 300 | N/A | N/A | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2011-004 | 05 SOUTHWEST | 7 | DIS-11-2 | Wind | 19.8 | N/A | N/A | ER | SPS
GEN-2011-045 | 05 SOUTHWEST | 7 | DIS-11-2 | Thermal | 205 | N/A | N/A | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-046 | 05 SOUTHWEST | 7 | DIS-11-2 | Thermal | 23 | N/A | N/A | ER | SPS | Tucumcari 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-048 | 05 SOUTHWEST | 7 | DIS-11-2 | Thermal | 175 | N/A | N/A | ER/NR | SPS | Mustang 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-018 | 02 NEBRASKA | 6 | DIS-11-1 | Wind | 73.6 | N/A | N/A | ER/NR | NPPD | Steele City 115kV
GEN-2011-027 | 02 NEBRASKA | 6 | DIS-11-1 | Wind | 120 | N/A | N/A | ER/NR | NPPD | Wakefield 230kV
GEN-2004-008 | 03 CENTRAL | 6 | DIS-11-1 | Thermal | 850 | N/A | N/A | ER | KCPL |  | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-057 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 201 | N/A | N/A | ER/NR | MIDW | Rice County 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-008 | 03 CENTRAL | 6 | DIS-11-1 | Wind | 600 | N/A | N/A | ER | SUNC | Clark County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-055 | 04 SOUTHEAST | 6 | DIS-11-1 | Thermal | 4.5 | N/A | N/A | ER | AEPW | Wekiwa 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-010 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 100.8 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 175 | N/A | N/A | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 SOUTHEAST | 6 | DIS-11-1 | Wind | 165.6 | N/A | N/A | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2011-002 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 20 | N/A | N/A | ER | SPS
ASGI-2011-003 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 10 | N/A | N/A | ER | SPS
GEN-2011-014 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 198 | N/A | N/A | ER | OKGE | Beaver CountyÂ-Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-022 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 299 | N/A | N/A | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-025 | 05 SOUTHWEST | 6 | DIS-11-1 | Wind | 79.96 | N/A | N/A | ER | SPS | Tap Floyd County - Crosby County 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-051 | 02 NEBRASKA | 5 | DIS-10-2 | Wind | 200 | N/A | N/A | ER | NPPD | Wakefield 230kV
GEN-2010-036 | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 4.6 | N/A | N/A | ER | WERE | 6th Street 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-036PQ | 03 CENTRAL | 5 | DIS-10-2 | Hydro | 2.757 | N/A | N/A | ER | WERE
GEN-2010-040 | 04 SOUTHEAST | 5 | DIS-10-2 | Wind | 300 | N/A | N/A | ER | OKGE | Cimarron 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-020 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 30 | N/A | N/A | ER | SPS
ASGI-2010-021 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 15 | N/A | N/A | ER | SPS
ASGI-2011-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 27.3 | N/A | N/A | ER | SPS
GEN-2010-001 | 05 SOUTHWEST | 5 | DIS-10-2 | Wind | 300 | N/A | N/A | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-123N | 02 NEBRASKA | 4 | DIS-10-1 | Wind | 89.66 | N/A | N/A | ER | NPPD | Tap Pauline - Hildreth (Rosemont) 115kV
GEN-2009-008 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 198.69 | N/A | N/A | ER | MIDW | South Hays 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-020 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 48.3 | N/A | N/A | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-040 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 72 | N/A | N/A | ER | WERE | Tap Smittyville - Knob Hill 115KV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-003 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 99.5 | N/A | N/A | ER | WERE | Waverly 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-005 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 299.2 | N/A | N/A | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-009 | 03 CENTRAL | 4 | DIS-10-1 | Wind | 165.6 | N/A | N/A | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-037 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 99 | N/A | N/A | ER | WFEC | Tap Washita - Blue Canyon Wind 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-044 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 197.8 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-011 | 04 SOUTHEAST | 4 | DIS-10-1 | Wind | 29.7 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2010-010 | 05 SOUTHWEST | 4 | DIS-10-1 | Gas | 46.5 | N/A | N/A | ER | SPS
GEN-2008-022 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 299.65 | N/A | N/A | ER | SPS | Eddy County-Tolk (Crossroads) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-047 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 263.13 | N/A | N/A | ER | OKGE | Hitchland-Woodward EHV Dbl Ckt (Beaver County) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-006 | 05 SOUTHWEST | 4 | DIS-10-1 | Thermal | 205 | N/A | N/A | ER | SPS | Jones 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2010-014 | 05 SOUTHWEST | 4 | DIS-10-1 | Wind | 358.8 | N/A | N/A | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2006-037N1 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 75 | N/A | N/A | ER | NPPD | Broken Bow 115kV
GEN-2006-044N | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 40.5 | N/A | N/A | ER | OPPD | North Petersburg 115kV
GEN-2008-086N02 | 02 NEBRASKA | 3 | DIS-09-1 | Wind | 201 | N/A | N/A | ER | NPPD | Meadow Grove 230kV
GEN-2007-040 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 131.1 | N/A | N/A | ER | SUNC | Buckner 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-079 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 98.9 | N/A | N/A | ER | SUNC | Crooked Creek 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-092 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.5 | N/A | N/A | ER | MIDW | Post Rock 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-124 | 03 CENTRAL | 3 | DIS-09-1 | Wind | 200.1 | N/A | N/A | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-129 | 03 CENTRAL | 3 | DIS-09-1 | Thermal | 72 | N/A | N/A | ER | KCPL | Pleasant Hill 161kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-023 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 150 | N/A | N/A | ER | AEPW | Hobart Junction 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2009-025 | 04 SOUTHEAST | 3 | DIS-09-1 | Wind | 59.8 | N/A | N/A | ER | OKGE | TAP Deer Creek â€“ Sinclair 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-051 | 05 SOUTHWEST | 3 | DIS-09-1 | Wind | 161 | N/A | N/A | ER | SPS | Potter County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-025 | 03 CENTRAL | 2 | ICS1 | Wind | 299.2 | N/A | N/A | ER | WERE | Viola 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 CENTRAL | 2 | ICS1 | Wind | 250 | N/A | N/A | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-021 | 04 SOUTHEAST | 2 | ICS1 | Wind | 198.9 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-043 | 04 SOUTHEAST | 2 | ICS1 | Wind | 200 | N/A | N/A | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-044 | 04 SOUTHEAST | 2 | ICS1 | Wind | 299.2 | N/A | N/A | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-050 | 04 SOUTHEAST | 2 | ICS1 | Wind | 151.8 | N/A | N/A | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-052 | 04 SOUTHEAST | 2 | ICS1 | Thermal | 150 | N/A | N/A | ER | WFEC | Anadarko 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-062 | 04 SOUTHEAST | 2 | ICS1 | Wind | 424 | N/A | N/A | ER | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-003 | 04 SOUTHEAST | 2 | ICS1 | Wind | 101.2 | N/A | N/A | ER | OKGE | Woodward EHV 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-013 | 04 SOUTHEAST | 2 | ICS1 | Wind | 300 | N/A | N/A | ER | OKGE | Hunter 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2007-046 | 05 SOUTHWEST | 2 | ICS1 | Wind | 200 | N/A | N/A | ER | SPS | Hitchland 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GIA-118 | 03 CENTRAL | 23.5 | DIS-22-PQ | Solar | 32 | N/A | N/A | ER/NR | AECI | Anniston-Wyatt 69 kV
GIA-116 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | THERMAL | 26 | N/A | N/A | ER/NR | AECI | St. Francis 161 kV Bus
GIA-117 | 03 CENTRAL | 22.5 | DIS-21-1-PQ | THERMAL | 46 | N/A | N/A | ER/NR | AECI | St. Francis 161 kV Bus
GIA-96 | 04 SOUTHEAST | 19.5 | DIS-18-1-PQ | WIND | 97.5 | N/A | N/A | ER | AECI | Stroud 138kV

## Constraints Summary
Group | Assigned Study Number | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
03ALL | GIA-120 | ERIS | Voltage | None | N/A | None | [7 empty] | None
03ALL | GIA-120 | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
03ALL | GIA-120 | ERIS | Thermal | None | N/A | None | [7 empty] | None
00NR | GIA-120 | NRIS | Voltage | None | N/A | None | [7 empty] | None
00NR | GIA-120 | NRIS | Non-Converge | None | N/A | None | [7 empty] | None
00NR | GIA-120 | NRIS | Thermal | None | N/A | None | [7 empty] | None
00ALL | GIA-121 | ERIS | Voltage | None | N/A | None | [7 empty] | None
00ALL | GIA-121 | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
00ALL | GIA-121 | ERIS | Thermal | None | N/A | None | [7 empty] | None
00NR | GIA-121 | NRIS | Voltage | None | N/A | None | [7 empty] | None
00NR | GIA-121 | NRIS | Non-Converge | None | N/A | None | [7 empty] | None
00NR | GIA-121 | NRIS | Thermal | None | N/A | None | [7 empty] | None
03ALL | GIA-122 | ERIS | Voltage | None | N/A | None | [7 empty] | None
03ALL | GIA-122 | ERIS | Non-Converge | None | N/A | None | [7 empty] | None
03ALL | GIA-122 | ERIS | Thermal | None | N/A | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF %
Total | [6 empty] | 0 |  | 0

## Upgrade Summary
Upgrade Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time (months) | Total Upgrade Cost
0

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 03ALL | 0 | N/A | GIA-120 | " | None |  |  |  |  | None
Thermal | 03ALL | 0 | N/A | GIA-120 | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | N/A | GIA-120 | " | None |  |  |  |  | None
Thermal | 00NR | 0 | N/A | GIA-120 | " | None |  |  |  |  | None
Non-Converge | 00ALL | 0 | N/A | GIA-121 | " | None |  |  |  |  | None
Thermal | 00ALL | 0 | N/A | GIA-121 | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | N/A | GIA-121 | " | None |  |  |  |  | None
Thermal | 00NR | 0 | N/A | GIA-121 | " | None |  |  |  |  | None
Non-Converge | 03ALL | 0 | N/A | GIA-122 | " | None |  |  |  |  | None
Thermal | 03ALL | 0 | N/A | GIA-122 | " | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | Group | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 03ALL | 0 | N/A | GIA-120 | N/A | [7 empty] | N/A
Voltage | 00NR | 0 | N/A | GIA-120 | N/A | [7 empty] | N/A
Voltage | 00ALL | 0 | N/A | GIA-121 | N/A | [7 empty] | N/A
Voltage | 00NR | 0 | N/A | GIA-121 | N/A | [7 empty] | N/A
Voltage | 03ALL | 0 | N/A | GIA-122 | N/A | [7 empty] | N/A